## 1. Introduction
Back to user guide
1. Introduction
1.1 Contact Persons
Person | Country | Company | E-mail: | Mobile: | Specific con- tribution to task C
Anders Dyrelund | Denmark | Ramboll | AD@ramboll.com | +45 5161 8766 | Manager of task C
Søren M. Thomsen | Denmark | Ramboll | SMT@ramboll.com | +45 5161 2421 | Editor of this file
Jørgen Rose | Denmark | SBI | jro@sbi.aau.dk | +45 99 40 22 26
Oddgeir Gudmundsson | Denmark | Danfoss | og@danfoss.com | +45 29 44 15 63 | Equipment in buildings
Jens Peter Sandemann | Denmark | MOD | FES-BES25 Sandemand, Jens Peter <FES-BES25@mil.dk> | +45 72 31 33 36
Niels Vilstrup | Denmark | MPA | nivils@um.dk | +1 202 322 8858
Leif Holm Tambjerg | Denmark | EMD | lht@emd.dk | +45 96 35 44 57 | EnergyPRO
Anders Andersen | Denmark | EMD | ana@emd.dk | +45 40 19 80 66 | EnergyPro
Dominik Heering | Germany | GEF | dominik.hering@gef.de | +49 1636 9713 22 | Co-Manager of task C
Ruediger Lohse | Germany | KEA | Ruediger.Lohse@kea-bw.de | +49 1736 614 070
Dirk Pietruschka | Germany | Enisyst | dirk.pietruschka@enisyst.de | +49 7127 349 7987
Anna-Maria Fulterer | Austria | AEE INTEC | a.m.fulterer@aee.at | +43 3112 5886 - 365
Ingo Leusbrock | Austria | AEE INTEC | i.leusbrock@aee.at | +43 3112 5886 - 261
Yiyu Ding | Norway | NTNU | yiyu.ding@ntnu.no
Laxmi Rao | USA | IDEA | Laxmi.idea@districtenergy.org | +1 508 366 9339
Peter Ellis | USA | Big Ladder Software | peter.ellis@bigladdersoftware.com
Michael O'Keefe | USA | Big Ladder Software | michael.okeefe@bigladdersoftware.com | +1 303 949 3414
Antony Latino | USA | SC-B Consulting | anthony.latino@sc-binc.com | +1 815 383 5088
Ben Polly | USA | NREL | ben.polly@nrel.gov | +1
Dylan Cutler | USA | NREL | dylan.cutler@nrel.gov | +1
Alexander Zhivov | USA | MOD | Alexander.M.Zhivov@usace.army.mil | +1 217 373 4519
This list of contact persons include persons, which has contributed to the data or been directly involved in the database development.
The technologies database presented in this appendix was developed based on the information available from various sources. These included; NZP/SMPL tool, MIT LL ERA tool, REOpt tool, U.S. Department of Energy CHP factsheets, Danish Energy Agency Technology Catalogue and information provided by the International District Energy Association, EATON, Schneider Electric, TKDA, and GEF. The technology reliability data was provided by the U.S. Army Corps of Engineers Power Reliability Enhancement Program (PREP). The database is comprised of multiple energy conversion, distribution and storage technologies which can be integrated by energy planners into energy system architectures to create different alternatives of community energy systems.
The database features information on mature (first generation) technologies and state-of-the-art technologies available on the market for supplying electricity, heating, cooling and natural gas. It includes technical characteristics and costs and shows the economy of scale for different technologies and the way different technologies can interact with each other.
The database technology information contains general data which is accurate enough to support comparison of different concepts on the planning level, but is not designed for making specific investment decisions, system design, or equipment specification. Information is supported by references and links to examples of technology implementation, including case studies [Annex 73 Book of Case Studies].

## 2. User guide
2. User Guide
2.1 Table of contents
The technology catalogue consist of many tabs. In the text below, the data in each tab are described.
2.1.1 Introduction
In this tab, the project is introduced, and contact information on the involved persons in the project are also shown.
1. Introduction
2.1.2 User Guide
This tab provides an overview of the model and describes where information and calculations can be found. The cell formating, tab colors and the flow of the model
is also explained. The user is referred to this sheet, if questions arise on where to find certain data and calculations.
Tab 2.1 Matrix shows a matrix of cases with links to the relevant energy system analysis and technologies applied in the specific case.
2.1.3 Energy systems
Analysis results from different energy systems are presented. The LCOE calculation can be found in subsequent tabs. The following information can be found:
3. Energy systems
3.1 Arctic climate
3.2 Tropic climate
3.3 Mild climate
3.3.1 Energy system analysis (w/ grid connection)
3.3.2 Energy system analysis (wo/ grid connection)
3.3.3 Energy system analysis (wo/ grid connection, w/ wind energy)
3.4 New energy system 1
3.5 New energy system 2
3. Energy systems
2.1.4 Energy storage
In this tab are data on energy storage presented. The following information can be found:
4. Energy storage
4.1 Hot water tanks (pressure-less)
4.2 Hot water tanks (pressurized)
4.3 Pit thermal energy storage
4.4 Cold storage
4.5 Subsurface gas storage
4.6 Pumped hydro storage
4.7 Electric batteries
4.8 New technology 1
4.9 New technology 2
4. Energy storage
2.1.5 Boiler plants
In this tab are data on boiler plants presented. The following information can be found:
5. Boiler plants
5.1 Natural gas boiler
5.2 Biomass boiler
5.2.1 Wood pellet boiler
5.2.2 Wood chips boiler
5.2.3 Straw boiler
5.3 Electric boiler
5.4 Waste boiler
5.5 Coal boiler
5.6 Oil boiler
5.7 New technology 1
5.8 New technology 2
5. Boiler plants
2.1.6 CHP and condensing power plants
In this tab are data on CHP and condensing power plants presented. The following information can be found:
6. CHP and condensing power plants
6.1 Gas engine
6.2 Gas turbine combined cycle
6.3 Gas turbine simple cycle
6.4 Biomass CHP
6.4.1 Wood chips CHP
6.4.2 Wood pellets CHP
6.4.3 Straw CHP
6.5 Waste CHP
6.6 New technology 1
6.7 New technology 2
6. CHP and cond. power plants
2.1.7 Heat pumps and chillers
In this tab are data on heat pumps and chillers presented. The following information can be found:
7. Heat pumps and chillers
7.1 Electric heat pump
7.2 Absorption heat pump
7.3 Electric chiller
7.4 New technology 1
7.5 New technology 2
7. Heat pumps and chillers
2.1.8 Renewable energy
In this tab are data on renewable energy technologies presented. The following information can be found:
8. Renewable energy
8.1 Solar heating
8.2 High temperature solar heating (no data)
8.3 Solar PV
8.4 Wind turbine
8.5 Deep geothermal
8.6 Biogas plant
8.7 Solar PVT
8.8 Fuel cells
8.9 New technology 1
8.10 New technology 2
8. Renewable energy
2.1.9 District heating network
In this tab are data on district heating networks presented. The following information can be found:
9. District heating network
9.1 Capacities and losses
9.2 Prices
9.3 Hydraulic network analysis
9.4 Pre-insulated pipes
9.5 District heating development
9.6 Two-pipe active beam system
9.7 Steam pipes
9.8 New technology 1
9.9 New technology 2
9. District heating network
2.1.10 District cooling network
In this tab are data on district cooling networks presented. The following information can be found:
10. District cooling network
10.1 Capacities and losses
10.2 PEX pipes
10.3 New technology 1
10.4 New technology 2
10. District cooling network
2.1.11 Natural gas network
In this tab are data on natural gas networks presented. The following information can be found:
11. Natural gas network
11.1 Natural gas transmission
11.2 Natural gas distribution
11.3 Biogas networks
11.4 Hydrogen networks
11.5 New technology 1
11.6 New technology 2
11. Natural gas network
2.1.12 Electric network
In this tab are data on electric networks presented. The following information can be found:
12. Electric network
12.1 Electric transmission network
12.2 Electric distribution network
12.3 Microgrid
12.4 New technology 1
12.5 New technology 2
12. Electric network
2.1.13 HVAC
In this tab are data on HVAC presented. The following information can be found:
13. HVAC
13.1 Heat exchangers (building level)
13.2 Central heating
13.3 Ventilation system
13.4 Ventilation with heat recovery
13.5 Hot tap water system
13.6 Hydronic balancing
13.7 New technology 1
13.8 New technology 2
13. HVAC
2.1.14 Resiliency
In this tab are data on resiliency presented. The following information can be found:
14. Resiliency
14.1 Emergency generators
14.2 UPS
14.3 Emergency power system
14.4 Back-up boiler and storage
14.5 Reliability technology data
14.6 New technology 1
14.7 New technology 2
14. Resiliency
2.1.15 Miscellaneous
In this tab are data on miscellaneous presented. The following information can be found:
15. Miscellaneous
15.1 Heat exchanger stations
15.2 Pressure sectioning
15.3 Pressure regulator
15.4 SCADA systems
15.5 New technology 1
15.6 New technology 2
15. Miscellaneous
2.1.16 Non energy
In this tab are data on non energy presented. The following information can be found:
16. Non energy
16.1 Flood control
16.2 Tunnels
16.3 New technology 1
16.4 New technology 2
16. Non energy
2.1.17 Energy system planning models
In this tab are selected energy system planning models presented. The following information can be found:
17. Energy system planning models
17.1 Energy system analysis and planning programs overview
17.2 Use of the tools
17.3 Project phases
17.4 Balmorel
17.5 EnergyPLAN
17.6 EnergyPRO
17.7 TIMES
17.8 SIFRE
17.9 Statistical analysis
17.10 Stochastic programming
17.11 Hydraulic analysis
17.12 New technology 1
17.13 New technology 2
17 ES planning models
2.1.18 Energy system operation models
In this tab are selected energy system operation models presented. The following information can be found:
18. Energy system operation models
18.1 Mentor Planner
18.2 Flexynets
18.3 HeatFor
18.4 New technology 1
18.5 New technology 2
18. ES operation models
2.1.19 Database output
In this tab are the output for the energy system analysis model presented. The following information can be found:
19. Database output
19.1 Extraction of data from the database
19.2 Converted to local currency
19. Database output
2.2 Cell formatting
Type of cell |  |  | Allowed action | Explanation
Standard input |  |  | Insert value | Input can be changed
Detailed input |  |  | Insert value | Detailed data required for changing input
Calculations |  |  | Do not change! | These cells should not be updated as they contain formulas
2.3 Tabs formatting
In the tab with dark green color are the results from the energy system analysis and LCOE calculation presented
In the tabs with light green color are the data on energy production units presented
In the tabs with blue color are the data on energy networks presented
In the tabs with grey color are data on miscellaneous non energy related technologies presented
In the tabs with red color are various energy system planning and operation models presented
2.4 Nomenclature
Abbreviation |  |  |  | Units
CO2 |  | Carbon dioxid |  | W | Watt
CH4 |  | Methan |  | kW | Kilowatt
N2O |  | Nitrogen oxid |  | MW | Megawatt
SO2 |  | Sulphur oxide |  | MW-e | Megawatt-el
NOx |  | Nitrogen oxids |  | MW-h | Megawatt-heating
PM2.5 |  | Particles |  | MW-c | Megawatt-cooling
ATES |  | Aquifer Thermal Energy Storage |  | MW-f | Megawatt-fuel
# |  | Number |  | Wh | Watt-hours
|  |  |  | kWh | Kilowatt-hours
|  |  |  | MWh | Megawatt-hours
|  |  |  | m | Meter
|  |  |  | m2 | Squaremeter
|  |  |  | m3 | Cubicmeter
|  |  |  | K | Kelvin
|  |  |  | oC | Degree celcius
|  |  |  | g | Gram
|  |  |  | kg | Kilogram
|  |  |  | ton | Tonnes
|  |  |  | mil. | Million
2.5 References
[1] | Energistyrelsen and Energinet.dk: Technology catalogue, 2019
https://ens.dk/service/fremskrivninger-analyser-modeller/teknologikataloger
[2] | Energistyrelsen and Energinet.dk: Technology catalogue for individual heating plants, 2018
https://ens.dk/service/fremskrivninger-analyser-modeller/teknologikataloger/teknologikatalog-individuelle
[3] | Energistyrelsen and Energinet.dk: Technology catalogue for energy storage, 2018
https://ens.dk/service/fremskrivninger-analyser-modeller/teknologikataloger/teknologikatalog-energilagring
[4] | Energinet.dk: Analysis assumptions, 2019
https://ens.dk/service/fremskrivninger-analyser-modeller/analyseforudsaetninger-til-energinet
[5] | Energistyrelsen: Socio-economic analysis methodology and assumptions, 2019
https://ens.dk/service/fremskrivninger-analyser-modeller/samfundsoekonomiske-analysemetoder
[6] | Thomson Reuters Eikon (Prices downloaded July 11, 2019)
https://eikon.thomsonreuters.com/index.html
[7] | IEA, World Energy Outlook, 2017
https://www.iea.org/weo2017/
[8] | European Environmental Agency, Costs of air pollution from European industrial facilities 2008-2012, 2014
https://www.eea.europa.eu/publications/costs-of-air-pollution-2008-2012
[9] | Dansk Energi, Electricity price outlook, 2019
https://www.danskenergi.dk/udgivelser/elpris-outlook-2019
[10] | Big Ladder Software, NZP/SMPL Tool, 2019
[11] | MIT, LL ERA Tool, 2019
[12] | NREL, REopt Tool, 2019
[13] | US Department of Energy, CHP factsheets, 2019
https://www.energy.gov/eere/amo/publications-0
Industrial knowledge from energy planning projects
[14] | Ramboll
[15] | EATON
[16] | Schneider Electric
[17] | TKDA
[18] | GEF Engineering
[19] | International Energy Association
[20] | US Army Corps of Engineers

## 2.1 Matrix
| Classification System |  |  |  |  | Case |  | District heating |  |  |  | District cooling |  | Renewable energy |  |  |  | CHP |  |  |  | E2H & E2C |  |  |  | Boiler |  |  |  | Storage |  |  | Resiliency |  |  |  | Dropdown list
System design and case number | Type of example | Spatial location | Buildings to be supplied from the outside with ... | No. of example | Indexation | Case number (Task B) | Energy system example (Task C) | Steam system | District heating system (160/70) | District heating system (110/80/50) | District heating system (70/60/40) | High temperature cooling 10/15 | District cooling system (5/10) | Solar Heating | Deep geothermal | Solar PV | Wind turbine | Oil CHP | Gas CHP | Biomass CHP | Waste CHP | Electric chiller | Electric heat pump | Absorption heat pump | Electric boiler | Oil boiler | Gas boiler | Biomass boiler | Waste boiler | Thermal tank storage | Cold storage | Thermal pit storage | Security 0 to 10 | Fuel 0 to 10 | Description, draft to be considered, and explained in detail in section on system design |  | Digit 1 | Digit 2 | Digit 3 | Digit 4
1 | Best practice examples | At community level | Power + heating | Example 1 | 2.3.1.1 | --- | Arctic Climate | X | --- | --- | --- | --- | --- | --- | --- | --- | --- | X | --- | --- | --- | --- | --- | --- | --- | X | --- | --- | --- | --- | --- | --- | 0 | 1 | Risk of break down and fuel shortage | 1 | Solutions for generation within the community (on community, cluster, building level or combination) | At building level | Power + heating | Example 1
2 | Best practice examples | Combination | Power + heating | Example 2 | 2.4.1.2 | --- | Mild climate (w/ grid connection) | --- | --- | --- | X | X | --- | --- | --- | --- | --- | --- | X | --- | --- | X | X | --- | X | --- | X | --- | --- | X | X | --- | 10 | 10 | Reliable heating cooling and power, smart use of electricity | 2 | Best practice examples | At cluster level | Power + cooling | Example 2
3 | Best practice examples | At community level | Power + heating + cooling | Example 3 | 2.3.4.3 | --- | Mild climate (wo/ grid connection) | --- | --- | --- | X | X | --- | X | --- | --- | --- | X | --- | --- | --- | X | X | --- | X | X | --- | --- | --- | X | X | --- | 10 | 10 | Reliable heating cooling and power, smart use of electricity | 3 | Generation outside the community | At community level | Power | Example 3
4 | Best practice examples | At community level | Power + heating + cooling | Example 4 | 2.3.4.4 | --- | Mild climate (wo/ grid connection, w/ wind energy) | --- | --- | --- | X | X | --- | X | --- | --- | X | X | --- | --- | --- | X | X | --- | X | X | --- | --- | --- | X | X | X | 10 | 10 | Reliable heating cooling and power, smart use of electricity | 4 | Solutions for remote locations (island solutions) | Combination | Power + heating + cooling | Example 4
5 | Best practice examples | At community level | Power + heating + cooling | Example 5 | 2.3.4.5 | --- | Tropic climate | --- | --- | --- | X | X | --- | --- | --- | --- | --- | --- | --- | X | X | X | X | X | --- | --- | X | --- | --- | X | X | --- | 10 | 10 | Large city, Reliable heating cooling and power, smart use of electricity | 5 | Systems with electrical enhancement |  |  | Example 5
6 | [35 empty] | 6 |  |  |  | Example 6
7 | [35 empty] | 7 |  |  |  | Example 7
8 | [35 empty] | 8 |  |  |  | Example 8
9 | [35 empty] | 9 |  |  |  | Example 9
10 | [35 empty] | 10 |  |  |  | Example 10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
---
1 | Best practice examples | At community level | Power + heating | Example 1 | 2.3.1.1 | Quanaaq, Greenland | --- | --- | --- | X | --- | --- | --- | --- | --- | --- | --- | X | --- | --- | --- | --- | --- | --- | --- | X | --- | --- | X | --- | --- | ---
2 | Best practice examples | At community level | Power + heating + cooling | Example 1 | 2.3.4.1 | Taarnby district heating | --- | --- | --- | X | --- | --- | --- | --- | --- | --- | --- | --- | --- | X | X | --- | --- | --- | --- | --- | X | X | --- | X | --- | ---
3 | Best practice examples | At community level | Power + heating + cooling | Example 2 | 2.3.4.2 | Taarnby district cooling | --- | --- | --- | X | X | X | --- | --- | --- | --- | --- | --- | X | X | X | --- | X | --- | --- | --- | --- | --- | --- | X | X | ---
4 | Best practice examples | Combination | Power + heating + cooling | Example 2 | 2.4.4.2 | Greater Copenhagen district heating | --- | --- | --- | X | X | X | X | --- | --- | --- | --- | --- | X | X | X | --- | X | --- | X | --- | X | --- | --- | X | X | (X)
5 | Best practice examples | At community level | Power + heating | Example 1 | 2.3.1.1 | Gram district heating | --- | --- | --- | --- | X | --- | --- | --- | --- | --- | --- | --- | X | --- | --- | --- | X | --- | X | --- | X | --- | --- | X | --- | X
6 | Best practice examples | At community level | Power + heating + cooling | Example 2 | 2.3.4.2 | Favrholm urban development | --- | --- | --- | --- | X | X | --- | --- | --- | --- | --- | --- | --- | X | --- | --- | X | --- | --- | --- | X | --- | --- | X | X | ---
7 | Best practice examples | At community level | Power + heating + cooling | Example 4 | 2.3.4.4 | University of California Davis | --- | X | --- | --- | --- | --- | X | --- | --- | --- | --- | --- | X | --- | --- | --- | --- | --- | --- | --- | X | --- | --- | --- | --- | --- | 7 | 9 | Laxmi to update the energy system structure (inputs)
8 | Best practice examples | At community level | Power + heating + cooling | Example 5 | 2.3.4.5 | University of Texas at Austin | --- | X | --- | --- | --- | --- | X | --- | --- | --- | --- | --- | X | --- | --- | --- | --- | --- | --- | --- | X | --- | --- | --- | --- | --- | 7 | 9 | Laxmi to update the energy system structure (inputs)
9 | Best practice examples | At community level | Power + heating | Example 2 | 2.3.1.2 | University of British Columbia | --- | X | --- | --- | --- | --- | X | --- | --- | --- | --- | --- | X | --- | --- | --- | --- | --- | --- | --- | X | --- | --- | --- | --- | --- | 7 | 9 | Laxmi to update the energy system structure (inputs)
---
---
---
---
---
---
---
---
---
---
---
---
---
---
---
---
---
---
This table show combinations of environment and need for energy services and resilience
For each combination of environment and demand there may be one or more system design cases in task C, which is a composition of technologies
For each system design case there may be reference to one or more case studies in task B, which demonstrate one or more of the key technologies or all

## 3. Energy systems
Back to user guide
3. Energy systems
Figure 3-1: The smart (integrated) energy system
List of contents
3. Energy systems
3.1 Arctic climate
3.2 Tropic climate
3.3 Mild climate
3.3.1 Energy system analysis (w/ grid connection)
3.3.2 Energy system analysis (wo/ grid connection)
3.3.3 Energy system analysis (wo/ grid connection, w/ wind energy)
3.4 New energy system 1
3.5 New energy system 2
Assumptions applied (selected in 3.1 LCOE results)
Discount rate | 5% | %
Calculation period | 1
Start year of calculation | 2022
Electricity price development | Green
Fuel and CO2 price scenario | Sustainable development scenario
Country | EU
Currency abbreviation | EUR
Currency factor | 1
Equipment | 1
Installation | 1
3.1 Arctic climate
3.1.1 Energy system analysis
Table 3-1: District heating demand
Unit
Annual heat demand | MWh-h | 7500
Heat storage tank | MWh-h | 15
Efficient storage volume | m3 | 287.3563
Supply temperature | oC | 90
Return temperature | oC | 45
Table 3-2: Electricity demand
Unit
Annual electricity demand | MWh-e | 2500
Table 3-3: Production units
Unit
Diesel engine | MW-e | 1.5
Electric efficiency (diesel engine) | % | 36%
Heat efficiency (diesel engine) | % | 50%
Diesel boiler | MW-h | 2
Heat efficiency (diesel boiler) | % | 90%
Table 3-4: Analysis assumptions
Unit
Oil | EUR/MWh | 41.3568
CO2-tax | EUR/ton | 44.7377
O&M (diesel engine) | EUR/MWh-e | 5.4
O&M (diesel boiler) | EUR/MWh-h | 1.1
CO2 emission | kg/GJ | 74
Heating value (oil) | GJ/ton | 43
Table 3-5: Production distribution
| MWh-e | % | MWh-h | % | MWh-f | Ton CO2
Diesel engine | 2500 | 100% | 3472.2222 | 46.3% | 6944.4444 | 1850
Diesel boiler | 0 | 0% | 4027.7778 | 53.7% | 4475.3086 | 1192.2222
Total | 2500 | 100% | 7500 | 100% | 11419.7531 | 3042.2222
Table 3-6: Production costs
| Fuel | O&M | CO2 | Total
| EUR | EUR | EUR | mEUR
Diesel engine | 287200 | 13500 | 82764.6912 | 0.38346
Diesel boiler | 185084.4444 | 4430.5556 | 53337.2455 | 0.24285
Total | 472284.4444 | 17930.5556 | 136101.9367 | 0.62632
Figure 3-3: District heating production
Figure 3-4: Electricity production
3.2 Tropic climate
3.2.1 Energy system analysis
Table 3-7: District cooling demand |  |  |  | Table 3-10: Analysis assumptions
| Unit | [6 empty] | Unit
Annual cooling demand | MWh-c | 40000 |  | Natural gas |  |  |  | EUR/MWh | 22.8672
Chilled water tank capacity | MWh-c | 40 |  | Electricity |  |  |  | EUR/MWh-e | 60.8137
Efficient storage volume | m3 | 2873.5632 |  | CO2-tax |  |  |  | EUR/ton | 44.7377
Supply temperature | oC | 8 |  | O&M (chiller) |  |  |  | EUR/MWh-c | 4.8
Return temperature | oC | 20 |  | O&M (heat pump) |  |  |  | EUR/MWh-h | 3.2
|  |  |  | O&M (gas boiler) |  |  |  | EUR/MWh-h | 1.1
Table 3-8: District heating demand |  |  |  | CO2 emission (electricity) |  |  |  | kg/GJ | 37.7778
| Unit |  |  | CO2 emission (natural gas) |  |  |  | kg/GJ | 57
Annual heat demand | MWh-h | 20000 |  | Heating value (natural gas) |  |  |  | GJ/1000Nm3 | 39.53
Heat storage tank | MWh-h | 20
Efficient storage volume | m3 | 383.1418
Supply temperature | oC | 90
Return temperature | oC | 45
Table 3-9: Production units
| MW-h | MW-c | Eff. (%)
Chiller |  | 10 | 350%
Heat pump | 9 | 6 | 300%
Gas boiler | 15 |  | 90%
Table 3-11: Production distribution
| MWh-c | % | MWh-h | % | MWh-f | Ton CO2
Chiller | 30915.6 | 77.29% | 0 | 0% | 8833.0286 | 1201.2919
Heat pump | 9084.4 | 22.71% | 13626.7 | 68.13% | 4542.2333 | 617.7437
Gas boiler | 0 | 0% | 6373 | 31.87% | 7081.1111 | 1453.044
Total | 40000 | 100% | 19999.7 | 100% | --- | 3272.0796
Table 3-12: Production costs
| Fuel | O&M | CO2 | Total
| EUR | EUR | EUR | mEUR
Chiller | 537169.5852 | 148394.88 | 53743.0011 | 0.73931
Heat pump | 276230.2393 | 43605.44 | 27636.4159 | 0.34747
Gas boiler | 161925.184 | 7010.3 | 65005.8043 | 0.23394
Total | 975325.0085 | 199010.62 | 146385.2212 | 1.3207
Figure 3-6: District heating production
Figure 3-7: District cooling production
3.3 Mild climate
3.3.1 Energy system analysis (w/ grid connection)
Table 3-13: District cooling demand
Unit
Annual cooling demand | MWh-c | 20000
Chilled water tank capacity | MWh-c | 15
Efficient storage volume | m3 | 1077.5862
Supply temperature | oC | 8
Return temperature | oC | 20
Table 3-14: District heating demand
Unit
Annual heat demand | MWh-h | 50000
Heat storage tank | MWh-h | 100
Efficient storage volume | m3 | 1915.7088
Supply temperature | oC | 90
Return temperature | oC | 45
Table 3-15: Production units
| MW-h | MW-c | MW-e | Eff. (%)
Chiller |  | 15 |  | 500%
Heat pump | 6 | 4 |  | 300%
Electric boiler | 6 |  |  | 100%
Gas engine | 10 |  | 8 | 90%
Gas boiler | 20 |  |  | 90%
Table 3-16: Analysis assumptions
| Unit | Buy | Sell
Natural gas | EUR/MWh | 22.8672
Electricity | EUR/MWh-e | 60.8137 | 60.8137
CO2-tax | EUR/ton | 44.7377
O&M (chiller) | EUR/MWh-c | 4.8
O&M (heat pump) | EUR/MWh-h | 3.2
O&M (electric boiler) | EUR/MWh-h | 0.9
O&M (gas engine) | EUR/MWh-e | 5.4
O&M (gas boiler) | EUR/MWh-h | 1.1
CO2 emission (electricity) | kg/GJ | 37.7778
CO2 emission (natural gas) | kg/GJ | 57
Table 3-17: Production distribution
| MWh-c | % | MWh-h | % | MWh-e | % | MWh-f | Ton CO2
Chiller | 12283.2 | 61.42% | 0 | 0% | 0 | 0% | 2456.64 | 334.103
Heat pump | 7716.8 | 38.58% | 34767.4 | 69.53% | 0 | 0% | 11589.1333 | 1576.1221
Electric boiler | 0 | 0% | 3451.9 | 6.904% | 0 | 0% | 3451.9 | 469.4584
Gas engine | 0 | 0% | 6350 | 12.7% | 5080 | 100% | 12700 | 2606.04
Gas boiler | 0 | 0% | 5430.6 | 10.86% | 0 | 0% | 6034 | 1238.1768
Total | 20000 | 100% | 49999.9 | 100% | 5080 | 100% | --- | 6223.9004
Table 3-18: Production costs
| Fuel | O&M | CO2 | Total
| EUR | EUR | EUR | mEUR
Chiller | 149397.4891 | 58959.36 | 14946.9919 | 0.2233
Heat pump | 704778.6493 | 111255.68 | 70512.0333 | 0.88655
Electric boiler | 209922.9813 | 3106.71 | 21002.4754 | 0.23403
Gas engine | 286715.1279 | 27432 | 116588.1599 | 0.43074
Gas boiler | 137980.6848 | 5973.66 | 55393.1462 | 0.19935
Total | 1488794.9324 | 206727.41 | 278442.8068 | 1.974
Figure 3-8: District heating daily production (with storage)
Figure 3-9: District cooling production
3.3.2 Energy system analysis (wo/ grid connection)
Table 3-19: District cooling demand
Unit
Annual cooling demand | MWh-c | 20000
Chilled water tank capacity | MWh-c | 15
Efficient storage volume | m3 | 1077.5862
Supply temperature | oC | 8
Return temperature | oC | 20
Table 3-20: District heating demand
Unit
Annual heat demand | MWh-h | 50000
Heat storage tank | MWh-h | 100
Efficient storage volume | m3 | 1915.7088
Supply temperature | oC | 90
Return temperature | oC | 45
Table 3-21: Electricity demand
Unit
Annual electricity demand | MWh-e | 20000
Table 3-22: Production units
| MW-h | MW-c | MW-e | Eff. (%)
Chiller |  | 15 |  | 500%
Heat pump | 6 | 4 |  | 300%
Diesel engine | 20 |  | 16 | 90%
Diesel boiler | 20 |  |  | 90%
Table 3-23: Analysis assumptions
Unit
Oil | EUR/MWh | 41.3568
CO2-tax | EUR/ton | 44.7377
O&M (chiller) | EUR/MWh-c | 4.8
O&M (heat pump) | EUR/MWh-h | 3.2
O&M (diesel engine) | EUR/MWh-e | 5.4
O&M (diesel boiler) | EUR/MWh-h | 1.1
CO2 emission (diesel) | kg/GJ | 74
Table 3-24: Production distribution
| MWh-c | % | MWh-h | % | MWh-e | % | MWh-f | Ton CO2
Chiller | 5239.1 | 26.2% | 0 | 0% | 0 | 0% | 0 | 0
Heat pump | 14760.9 | 73.8% | 22141.3 | 44.28% | 0 | 0% | 0 | 0
Diesel engine | 0 | 0% | 35600.8 | 71.2% | 28480.7 | 100% | 71201.6667 | 18968.124
Diesel boiler | 0 | 0% | 20727.9 | 41.46% | 0 | 0% | 23031 | 6135.4584
Heat rejection | 0 | 0% | -28470 | -56.94% | 0 | 0% | 0 | 0
Total | 20000 | 100% | 50000 | 100% | 28480.7 | 100% | --- | 25103.5824
Table 3-25: Production costs
| Fuel | O&M | CO2 | Total
| EUR | EUR | EUR | mEUR
Chiller | 0 | 25147.68 | 0 | 0.025148
Heat pump | 0 | 70852.16 | 0 | 0.070852
Diesel engine | 2944673.088 | 153795.78 | 848589.6896 | 3.9471
Diesel boiler | 952488.4608 | 22800.69 | 274486.1189 | 1.2498
Total | 3897161.5488 | 272596.31 | 1123075.8085 | 5.2928
Figure 3-10: District heating production
Figure 3-11: District cooling production
Figure 3-12: Electricity production
3.3.3 Energy system analysis (wo/ grid connection, w/ wind energy)
Table 3-26: Production units
| MW-h | MW-c | MW-e | Eff. (%)
Wind turbine |  |  | 2
Table 3-27: Analysis assumptions
Unit
O&M (wind turbine) | EUR/MWh-e | 1.5
Table 3-28: Production distribution
| MWh-c | % | MWh-h | % | MWh-e | % | MWh-f | Ton CO2
Chiller | 5239.1 | 26.2% | 0 | 0% | 0 | 0% | 0 | 0
Heat pump | 14760.9 | 73.8% | 22141.3 | 44.28% | 0 | 0% | 0 | 0
Diesel engine | 0 | 0% | 30821.8 | 61.64% | 24657.4 | 86.58% | 61643.5556 | 16421.8432
Diesel boiler | 0 | 0% | 23423.7 | 46.85% | 0 | 0% | 26026.3333 | 6933.4152
Wind turbine | 0 | 0% | 0 | 0% | 3823.2 | 13.42% | 0 | 0
Heat rejection | 0 | 0% | -26386.8 | -52.77% | 0 | 0% | 0 | 0
Total | 20000 | 100% | 50000 | 100% | 28480.6 | 100% | --- | 23355.2584
Table 3-29: Production costs
| Fuel | O&M | CO2 | Total
| EUR | EUR | EUR | mEUR
Chiller | 0 | 25147.68 | 0 | 0.025148
Heat pump | 0 | 70852.16 | 0 | 0.070852
Diesel engine | 2549380.1984 | 133149.96 | 734675.0171 | 3.4172
Diesel boiler | 1076365.8624 | 25766.07 | 310184.8476 | 1.4123
Wind turbine | 0 | 5734.8 | 0 | 0.0057348
Total | 3625746.0608 | 260650.67 | 1044859.8647 | 4.9313
Figure 3-13: District heating production
Figure 3-14: District cooling production
Figure 3-15: Electricity production
3.4 New energy system 1
3.4.1 Energy system analysis
3.5 New energy system 2
3.5.1 Energy system analysis
In essence, a smart energy system builds on energy flows from and between four energy systems. Each system must ensure an intelligent interaction between production, conversion, storage and consumption in the different forms of energy, and an intelligent interaction must also be ensured between the four energy systems. The primary energy flows in the systems move from production for conversion, storage and final consumption. The production contains in principle all resources in a 100% VRES-based energy system and therefore contributes energy to the four systems.
Two key elements of a smart energy system are - unlike the conventional energy system -
respectively: the conversion of primary energy resources to other uses, and the storage of energy, which ensures the necessary flexibility in an energy system with fluctuating energy sources. Conversion ensures the interaction between the four systems, ie. when resources are to be converted from an energy form that originates from one system into a form that can be used in another system. The conversion thus contributes partly to utilizing a given energy source optimally (such as the conversion from electricity to heat), and partly to create flexibility in a smart energy system, from one source of energy at given times replaced by another source of energy. For example, a heat pump can take off power from the electrical system and deliver heat and cooling to respectively. district heating system and district cooling system, and a gas engine can extract gas from the gas system and supply electricity and district heating.
The gas storage line creates additional flexibility by building energy reserves that can be provided to every systems in a smart energy system during peak periods, in periods of lack of a given energy source or in periods of very high electricity prices. The final point is the consumer link, as of course are the primary buyers of energy. However, in a smart energy context it is important to note that the consumer link can also act as a flexible component by regulating up or down for consumption, or by storing energy in, for example, electric cars or in the buildings' heat storage.
The many and very varied definitions of smart energy systems, and the many components, which is part of a fully-fledged smart energy system as shown above, involves the risk that it can be difficult to identify - and thus regulate and implement - the key elements of a smart energy system. Such a system must not be fully designed at the same time, but can and should be gradually expanded as the continuous phasing-in of fluctuating energy (in Denmark especially wind power), and - especially in the first stages - with a focus on the core elements necessary to cope with such increasing amounts of fluctuation.
Certain elements of a smart energy system are crucial to the ability to record and apply large amounts of fluctuating VRES in a socio-economically appropriate way - while other elements are less crucial (because they have, for example, a limited overall effect in a smart energy system). Certain elements are technologically and economically mature for implementation within a shorter number of years - while other elements are not yet technologically or economically mature.
The challenge is to establish campusses and settlements in the arctic areas. The temperature can be as low as -40 dgr.C, and all urban infrastructure has to be very reliable and protected.
There can be long distance to renewable energy and the nearest power grid. Therefore island operation of the power grid and the resources, in terms of equipment and light oil can only be shipped to the settlement during a few summer months.
This case demonstrates how the whole system can be established in an efficient way based on ligh oil and prepared for integration of wind energy and heat from waste incineration. All buildings are interconnected with a district heating network, situated above ground in infrastructure grids which contains water, waste water, power and tele cables. This is a very resilient construction for the artic areas.
Yet, there are a number of barriers and challenges as well as risks involved in implementing large scale VRES in arctic areas. The following list is based on experience from Greenland. The most important barriers and challenges are as follows:
1. Pricing of electricity and heat takes place politically. At present, pricing of heat does not provide a private economic incentive to choose district heating rather than individual heating. In addition, the pricing foundation is not insufficiently transparent to allow the policies to make decisions that support the policy objectives;
2. Goods such as "water" for hydropower, "waste" of waste heat and "residual heat" in electricity generation should be recognized with a value of 0 $., Which should be reflected in the district heating price;
3. Lack of evaluation and follow-up of operations in individual cities / towns means ignoring the possibilities for increased residual heat utilization and not following up energy efficiency measures;
4. The complexity of energy systems increases by implementing large scale VRES, which increases the need to enhance computer-based measurement, management, control and monitoring.
5. Before major investments are made in VRES, experience with VRES technology under arctic conditions should be carefully evaluated, including years of experience at the Center for Arctic Technology (ARTEK).
The challenge is to establish campusses and settlements in a tropic climate. The temperature can be up to 40-50 dgr. C in the summer causing a need for cooling.
There can be island energy systems (for example on an island), but typically there are transmission lines to a national/international power grid. This case demonstrates how a local energy system consisting of district heating and district cooling can be established.
The challenge is to establish campusses and settlements in a mild climate. The temperature can be up to 30 dgr. C in the summer causing a need for cooling, and down to - 20 dgr. C in the winter causing a need for heating.
There can be island energy systems (for example on an island), but typically there are transmission lines to a national/international power grid.
We set-up three different cases:
1. Grid connected systems
2. Not grid connected system
3. Not grid connected system with a wind turbine
The assumptions for the energy system analysis are shown in Table 3-1 to Table 3-4.
We perform the energy system analysis using prices forecasted for 2020, and includes a CO2 tax.
We have used a scaled electricity consumtpion profile from Denmark. This is probably not completely right, but provides an opportunity for initial assessment.
The production distribution is calculated in Table 3-5.
The production costs are calculated in Table 3-6.
The district heating and electricity productions on an hourly basis are shown on Figure 3-2 and 3-3. The production distributions are calculated using EnergyPRO.
The assumptions for the energy system analysis are shown in Table 3-13 to Table 3-16.
We perform the energy system analysis using prices forecasted for 2020, and includes a CO2 tax.
We apply an electricity price from Denmark.
The production distribution is calculated in Table 3-17.
The production costs are calculated in Table 3-18.
The district heating and district cooling productions on an hourly basis are shown on Figure 3-8 to 3-9. The production distributions are calculated using EnergyPRO.
The assumptions for the energy system analysis are shown in Table 3-19 to Table 3-23.
We perform the energy system analysis using prices forecasted for 2020, and includes a CO2 tax.
We have used a scaled electricity consumtpion profile from Denmark.
The production distribution is calculated in Table 3-24.
The production costs are calculated in Table 3-25.
The district heating, district cooling and electricity productions on an hourly basis are shown on Figure 3-10 to 3-12. The production distributions are calculated using EnergyPRO.
The assumptions for the energy system analysis are shown in Table 3-7 to Table 3-10. We perform the energy system analysis using prices forecasted for 2020, and includes a CO2 tax.
We apply an electricity price from Denmark.
The production distribution is calculated in Table 3-11.
The production costs are calculated in Table 3-12.
The district heating and cooling productions on an hourly basis are shown on Figure 3-5 and 3-6. The production distributions are calculated using EnergyPRO.
The assumptions for the energy system analysis are shown in Table 3-19 to Table 3-23 and Table 3-26 to 3-27. We perform the energy system analysis using prices forecasted for 2020, and includes a CO2 tax. We have used a scaled electricity consumtpion profile from Denmark. The production distribution is calculated in Table 3-28. The production costs are calculated in Table 3-29. The district heating, district cooling and electricity productions on an hourly basis are shown on Figure 3-13 to 3-15. The production distributions are calculated using EnergyPRO.

## 3.1 LCOE results
3.1 LCOE Results
3.1.1 Input
Discount rate |  | 5% | %
Calculation period |  | 1
Start year of calculation |  | 2022
Electricity price development |  | Green
Expected solar thermal production |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  | Sustainable development scenario
Country |  | EU
Table 1: LCOE calculation input for district heating technologies
District heating | Technologies |  | Solar thermal size | Heat coverage by solar |  | Storage size |  | Storage type
Unit |  |  | m2 panel | % of total demand |  | m3 storage |  | ---
Technology 1 | Solar - large |  | 45000 | 65% |  | 120937.5 |  | Pit thermal storage
Technology 2 | Geothermal |  |  |  |  | 0
Technology 3 | Boiler - straw |  |  |  |  | 0
Technology 4 | Large CHP - wood pellets |  |  |  |  | 0
Technology 5 | Boiler - natural gas |  |  |  |  | 0
Technology 6 | Small CHP - wood pellets |  |  |  |  | 0
Technology 7 | Electric heat pump |  |  |  |  | 0
Technology 8 | Boiler - coal |  |  |  |  | 0
Technology 9 | Boiler - oil |  |  |  |  | 0
Technology 10 | Large CHP - straw |  |  |  |  | 0
Table 2: LCOE calculation input for individual technologies
Individual | Technologies
Unit
Technology 1 | Solar heating
Technology 2 | Gas boiler
Technology 3 | Oil boiler
Technology 4 | Wood pellet boiler
Technology 5 | Wood stove
Technology 6 | Heat pump - air to air
Technology 7 | Heat pump - air to water
Technology 8 | Heat pump - brine to water
Technology 9 | Gas driven heat pump - brine to water
Technology 10 | Electric heating
Table 3: Equipment and installation factors per country (relative to Europe)
Country | Equipment | Installation
Australia | 1 | 1.2
Brazil | 0.9 | 0.5
Canada | 1.2 | 1
China | 0.7 | 0.5
Denmark | 1 | 1
EU | 1 | 1
Great Britain | 1 | 1.2
India | 0.8 | 0.6
Indonesia | 0.8 | 0.6
Japan | 1 | 1.2
Kazakhstan | 0.7 | 0.6
Malaysia | 0.8 | 0.6
Mexico | 0.9 | 0.8
Philippines | 0.8 | 0.6
Russia | 0.8 | 0.7
Singapore | 1.2 | 1.3
South Africa | 0.8 | 0.7
Sweden | 1 | 1
Switzerland | 1 | 1
Turkey | 0.9 | 0.8
Ukraine | 0.8 | 0.7
USA | 1 | 1.2
Include/exclude
Capital cost | TRUE
Fuel cost | TRUE
O&M cost | TRUE
Electricity sale revenue | TRUE
DH sale revenue | TRUE
CO2 emissions | TRUE
Climate externalities | TRUE
Air pollution | TRUE
3.1.2 LCOE results
Figure 1: LCOE for district heating producing technologies
Figure 2: LCOE for electricity producing technologies
Figure 3: LCOE for individual heat producing technologies
3.1.3 LCOE results for boilers
|  |  | Unit | Large CHP - straw | Boiler - waste | Boiler - wood chips | Boiler - wood pellets | Boiler - straw | Boiler - natural gas | Boiler - oil | Electric boiler | Boiler - coal
Heat production cost | Capital cost |  | EUR/MWh-h | 27.4744
| Fixed O&M |  | EUR/MWh-h | 14.2247
| Var O&M |  | EUR/MWh-h | 0.86556 | 5.5 | 1 | 0.5 | 0.6 | 1.1 | 1.1 | 0.9 | 1.6 | 0 | 0
| Fuel cost |  | EUR/MWh-h | 31.7707 | -17.1429 | 21.9465 | 32.0755 | 21.1805 | 22.2012 | 40.1522 | 13.4 | 10.504 | 0 | 0
| CO2 |  | EUR/MWh-h | 0 | 5.6753 | 0 | 0 | 0 | 8.9128 | 11.571 | 6.0843 | 16.8214 | 0 | 0
| CH4 |  | EUR/MWh-h | 0 | 1.5339e-05 | 0.0015405 | 0 | 0.0017369 | 0.00046909 | 0 | 0.09709 | 0.00026843 | 0 | 0
| N2O |  | EUR/MWh-h | 0.00023685 | 0.00015339 | 0.00042015 | 0.00016106 | 0.00047369 | 0.00015636 | 0 | 0.033755 | 0.00014316 | 0 | 0
| SO2 |  | EUR/MWh-h | 0.00076235 | 3.7029e-05 | 0 | 0 | 0.00050824 | 0.020971 | 0.034951 | 1.3166 | 0.4 | 0 | 0
| NOX |  | EUR/MWh-h | 3.5471 | 2.2971 | 1.9722 | 1.944 | 2.5412 | 0.31456 | 0.87379 | 1.7434 | 1.4 | 0 | 0
| PM2.5 |  | EUR/MWh-h | 0.079412 | 0.051429 | 0.046957 | 0.054 | 0.052941 | 0 | 0.034951 | 0.050638 | 0.1 | 0 | 0
| Electricity revenue |  | EUR/MWh-h | -36.0605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total LCOE | Levelized cost |  | EUR/MWh-h | 41.9024 | 26.1588 | 41.199 | 51.3908 | 47.2669 | 44.9644 | 66.1812 | 89.1577 | 44.7349 | 0 | 0
|  |  | Unit | Boiler - waste | Boiler - wood chips | Boiler - wood pellets | Boiler - straw | Boiler - natural gas | Boiler - oil | Electric boiler | Boiler - coal | 0 | 0
Heat production cost | Capital cost |  | EUR/MWh-h | 18.549 | 9.7914 | 10.2172 | 12.6295 | 8.5143 | 8.5143 | 60.1819 | 9.6291 | 0 | 0
| Fuel cost |  | EUR/MWh-h | -17.1429 | 21.9465 | 32.0755 | 21.1805 | 22.2012 | 40.1522 | 13.4 | 10.504 | 0 | 0
| O&M cost |  | EUR/MWh-h | 16.7286 | 7.44 | 7.1 | 10.86 | 5 | 5 | 6.25 | 5.88 | 0 | 0
| CO2 emissions |  | EUR/MWh-h | 5.6753 | 0 | 0 | 0 | 8.9128 | 11.571 | 6.0843 | 16.8214 | 0 | 0
| Climate externalities |  | EUR/MWh-h | 0.00016872 | 0.0019607 | 0.00016106 | 0.0022106 | 0.00062546 | 0 | 0.13085 | 0.00041159 | 0 | 0
| Air pollution |  | EUR/MWh-h | 2.3486 | 2.0191 | 1.998 | 2.5946 | 0.33553 | 0.94369 | 3.1106 | 1.9 | 0 | 0
| Electricity sale revenue |  | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total LCOE | Total LCOE |  | EUR/MWh-h | 26.1588 | 41.199 | 51.3908 | 47.2669 | 44.9644 | 66.1812 | 89.1577 | 44.7349 | 0 | 0
|  |  |  | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1
|  |  | Unit | 0 | 0 | Boiler - waste | Boiler - wood chips | Boiler - coal | Boiler - natural gas | Boiler - straw | Boiler - wood pellets | Boiler - oil | Electric boiler
Heat production cost | Capital cost |  | EUR/MWh-h | 0 | 0 | 18.549 | 9.7914 | 9.6291 | 8.5143 | 12.6295 | 10.2172 | 8.5143 | 60.1819
| Fuel cost |  | EUR/MWh-h | 0 | 0 | -17.1429 | 21.9465 | 10.504 | 22.2012 | 21.1805 | 32.0755 | 40.1522 | 13.4
| O&M cost |  | EUR/MWh-h | 0 | 0 | 16.7286 | 7.44 | 5.88 | 5 | 10.86 | 7.1 | 5 | 6.25
| CO2 emissions |  | EUR/MWh-h | 0 | 0 | 5.6753 | 0 | 16.8214 | 8.9128 | 0 | 0 | 11.571 | 6.0843
| Climate externalities |  | EUR/MWh-h | 0 | 0 | 0.00016872 | 0.0019607 | 0.00041159 | 0.00062546 | 0.0022106 | 0.00016106 | 0 | 0.13085
| Air pollution |  | EUR/MWh-h | 0 | 0 | 2.3486 | 2.0191 | 1.9 | 0.33553 | 2.5946 | 1.998 | 0.94369 | 3.1106
| Electricity sale revenue |  | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total LCOE | Total LCOE |  | EUR/MWh-h | 0 | 0 | 26.1588 | 41.199 | 44.7349 | 44.9644 | 47.2669 | 51.3908 | 66.1812 | 89.1577
3.1.4 LCOE results for CHP plants
|  |  | Unit | Large CHP - straw | Medium CHP - waste | Large CHP - waste | Medium CHP - wood chips | Large CHP - wood chips | Medium CHP - wood pellets | Large CHP - wood pellets | Large CHP - straw | Large CHP - coal | Large CHP - coal - carbon capture | Large CHP - wood chips - carbon capture
Heat production cost | Capital cost |  | EUR/MWh-h | 27.4744
| Fixed O&M |  | EUR/MWh-h | 14.2247
| Var O&M |  | EUR/MWh-h | 0.86556 | 7.0312 | 7.311 | 1.3446 | 1.3897 | 0.75556 | 0.8 | 0.86556 | 2.4351 | 2.3191 | 1.0563
| Fuel cost |  | EUR/MWh-h | 31.7707 | -23.0769 | -23.0769 | 30.7786 | 30.7786 | 47.8739 | 50.1179 | 31.7707 | 18.9072 | 23.634 | 35.0534
| CO2 |  | EUR/MWh-h | 0 | 7.6398 | 7.6398 | 0 | 0 | 0 | 0 | 0 | 30.2785 | 3.7848 | 0
| CH4 |  | EUR/MWh-h | 0 | 2.0648e-05 | 2.0648e-05 | 0.00039282 | 0.00039282 | 0 | 0 | 0 | 0.00048317 | 0.00060396 | 0.00044738
| N2O |  | EUR/MWh-h | 0.00023685 | 0.00020648 | 0.00020648 | 0.00019641 | 0.0015713 | 0.00024038 | 0.00025165 | 0.00023685 | 0.00025769 | 0.00032211 | 0.0017895
| SO2 |  | EUR/MWh-h | 0.00076235 | 4.9846e-05 | 4.9846e-05 | 0 | 0 | 0 | 0 | 0.00076235 | 0.0011664 | 0.001458 | 0
| NOX |  | EUR/MWh-h | 3.5471 | 2.5846 | 2.5846 | 3.161 | 1.0537 | 3.3313 | 1.1812 | 3.5471 | 2.52 | 3.15 | 1.2
| PM2.5 |  | EUR/MWh-h | 0.079412 | 0.069231 | 0.069231 | 0.065854 | 0.065854 | 0.080597 | 0.084375 | 0.079412 | 0 | 0 | 0.075
| Electricity revenue |  | EUR/MWh-h | -36.0605 | -19.358 | -20.2904 | -28.0094 | -28.9479 | -38.1466 | -42.915 | -36.0605 | -72.0709 | -68.6362 | -23.8583
Total LCOE | Levelized cost |  | EUR/MWh-h | 41.9024 | 11.4716 | 5.4747 | 43.5245 | 35.3203 | 65.3101 | 47.134 | 41.9024 | 28.4816 | 48.3317 | 79.6272
|  |  | Unit | Medium CHP - waste | Large CHP - waste | Medium CHP - wood chips | Large CHP - wood chips | Medium CHP - wood pellets | Large CHP - wood pellets | Large CHP - straw | Large CHP - coal | Large CHP - coal - carbon capture | Large CHP - wood chips - carbon capture
Heat production cost | Capital cost |  | EUR/MWh-h | 25.942 | 23.3071 | 22.5956 | 22.0554 | 32.5856 | 27.1984 | 27.4744 | 37.733 | 66.5738 | 53.8432
| Fuel cost |  | EUR/MWh-h | -23.0769 | -23.0769 | 30.7786 | 30.7786 | 47.8739 | 50.1179 | 31.7707 | 18.9072 | 23.634 | 35.0534
| O&M cost |  | EUR/MWh-h | 17.6705 | 15.241 | 14.9323 | 10.3128 | 19.5852 | 11.4667 | 15.0903 | 11.112 | 19.8229 | 13.3117
| CO2 emissions |  | EUR/MWh-h | 7.6398 | 7.6398 | 0 | 0 | 0 | 0 | 0 | 30.2785 | 3.7848 | 0
| Climate externalities |  | EUR/MWh-h | 0.00022713 | 0.00022713 | 0.00058923 | 0.0019641 | 0.00024038 | 0.00025165 | 0.00023685 | 0.00074086 | 0.00092607 | 0.0022369
| Air pollution |  | EUR/MWh-h | 2.6539 | 2.6539 | 3.2268 | 1.1195 | 3.4119 | 1.2656 | 3.6272 | 2.5212 | 3.1515 | 1.275
| Electricity sale revenue |  | EUR/MWh-h | -19.358 | -20.2904 | -28.0094 | -28.9479 | -38.1466 | -42.915 | -36.0605 | -72.0709 | -68.6362 | -23.8583
Total LCOE | Total LCOE |  | EUR/MWh-h | 11.4716 | 5.4747 | 43.5245 | 35.3203 | 65.3101 | 47.134 | 41.9024 | 28.4816 | 48.3317 | 79.6272
|  |  |  | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1
|  |  | Unit | Large CHP - waste | Medium CHP - waste | Large CHP - coal | Large CHP - wood chips | Large CHP - straw | Medium CHP - wood chips | Large CHP - wood pellets | Large CHP - coal - carbon capture | Medium CHP - wood pellets | Large CHP - wood chips - carbon capture
Heat production cost | Capital cost |  | EUR/MWh-h | 23.3071 | 25.942 | 37.733 | 22.0554 | 27.4744 | 22.5956 | 27.1984 | 66.5738 | 32.5856 | 53.8432
| Fuel cost |  | EUR/MWh-h | -23.0769 | -23.0769 | 18.9072 | 30.7786 | 31.7707 | 30.7786 | 50.1179 | 23.634 | 47.8739 | 35.0534
| O&M cost |  | EUR/MWh-h | 15.241 | 17.6705 | 11.112 | 10.3128 | 15.0903 | 14.9323 | 11.4667 | 19.8229 | 19.5852 | 13.3117
| CO2 emissions |  | EUR/MWh-h | 7.6398 | 7.6398 | 30.2785 | 0 | 0 | 0 | 0 | 3.7848 | 0 | 0
| Climate externalities |  | EUR/MWh-h | 0.00022713 | 0.00022713 | 0.00074086 | 0.0019641 | 0.00023685 | 0.00058923 | 0.00025165 | 0.00092607 | 0.00024038 | 0.0022369
| Air pollution |  | EUR/MWh-h | 2.6539 | 2.6539 | 2.5212 | 1.1195 | 3.6272 | 3.2268 | 1.2656 | 3.1515 | 3.4119 | 1.275
| Electricity sale revenue |  | EUR/MWh-h | -20.2904 | -19.358 | -72.0709 | -28.9479 | -36.0605 | -28.0094 | -42.915 | -68.6362 | -38.1466 | -23.8583
Total LCOE | Total LCOE |  | EUR/MWh-h | 5.4747 | 11.4716 | 28.4816 | 35.3203 | 41.9024 | 43.5245 | 47.134 | 48.3317 | 65.3101 | 79.6272
3.1.5 LCOE results for heat pumps
|  |  | Unit | Large CHP - straw | Electric heat pump
Heat production cost | Capital cost |  | EUR/MWh-h | 27.4744
| Fixed O&M |  | EUR/MWh-h | 14.2247
| Var O&M |  | EUR/MWh-h | 0.86556 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel cost |  | EUR/MWh-h | 31.7707 | 3.7222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CO2 |  | EUR/MWh-h | 0 | 1.6901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 |  | EUR/MWh-h | 0 | 0.02697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O |  | EUR/MWh-h | 0.00023685 | 0.0093764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 |  | EUR/MWh-h | 0.00076235 | 0.36572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX |  | EUR/MWh-h | 3.5471 | 0.48428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PM2.5 |  | EUR/MWh-h | 0.079412 | 0.014066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electricity revenue |  | EUR/MWh-h | -36.0605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total LCOE | Levelized cost |  | EUR/MWh-h | 41.9024 | 25.7889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Unit | Electric heat pump | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat production cost | Capital cost |  | EUR/MWh-h | 15.6095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel cost |  | EUR/MWh-h | 3.7222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&M cost |  | EUR/MWh-h | 3.8667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CO2 emissions |  | EUR/MWh-h | 1.6901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Climate externalities |  | EUR/MWh-h | 0.036346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Air pollution |  | EUR/MWh-h | 0.86407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electricity sale revenue |  | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total LCOE | Total LCOE |  | EUR/MWh-h | 25.7889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1
|  |  | Unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Electric heat pump
Heat production cost | Capital cost |  | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6095
| Fuel cost |  | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7222
| O&M cost |  | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8667
| CO2 emissions |  | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6901
| Climate externalities |  | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036346
| Air pollution |  | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86407
| Electricity sale revenue |  | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total LCOE | Total LCOE |  | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.7889
3.1.6 LCOE results for renewable energy
|  |  | Unit | Large CHP - straw | Solar PV | Large onshore wind turbine
Heat production cost | Capital cost |  | EUR/MWh-h | 60.3096
| Fixed O&M |  | EUR/MWh-h | 31.225
| Var O&M |  | EUR/MWh-h | 1.9 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel cost |  | EUR/MWh-h | 69.7406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CO2 |  | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 |  | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O |  | EUR/MWh-h | 0.00051991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 |  | EUR/MWh-h | 0.0016735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX |  | EUR/MWh-h | 7.7862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PM2.5 |  | EUR/MWh-h | 0.17432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DH revenue |  | EUR/MWh-h | -87.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total LCOE | Levelized cost |  | EUR/MWh-h | 83.3331 | 55.0956 | 28.1138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Unit | Solar PV | Large onshore wind turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat production cost | Capital cost |  | EUR/MWh-e | 47.3813 | 22.4961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel cost |  | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&M cost |  | EUR/MWh-e | 7.7143 | 5.6176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CO2 emissions |  | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Climate externalities |  | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Air pollution |  | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DH revenue |  | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total LCOE | Total LCOE |  | EUR/MWh-e | 55.0956 | 28.1138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1
|  |  | Unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Large onshore wind turbine | Solar PV
Heat production cost | Capital cost |  | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.4961 | 47.3813
| Fuel cost |  | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&M cost |  | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6176 | 7.7143
| CO2 emissions |  | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Climate externalities |  | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Air pollution |  | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DH revenue |  | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total LCOE | Total LCOE |  | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.1138 | 55.0956
On/off
On/off
On/off
On/off
On/off
On/off
On/off
On/off

## 3.2 LCOE assumptions
3.2 Assumptions
In this tab are the assumptions for the calculations inserted. References can be found in the tables.
3.2.1 Technology- and price catalogue
3.2.1.1 District heating technologies
| Technology | Reference | Electric capacity | Heat capacity | Solar thermal size | Storage size | Fuel | Voltage connection level | Full load hours |  |  | Investment (el) (eqiupment) | Investment (el) (installation) | Investment (heat) (equipment) | Investment (heat) (installation) | Investment (solar) | Investment (storage) | Fixed O&M (el) | Fixed O&M (heat) | Fixed O&M (solar) | Fixed O&M (storage) | Var. O&M (el) | Var. O&M (heat) | Lifetime | CV | CB | Electric efficiency CHP | Heat efficiency CHP | Electric efficiency condensing | Heat efficiency | CO2 capture rate (amount of emission) | SO2 (degree of desulphuring) | Emission factor SO2 | Emission factor NOX | Emission factor CH4 | Emission factor N2O | Emission factor PM2.5
|  |  | MW-e | MW-h | m2 panel | m3 storage |  |  | Black | Blue | Green | mil. EUR/MW-el | mil. EUR/MW-el | mil. EUR/MW-heat | mil. EUR/MW-heat | EUR/m2 panel | EUR/m3 storage | EUR/MW-el/year | EUR/MW-heat/year | EUR/m2 panel/year | EUR/m3 storage/year | EUR/MWh-el | EUR/MWh-heat | year |  |  | MW-el/MW-fuel | MW-heat/MW-fuel | MW-el/MW-fuel | MW-heat/MW-fuel | % | % | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f
Storages | Tank thermal storage | Ramboll | --- | --- | --- | 3000 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 175 | --- | --- | --- | 0.5 | --- | --- | 40 | --- | --- | --- | --- | --- | --- | 0 | --- | --- | --- | --- | --- | ---
| Pit thermal storage | Ramboll | --- | --- | --- | 120000 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 50 | --- | --- | --- | 0.2 | --- | --- | 20 | --- | --- | --- | --- | --- | --- | 0 | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Boilers | Boiler - wood chips | [1] | --- | 7 | --- | --- | Wood chips | --- | 5000 | 5000 | 5000 | --- | --- | 0.4 | 0.29 | --- | --- | --- | 32200 | --- | --- | --- | 1 | 25 | --- | --- | --- | --- | --- | 1.15 | 0 | 0.98 | --- | 226.8 | 39.6 | 10.8 | 1.08
| Boiler - wood pellets | [1] | --- | 6 | --- | --- | Wood pellets | --- | 5000 | 5000 | 5000 | --- | --- | 0.44 | 0.28 | --- | --- | --- | 33000 | --- | --- | --- | 0.5 | 25 | --- | --- | --- | --- | --- | 1 | 0 | 0.983 | --- | 194.4 | 0 | 3.6 | 1.08
| Boiler - straw | [1] | --- | 6 | --- | --- | Straw | --- | 5000 | 5000 | 5000 | --- | --- | 0.43 | 0.46 | --- | --- | --- | 51300 | --- | --- | --- | 0.6 | 25 | --- | --- | --- | --- | --- | 1.02 | 0 | 0.964 | --- | 259.2 | 39.6 | 10.8 | 1.08
| Boiler - natural gas | [1] | --- | 5.3 | --- | --- | Natural gas | --- | 500 | 500 | 500 | --- | --- | 0.04 | 0.02 | --- | --- | --- | 1950 | --- | --- | --- | 1.1 | 25 | --- | --- | --- | --- | --- | 1.03 | 0 | --- | 1.08 | 32.4 | 10.8 | 3.6 | 0
| Boiler - oil | [1] | --- | 5 | --- | --- | Oil | --- | 500 | 500 | 500 | --- | --- | 0.04 | 0.02 | --- | --- | --- | 1950 | --- | --- | --- | 1.1 | 25 | --- | --- | --- | --- | --- | 1.03 | 0 | --- | 1.8 | 90 | 0 | 0 | 0.72
| Electric boiler | [1] | --- | 5 | --- | --- | Electricity | High voltage level | 200 | 200 | 200 | --- | --- | 0.12 | 0.03 | --- | --- | --- | 1070 | --- | --- | --- | 0.9 | 20 | --- | --- | --- | --- | --- | 1 | 0 | --- | --- | --- | --- | --- | ---
| Boiler - coal | [1] | --- | 5 | --- | --- | Coal | --- | 500 | 500 | 500 | --- | --- | 0.04 | 0.02 | --- | --- | --- | 2140 | --- | --- | --- | 1.6 | 20 | --- | --- | --- | --- | --- | 0.9 | 0 | --- | 18 | 126 | 5.4 | 2.88 | 1.8
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
CHP's | Small CHP - waste | [1] | 8 | 30 | --- | --- | Waste | --- | 7000 | 7000 | 7000 | 6.5 | 4 | --- | --- | --- | --- | 413600 | --- | --- | --- | 25.6 | --- | 25 | 1 | 0.26582 | 0.21 | 0.79 | --- | --- | 0 | 0.998 | --- | 241.2 | 0.36 | 3.6 | 1.08
| Medium CHP - waste | [1] | 18 | 64 | --- | --- | Waste | --- | 7000 | 7000 | 7000 | 5.5 | 3.6 | --- | --- | --- | --- | 264800 | --- | --- | --- | 25 | --- | 25 | 1 | 0.28205 | 0.22 | 0.78 | --- | --- | 0 | 0.998 | --- | 201.6 | 0.36 | 3.6 | 1.08
| Large CHP - waste | [1] | 51 | 173 | --- | --- | Waste | --- | 7000 | 7000 | 7000 | 4.7 | 3.1 | --- | --- | --- | --- | 188300 | --- | --- | --- | 24.8 | --- | 25 | 1 | 0.29487 | 0.23 | 0.78 | --- | --- | 0 | 0.998 | --- | 201.6 | 0.36 | 3.6 | 1.08
| Boiler - waste | [1] | --- | 37 | --- | --- | Waste | --- | 7000 | 7000 | 7000 | --- | --- | 1.05 | 0.78 | --- | --- | --- | 78600 | --- | --- | --- | 5.5 | 25 | --- | --- | --- | --- | --- | 1.05 | 0 | 0.998 | --- | 241.2 | 0.36 | 3.6 | 1.08
| Small CHP - wood chips | [1] | 3 | 21 | --- | --- | Wood chips | --- | 5000 | 4500 | 4000 | 4 | 2.5 | --- | --- | --- | --- | 288900 | --- | --- | --- | 7.8 | --- | 25 | 1 | 0.14433 | 0.14 | 0.97 | --- | --- | 0 | 0.98 | --- | 226.8 | 39.6 | 3.6 | 1.08
| Medium CHP - wood chips | [1] | 23 | 65 | --- | --- | Wood chips | --- | 5000 | 4500 | 4000 | 2.4 | 1.2 | --- | --- | --- | --- | 153600 | --- | --- | --- | 3.8 | --- | 25 | 1 | 0.35366 | 0.29 | 0.82 | --- | --- | 0 | 0.98 | --- | 259.2 | 7.2 | 3.6 | 1.08
| Large CHP - wood chips | [1] | 177 | 484 | --- | --- | Wood chips | --- | 5000 | 4500 | 4000 | 2.2 | 1.2 | --- | --- | --- | --- | 97600 | --- | --- | --- | 3.8 | --- | 25 | 1 | 0.36585 | 0.3 | 0.82 | --- | --- | 0 | 0.98 | --- | 86.4 | 7.2 | 28.8 | 1.08
| Small CHP - wood pellets | [1] | 3 | 16 | --- | --- | Wood pellets | --- | 4000 | 3500 | 3000 | 4 | 2.2 | --- | --- | --- | --- | 275900 | --- | --- | --- | 3.4 | --- | 25 | 1 | 0.18293 | 0.15 | 0.82 | --- | --- | 0 | 0.983 | --- | 194.4 | 0 | 3.6 | 1.08
| Medium CHP - wood pellets | [1] | 24 | 54 | --- | --- | Wood pellets | --- | 4000 | 3500 | 3000 | 2 | 1.1 | --- | --- | --- | --- | 127100 | --- | --- | --- | 1.7 | --- | 25 | 1 | 0.44776 | 0.3 | 0.67 | --- | --- | 0 | 0.983 | --- | 223.2 | 0 | 3.6 | 1.08
| Large CHP - wood pellets | [1] | 261 | 522 | --- | --- | Wood pellets | --- | 4000 | 3500 | 3000 | 1.3 | 1 | --- | --- | --- | --- | 64000 | --- | --- | --- | 1.6 | --- | 25 | 1 | 0.5 | 0.32 | 0.64 | --- | --- | 0 | 0.983 | --- | 75.6 | 0 | 3.6 | 1.08
| Small CHP - straw | [1] | 3 | 17 | --- | --- | Straw | --- | 5000 | 4500 | 4000 | 3.8 | 3 | --- | --- | --- | --- | 318200 | --- | --- | --- | 4 | --- | 25 | 1 | 0.17857 | 0.15 | 0.84 | --- | --- | 0 | 0.964 | --- | 259.2 | 39.6 | 3.6 | 1.08
| Medium CHP - straw | [1] | 24 | 53 | --- | --- | Straw | --- | 5000 | 4500 | 4000 | 2.3 | 1.5 | --- | --- | --- | --- | 149900 | --- | --- | --- | 2 | --- | 25 | 1 | 0.45588 | 0.31 | 0.68 | --- | --- | 0 | 0.964 | --- | 252 | 0 | 3.6 | 1.08
| Large CHP - straw | [1] | 41 | 90 | --- | --- | Straw | --- | 5000 | 4500 | 4000 | 2.1 | 1.3 | --- | --- | --- | --- | 124900 | --- | --- | --- | 1.9 | --- | 25 | 1 | 0.45588 | 0.31 | 0.68 | --- | --- | 0 | 0.964 | --- | 241.2 | 0 | 3.6 | 1.08
| Large CHP - coal | [1] | 550 | 655 | --- | --- | Coal | --- | 5000 | 4000 | 3000 | 1.9 | --- | --- | --- | --- | --- | 31000 | --- | --- | --- | 2.9 | --- | 25 | 0.15 | 0.84 | 0.42 | 0.5 | 0.49 | --- | 0 | 0.97 | --- | 126 | 5.4 | 2.88 | 0
| Medium CHP - natural gas SC | [1] | 27.5 | 38 | --- | --- | Natural gas | --- | 4000 | 3500 | 3000 | 0.73 | --- | --- | --- | --- | --- | 18600 | --- | --- | --- | 5.1 | --- | 25 | --- | 0.72727 | 0.32 | 0.44 | 0.37 | --- | 0 | 0 | --- | 54 | 5.4 | 3.6 | 0
| Large CHP - natural gas SC | [1] | 82.5 | 87 | --- | --- | Natural gas | --- | 4000 | 3500 | 3000 | 0.59 | --- | --- | --- | --- | --- | 29500 | --- | --- | --- | 4.5 | --- | 25 | --- | 0.94595 | 0.35 | 0.37 | 0.4 | --- | 0 | 0 | --- | 54 | 5.4 | 3.6 | 0
| Medium CHP - natural gas CC | [1] | 55 | 42 | --- | --- | Natural gas | --- | 4000 | 3500 | 3000 | 1 | 0.3 | --- | --- | --- | --- | 29300 | --- | --- | --- | 4.4 | --- | 25 | --- | 1.3143 | 0.46 | 0.35 | 0.51 | --- | 0 | 0 | --- | 54 | 5.4 | 3.6 | 0
| Large CHP - natural gas CC | [1] | 300 | 167 | --- | --- | Natural gas | --- | 4000 | 3500 | 3000 | 0.68 | 0.2 | --- | --- | --- | --- | 29300 | --- | --- | --- | 4.4 | --- | 25 | --- | 1.8 | 0.54 | 0.3 | 0.59 | --- | 0 | 0 | --- | 54 | 5.4 | 3.6 | 0
| Engine - natural gas | [1] | 5.5 | 5.8 | --- | --- | Natural gas | --- | 4000 | 3500 | 3000 | 0.6 | 0.35 | --- | --- | --- | --- | 9750 | --- | --- | --- | 5.4 | --- | 25 | --- | 0.95455 | 0.42 | 0.44 | 0.47 | --- | 0 | 0 | --- | 216 | 1134 | 2.16 | 0
| Large CHP - coal - carbon capture | Ramboll | 495 | 619 | --- | --- | Coal | --- | 5000 | 4000 | 3000 | 3.52 | --- | --- | --- | --- | --- | 65666 | --- | --- | --- | 2.9 | --- | 25 | 0.15 | 0.8 | 0.32 | 0.4 | 0.39 | --- | 0.9 | 0.97 | --- | 126 | 5.4 | 2.88 | 0
| Large CHP - wood chips - carbon capture | Ramboll | 159 | 572 | --- | --- | Wood chips | --- | 4000 | 3500 | 3000 | 5.3235 | 2.8665 | --- | --- | --- | --- | 132266 | --- | --- | --- | 3.8 | --- | 25 | 1 | 0.27778 | 0.2 | 0.72 | --- | --- | 0.9 | 0.98 | --- | 86.4 | 7.2 | 28.8 | 1.08
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
HP's | Electric heat pump | [1] | --- | 4 | --- | --- | Electricity | High voltage level | 3000 | 3000 | 3000 | --- | --- | 0.33 | 0.33 | --- | --- | --- | 2000 | --- | --- | --- | 3.2 | 25 | --- | --- | --- | --- | --- | 3.6 | 0 | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
RE | Geothermal | [1] | --- | 10 | --- | --- | Electricity | High voltage level | 5000 | 5000 | 5000 | --- | --- | 1.95 | 0.65 | --- | --- | --- | 20000 | --- | --- | --- | 3.5 | 25 | --- | --- | --- | --- | --- | 3.6 | 0 | --- | --- | --- | --- | --- | ---
| Solar PV | [1] | 10 | --- | --- | --- | Solar PV | --- | 1050 | 1050 | 1050 | 0.62 | --- | --- | --- | --- | --- | 8100 | --- | --- | --- | --- | --- | 20 | --- | --- | --- | --- | --- | --- | 0 | --- | --- | --- | --- | --- | ---
| Solar - small | Ramboll | --- | --- | 2000 | --- | Solar | --- | --- | --- | --- | --- | --- | --- | --- | 380 | --- | --- | --- | 4 | --- | --- | --- | 30 | --- | --- | --- | --- | --- | --- | 0 | --- | --- | --- | --- | --- | ---
| Solar - medium | Ramboll | --- | --- | 10000 | --- | Solar | --- | --- | --- | --- | --- | --- | --- | --- | 200 | --- | --- | --- | 2 | --- | --- | --- | 30 | --- | --- | --- | --- | --- | --- | 0 | --- | --- | --- | --- | --- | ---
| Solar - large | Ramboll | --- | --- | 20000 | --- | Solar | --- | --- | --- | --- | --- | --- | --- | --- | 190 | --- | --- | --- | 2 | --- | --- | --- | 30 | --- | --- | --- | --- | --- | --- | 0 | --- | --- | --- | --- | --- | ---
| Large onshore wind turbine | [1] | 4.2 | --- | --- | --- | --- | --- | 3400 | 3400 | 3400 | 0.71 | 0.41 | --- | --- | --- | --- | 14000 | --- | --- | --- | 1.5 | --- | 27 | --- | --- | --- | --- | --- | --- | 0 | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
3.2.1.2 Individual technologies
| Technology | Reference | Heat capacity | Solar thermal size | Fuel | Voltage connection level | Full load hours | Investment (heat) | Investment (solar) | Fixed O&M (heat) | Fixed O&M (solar) | Var. O&M (heat) | Heat efficiency | Lifetime | Emission factor SO2 | Emission factor NOX | Emission factor CH4 | Emission factor N2O | Emission factor PM2.5
|  |  | MW-h | m2 panel |  |  | hours/year | mio. EUR/MW-heat | EUR/m2 panel | EUR/MW-heat/year | EUR/m2 panel/year | EUR/MWh-h | MW-heat/MW-fuel | year | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f
| Oil boiler | [2] | 0.015 | --- | Oil | --- | 3000 | 0.39 | --- | 16266 | --- | 0 | 0.92 | 20 | 1.8 | 108 | 0 | 0 | 0.072
| Gas boiler | [2] | 0.01 | --- | Natural gas | --- | 3000 | 0.31 | --- | 20500 | --- | 0 | 0.97 | 20 | 0 | 36 | 3.6 | 0 | 0
| Wood pellet boiler | [2] | 0.01 | --- | Wood pellets | --- | 3000 | 0.68 | --- | 50400 | --- | 0 | 0.82 | 20 | 90 | 252 | 7.2 | 14.4 | 54
| Wood stove | [2] | 0.005 | --- | Local wood | --- | 3000 | 0.5 | --- | 29000 | --- | 0 | 0.7 | 20 | 90 | 324 | 450 | 14.4 | 144
| Heat pump - air to air | [2] | 0.004 | --- | Electricity | Low voltage level | 3000 | 0.45 | --- | 40500 | --- | 0 | 5.1 | 12 | --- | --- | --- | --- | ---
| Heat pump - air to water | [2] | 0.01 | --- | Electricity | Low voltage level | 3000 | 0.94 | --- | 27800 | --- | 0 | 4.1 | 18 | --- | --- | --- | --- | ---
| Heat pump - brine to water | [2] | 0.01 | --- | Electricity | Low voltage level | 3000 | 1.5 | --- | 27800 | --- | 0 | 4.5 | 20 | --- | --- | --- | --- | ---
| Gas driven heat pump - brine to water | [2] | 0.03 | --- | Natural gas | --- | 3000 | 0.98 | --- | 15666 | --- | 0 | 1.45 | 20 | 0 | 36 | 3.6 | 0 | 0
| Electric heating | [2] | 0.003 | --- | Electricity | Low voltage level | 3000 | 0.96 | --- | 8000 | --- | 0 | 1 | 30 | --- | --- | --- | --- | ---
| Solar heating | Ramboll | --- | 5 | Solar | --- | --- | --- | 500 | --- | 9 | --- | --- | 25 | --- | --- | --- | --- | ---
3.2.2 Energy prices and taxes
3.2.2.1 Electricity prices and taxes
|  | Electricity price | Black | Blue | Green | Distribution tarif |  | Transport tarif | Total
| Reference | [6] | [9] | [9] | [9] | Ramboll | Ramboll | Ramboll
[6 empty] | Low voltage level | High voltage level |  | Low voltage level | High voltage level
|  | EUR/MWh-e | EUR/MWh-e | EUR/MWh-e | EUR/MWh-e | EUR/MWh-e | EUR/MWh-e | EUR/MWh-e | EUR/MWh-e | EUR/MWh-e
| 2006 | 50.7915
| 2007 | 37.9884
| 2008 | 65.8302
| 2009 | 38.8564
| 2010 | 44.4888
| 2011 | 51.1244
| 2012 | 42.6888
| 2013 | 37.7801
| 2014 | 32.7632
| 2015 | 31.6265
| 2016 | 28.9595
| 2017 | 36.329
| 2018 | 46.1815 | 46.1815 | 46.1815 | 46.1815 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2019 |  | 46.8222 | 47.2032 | 49.1079 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2020 |  | 47.4629 | 48.2248 | 52.0344 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2021 |  | 48.1037 | 49.2465 | 54.9608 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2022 |  | 48.7444 | 50.2682 | 57.8873 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2023 |  | 49.3852 | 51.2899 | 60.8137 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2024 |  | 50.0259 | 52.3116 | 63.7402 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2025 |  | 50.6667 | 53.3333 | 66.6667 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2026 |  | 51.4667 | 53.3333 | 65.8667 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2027 |  | 52.2667 | 53.3333 | 65.0667 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2028 |  | 53.0667 | 53.3333 | 64.2667 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2029 |  | 53.8667 | 53.3333 | 63.4667 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2030 |  | 54.6667 | 53.3333 | 62.6667 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2031 |  | 54.9333 | 54.4 | 63.2 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2032 |  | 55.2 | 55.4667 | 63.7333 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2033 |  | 55.4667 | 56.5333 | 64.2667 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2034 |  | 55.7333 | 57.6 | 64.8 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2035 |  | 56 | 58.6667 | 65.3333 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2036 |  | 56 | 58.6667 | 65.3333 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2037 |  | 56 | 58.6667 | 65.3333 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2038 |  | 56 | 58.6667 | 65.3333 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2039 |  | 56 | 58.6667 | 65.3333 | 15 | 5 | 8.4 | 23.4 | 13.4
| 2040 |  | 56 | 58.6667 | 65.3333 | 15 | 5 | 8.4 | 23.4 | 13.4
3.2.2.2 Fuel prices
3.2.2.2.1 District heating companies
|  | Natural gas price | Current policies scenario | New policies scenario | Sustainable development scenario |  |  | Coal price | Current policies scenario | New policies scenario | Sustainable development scenario |  |  | Oil price | Current policies scenario | New policies scenario | Sustainable development scenario
| Reference | [6] | [7] | [7] | [7] |  | Reference | [6] | [7] | [7] | [7] |  | Reference | [6] | [7] | [7] | [7] | [10 empty] | Current policies scenario | New policies scenario | Sustainable development scenario
|  | EUR/MWh-f | EUR/MWh-f | EUR/MWh-f | EUR/MWh-f |  |  | EUR/MWh-f | EUR/MWh-f | EUR/MWh-f | EUR/MWh-f |  |  | EUR/MWh-f | EUR/MWh-f | EUR/MWh-f | EUR/MWh-f | [10 empty] | 8.2 | 7.9 | 7
| 2006 | [5 empty] | 2006 | 6.3109 |  |  |  |  | 2006 | 30.5948 | [13 empty] | 7.462 | 7.189 | 6.37
| 2007 | 27.936 |  |  |  |  | 2007 | 7.8926 |  |  |  |  | 2007 | 30.6769 | [13 empty] | 25.4609 | 24.5294 | 21.7349
| 2008 | 35.1 |  |  |  |  | 2008 | 12.2348 |  |  |  |  | 2008 | 38.4071 | [13 empty] | 7.0725 | 6.8137 | 6.0375
| 2009 | 30.348 |  |  |  |  | 2009 | 6.2611 |  |  |  |  | 2009 | 25.945
| 2010 | 29.16 |  |  |  |  | 2010 | 8.6396 |  |  |  |  | 2010 | 35.2521 | [13 empty] | 81 | 77 | 67
| 2011 | 31.374 |  |  |  |  | 2011 | 10.7001 |  |  |  |  | 2011 | 46.286 | [13 empty] | 73.71 | 70.07 | 60.97
| 2012 | 30.69 |  |  |  |  | 2012 | 8.9417 |  |  |  |  | 2012 | 50.4683 | [13 empty] | 2.9842 | 2.8368 | 2.4684
| 2013 | 33.552 |  |  |  |  | 2013 | 7.5698 |  |  |  |  | 2013 | 47.5718
| 2014 | 29.592 |  |  |  |  | 2014 | 6.9426 |  |  |  |  | 2014 | 43.3449 | [13 empty] | 97 | 83 | 72
| 2015 | 26.73 |  |  |  |  | 2015 | 6.186 |  |  |  |  | 2015 | 28.0789 | [13 empty] | 88.27 | 75.53 | 65.52
| 2016 | 22.464 |  |  |  |  | 2016 | 6.5926 |  |  |  |  | 2016 | 23.723 | [13 empty] | 15.0592 | 12.8857 | 11.178
| 2017 | 21.7818 |  |  |  |  | 2017 | 9.0231 |  |  |  |  | 2017 | 28.1764
| 2018 | 22.0793 |  |  |  |  | 2018 | 9.5592 |  |  |  |  | 2018 | 35.3438
| 2019 | 27.504 | 27.504 | 27.504 | 27.504 |  | 2019 | 11.844 | 11.844 | 11.844 | 11.844 |  | 2019 | 45.936 | 45.936 | 45.936 | 45.936
| 2020 |  | 27.0936 | 26.9064 | 26.3448 |  | 2020 |  | 11.6208 | 11.5128 | 11.2464 |  | 2020 |  | 47.5848 | 46.0224 | 44.7912
| 2021 |  | 26.6832 | 26.3088 | 25.1856 |  | 2021 |  | 11.3976 | 11.1816 | 10.6488 |  | 2021 |  | 49.2336 | 46.1088 | 43.6464
| 2022 |  | 26.2728 | 25.7112 | 24.0264 |  | 2022 |  | 11.1744 | 10.8504 | 10.0512 |  | 2022 |  | 50.8824 | 46.1952 | 42.5016
| 2023 |  | 25.8624 | 25.1136 | 22.8672 |  | 2023 |  | 10.9512 | 10.5192 | 9.4536 |  | 2023 |  | 52.5312 | 46.2816 | 41.3568
| 2024 |  | 25.452 | 24.516 | 21.708 |  | 2024 |  | 10.728 | 10.188 | 8.856 |  | 2024 |  | 54.18 | 46.368 | 40.212
| 2025 |  | 25.861 | 24.7978 | 21.8559 |  | 2025 |  | 10.8302 | 10.2251 | 8.823 |  | 2025 |  | 55.4549 | 47.2311 | 39.8922
| 2026 |  | 26.2701 | 25.0796 | 22.0037 |  | 2026 |  | 10.9323 | 10.2622 | 8.7901 |  | 2026 |  | 56.7298 | 48.0943 | 39.5725
| 2027 |  | 26.6791 | 25.3614 | 22.1516 |  | 2027 |  | 11.0345 | 10.2993 | 8.7571 |  | 2027 |  | 58.0047 | 48.9574 | 39.2527
| 2028 |  | 27.0881 | 25.6432 | 22.2994 |  | 2028 |  | 11.1367 | 10.3364 | 8.7241 |  | 2028 |  | 59.2796 | 49.8206 | 38.9329
| 2029 |  | 27.4972 | 25.9249 | 22.4473 |  | 2029 |  | 11.2388 | 10.3735 | 8.6912 |  | 2029 |  | 60.5545 | 50.6837 | 38.6132
| 2030 |  | 27.9062 | 26.2067 | 22.5951 |  | 2030 |  | 11.341 | 10.4106 | 8.6582 |  | 2030 |  | 61.8294 | 51.5468 | 38.2934
| 2031 |  | 28.3153 | 26.5115 | 22.743 |  | 2031 |  | 11.4432 | 10.4367 | 8.6252 |  | 2031 |  | 63.1043 | 52.5339 | 37.9736
| 2032 |  | 28.7243 | 26.8162 | 22.8908 |  | 2032 |  | 11.5453 | 10.4627 | 8.5923 |  | 2032 |  | 64.3792 | 53.521 | 37.6539
| 2033 |  | 29.1333 | 27.1209 | 23.0387 |  | 2033 |  | 11.6475 | 10.4887 | 8.5593 |  | 2033 |  | 65.6541 | 54.508 | 37.3341
| 2034 |  | 29.5424 | 27.4256 | 23.1865 |  | 2034 |  | 11.7496 | 10.5147 | 8.5263 |  | 2034 |  | 66.929 | 55.4951 | 37.0143
| 2035 |  | 29.9514 | 27.7304 | 23.3344 |  | 2035 |  | 11.8518 | 10.5408 | 8.4934 |  | 2035 |  | 68.2039 | 56.4822 | 36.6946
| 2036 |  | 30.3604 | 28.0351 | 23.4822 |  | 2036 |  | 11.954 | 10.5668 | 8.4604 |  | 2036 |  | 69.4788 | 57.3596 | 36.3748
| 2037 |  | 30.7695 | 28.3398 | 23.6301 |  | 2037 |  | 12.0561 | 10.5928 | 8.4274 |  | 2037 |  | 70.7537 | 58.237 | 36.055
| 2038 |  | 31.1785 | 28.6446 | 23.7779 |  | 2038 |  | 12.1583 | 10.6189 | 8.3944 |  | 2038 |  | 72.0286 | 59.1144 | 35.7353
| 2039 |  | 31.5876 | 28.9493 | 23.9258 |  | 2039 |  | 12.2605 | 10.6449 | 8.3615 |  | 2039 |  | 73.3035 | 59.9918 | 35.4155
| 2040 |  | 31.9966 | 29.254 | 24.0736 |  | 2040 |  | 12.3626 | 10.6709 | 8.3285 |  | 2040 |  | 74.5784 | 60.8691 | 35.0957
|  | Natural gas | Coal | Oil | Straw | Wood chips | Wood pellets | Waste
| Reference | [6] | [6] | [6] | [4] | [4] | [4] | Ramboll
|  | EUR/MWh-f | EUR/MWh-f | EUR/MWh-f | EUR/MWh-f | EUR/MWh-f | EUR/MWh-f | EUR/MWh-f
2006
2007
2008
2009
2010
2011
2012
2013
2014
2015
2016
2017
2018
| 2019 | 27.504 | 11.844 | 45.936 | 20.8174 | 24.3194 | 32.6586 | -18
| 2020 | 26.3448 | 11.2464 | 44.7912 | 20.9812 | 24.5108 | 32.2887 | -18
| 2021 | 25.1856 | 10.6488 | 43.6464 | 21.188 | 24.7523 | 32.1886 | -18
| 2022 | 24.0264 | 10.0512 | 42.5016 | 21.3956 | 24.9949 | 32.1239 | -18
| 2023 | 22.8672 | 9.4536 | 41.3568 | 21.6041 | 25.2384 | 32.0755 | -18
| 2024 | 21.708 | 8.856 | 40.212 | 21.8134 | 25.4829 | 32.0478 | -18
| 2025 | 21.8559 | 8.823 | 39.8922 | 22.0234 | 25.7282 | 32.0169 | -18
| 2026 | 22.0037 | 8.7901 | 39.5725 | 22.1517 | 25.8782 | 32.1339 | -18
| 2027 | 22.1516 | 8.7571 | 39.2527 | 22.2802 | 26.0283 | 32.2507 | -18
| 2028 | 22.2994 | 8.7241 | 38.9329 | 22.4088 | 26.1785 | 32.3673 | -18
| 2029 | 22.4473 | 8.6912 | 38.6132 | 22.5375 | 26.3288 | 32.4837 | -18
| 2030 | 22.5951 | 8.6582 | 38.2934 | 22.6663 | 26.4793 | 32.5998 | -18
| 2031 | 22.743 | 8.6252 | 37.9736 | 22.7748 | 26.606 | 32.6926 | -18
| 2032 | 22.8908 | 8.5923 | 37.6539 | 22.8834 | 26.733 | 32.7853 | -18
| 2033 | 23.0387 | 8.5593 | 37.3341 | 22.9922 | 26.8601 | 32.8779 | -18
| 2034 | 23.1865 | 8.5263 | 37.0143 | 23.1011 | 26.9873 | 32.9704 | -18
| 2035 | 23.3344 | 8.4934 | 36.6946 | 23.2102 | 27.1147 | 33.0629 | -18
| 2036 | 23.4822 | 8.4604 | 36.3748 | 23.3108 | 27.2322 | 33.1396 | -18
| 2037 | 23.6301 | 8.4274 | 36.055 | 23.4114 | 27.3497 | 33.2162 | -18
| 2038 | 23.7779 | 8.3944 | 35.7353 | 23.512 | 27.4673 | 33.2926 | -18
| 2039 | 23.9258 | 8.3615 | 35.4155 | 23.6126 | 27.5849 | 33.3688 | -18
| 2040 | 24.0736 | 8.3285 | 35.0957 | 23.7133 | 27.7025 | 33.4448 | -18
3.2.2.2.2 Individual
|  | Natural gas | Oil | Wood pellets | Local wood
| Reference | --- | --- | --- | Ramboll
|  | EUR/MWh-f | EUR/MWh-f | EUR/MWh-f | EUR/MWh-f
2006
2007
2008
2009
2010
2011
2012
2013
2014
2015
2016
2017
2018
| 2019 | 31.504 | 49.936 | 33.6586 | 50
| 2020 | 30.3448 | 48.7912 | 33.2887 | 50
| 2021 | 29.1856 | 47.6464 | 33.1886 | 50
| 2022 | 28.0264 | 46.5016 | 33.1239 | 50
| 2023 | 26.8672 | 45.3568 | 33.0755 | 50
| 2024 | 25.708 | 44.212 | 33.0478 | 50
| 2025 | 25.8559 | 43.8922 | 33.0169 | 50
| 2026 | 26.0037 | 43.5725 | 33.1339 | 50
| 2027 | 26.1516 | 43.2527 | 33.2507 | 50
| 2028 | 26.2994 | 42.9329 | 33.3673 | 50
| 2029 | 26.4473 | 42.6132 | 33.4837 | 50
| 2030 | 26.5951 | 42.2934 | 33.5998 | 50
| 2031 | 26.743 | 41.9736 | 33.6926 | 50
| 2032 | 26.8908 | 41.6539 | 33.7853 | 50
| 2033 | 27.0387 | 41.3341 | 33.8779 | 50
| 2034 | 27.1865 | 41.0143 | 33.9704 | 50
| 2035 | 27.3344 | 40.6946 | 34.0629 | 50
| 2036 | 27.4822 | 40.3748 | 34.1396 | 50
| 2037 | 27.6301 | 40.055 | 34.2162 | 50
| 2038 | 27.7779 | 39.7353 | 34.2926 | 50
| 2039 | 27.9258 | 39.4155 | 34.3688 | 50
| 2040 | 28.0736 | 39.0957 | 34.4448 | 50
* An extra cost for transport is added to the fuel price
3.2.2.3 Electricity price factors
| Operation time (% of avail. time) |  | Electricity consuming units | Electricity producing units
| Reference |  | [6]
| From | To | Factor to be multiplied electricity price | Factor to be multiplied electricity price
| 0 | 5 | 0.058819 | 2.0324
| 5 | 10 | 0.27482 | 1.8107
| 10 | 15 | 0.39505 | 1.6756
| 15 | 20 | 0.47278 | 1.5823
| 20 | 25 | 0.5285 | 1.5123
| 25 | 30 | 0.57195 | 1.4575
| 30 | 35 | 0.60827 | 1.4114
| 35 | 40 | 0.64018 | 1.3713
| 40 | 45 | 0.66995 | 1.3351
| 45 | 50 | 0.69837 | 1.3016
| 50 | 55 | 0.72583 | 1.27
| 55 | 60 | 0.75248 | 1.2399
| 60 | 65 | 0.77849 | 1.211
| 65 | 70 | 0.8039 | 1.1835
| 70 | 75 | 0.82924 | 1.1572
| 75 | 80 | 0.85445 | 1.1318
| 80 | 85 | 0.88078 | 1.1068
| 85 | 90 | 0.9099 | 1.0806
| 90 | 95 | 0.9456 | 1.0496
| 95 | 100 | 1 | 1
* 2016 electricity prices applied
3.2.2.4 District heating price
DH price
| Reference | Ramboll
EUR/MWh-h
| 2019 | 40
| 2020 | 40
| 2021 | 40
| 2022 | 40
| 2023 | 40
| 2024 | 40
| 2025 | 40
| 2026 | 40
| 2027 | 40
| 2028 | 40
| 2029 | 40
| 2030 | 40
| 2031 | 40
| 2032 | 40
| 2033 | 40
| 2034 | 40
| 2035 | 40
| 2036 | 40
| 2037 | 40
| 2038 | 40
| 2039 | 40
| 2040 | 40
3.2.3 Emission factors
3.2.3.1 Electricity
|  | CO2 | Black | Blue | Green | CH4 | N2O | SO2 | NOX | PM2.5
| Reference | --- | [9] | [9] | [9] | Ramboll | Ramboll | Ramboll | Ramboll | Ramboll
|  | kg/MWh-e | kg/MWh-e | kg/MWh-e | kg/MWh-e | g/MWh-e | g/MWh-e | g/MWh-e | g/MWh-e | g/MWh-e
| 2019 |  | 262 | 213 | 188 | 120 | 3.5 | 91 | 241 | 1.4
| 2020 |  | 245 | 200 | 175 | 111.7021 | 3.258 | 84.7074 | 224.3351 | 1.3032
| 2021 |  | 228 | 187 | 162 | 103.4043 | 3.016 | 78.4149 | 207.6702 | 1.2064
| 2022 |  | 211 | 174 | 149 | 95.1064 | 2.7739 | 72.1223 | 191.0053 | 1.1096
| 2023 |  | 194 | 161 | 136 | 86.8085 | 2.5319 | 65.8298 | 174.3404 | 1.0128
| 2024 |  | 177 | 148 | 123 | 78.5106 | 2.2899 | 59.5372 | 157.6755 | 0.91596
| 2025 |  | 160 | 135 | 110 | 70.2128 | 2.0479 | 53.2447 | 141.0106 | 0.81915
| 2026 |  | 151 | 125 | 100 | 63.8298 | 1.8617 | 48.4043 | 128.1915 | 0.74468
| 2027 |  | 142 | 115 | 90 | 57.4468 | 1.6755 | 43.5638 | 115.3723 | 0.67021
| 2028 |  | 133 | 105 | 80 | 51.0638 | 1.4894 | 38.7234 | 102.5532 | 0.59574
| 2029 |  | 124 | 95 | 70 | 44.6809 | 1.3032 | 33.883 | 89.734 | 0.52128
| 2030 |  | 115 | 85 | 60 | 38.2979 | 1.117 | 29.0426 | 76.9149 | 0.44681
| 2031 |  | 112 | 82 | 56 | 35.7447 | 1.0426 | 27.1064 | 71.7872 | 0.41702
| 2032 |  | 109 | 79 | 52 | 33.1915 | 0.96809 | 25.1702 | 66.6596 | 0.38723
| 2033 |  | 106 | 76 | 48 | 30.6383 | 0.89362 | 23.234 | 61.5319 | 0.35745
| 2034 |  | 103 | 73 | 44 | 28.0851 | 0.81915 | 21.2979 | 56.4043 | 0.32766
| 2035 |  | 100 | 70 | 40 | 25.5319 | 0.74468 | 19.3617 | 51.2766 | 0.29787
| 2036 |  | 97 | 67 | 36 | 22.9787 | 0.67021 | 17.4255 | 46.1489 | 0.26809
| 2037 |  | 94 | 64 | 32 | 20.4255 | 0.59574 | 15.4894 | 41.0213 | 0.2383
| 2038 |  | 91 | 61 | 28 | 17.8723 | 0.52128 | 13.5532 | 35.8936 | 0.20851
| 2039 |  | 88 | 58 | 24 | 15.3191 | 0.44681 | 11.617 | 30.766 | 0.17872
| 2040 |  | 85 | 55 | 20 | 12.766 | 0.37234 | 9.6809 | 25.6383 | 0.14894
* Total emissions from the electricity sector are divided with electricity consumption. Import/export are not considered.
3.2.3.2 Fuels
3.2.3.2.1 CO2 emission
CO2 emission
| Reference | [5]
kg/MWh-f
| Natural gas | 205.2
| Coal | 338.4
| Fueloil | 284.4
| Oil | 266.4
| Straw | 0
| Wood chips | 0
| Wood pellets | 0
| Waste | 133.2
| Local wood | 0
3.2.3.2.2 SO2 emission
SO2 emission
| Reference | [5]
g/MWh-f
| Natural gas | 0
| Coal | 0.972
| Fueloil | 0.9
| Oil | 0.252
| Straw | 0.72
| Wood chips | 0
| Wood pellets | 0
| Waste | 0.972
| Local wood | 0
3.2.3.2.3 CO2 equivalents
|  | CH4 | N2O
| Reference | [5] | [5]
|  | kg CO2/kg emission | kg CO2/kg emission
| CO2 equivalents | 25 | 298
3.2.3.3 Emission prices
|  | CO2 quota price | Current policies scenario | New policies scenario | Sustainable development scenario | SO2 | NOX | PM2.5
| Reference | [6] | [7] | [7] | [7] | [8] | [8] | [8]
|  | EUR/ton | EUR/ton | EUR/ton | EUR/ton | EUR/kg | EUR/kg | EUR/kg
| 2006 | 17.6398
| 2007 | 1.361
| 2008 | 22.3933
| 2009 | 13.3571
| 2010 | 14.4676
| 2011 | 13.2731
| 2012 | 7.4842
| 2013 | 4.5197
| 2014 | 6.0078
| 2015 | 7.7212
| 2016 | 5.3641
| 2017 | 5.8383
| 2018 | 15.9568 | 15.9568 | 15.9568 | 15.9568
| 2019 |  | 16.4834 | 16.8661 | 21.713 | 20 | 10 | 50
| 2020 |  | 17.01 | 17.7753 | 27.4692 | 20 | 10 | 50
| 2021 |  | 17.5366 | 18.6845 | 33.2253 | 20 | 10 | 50
| 2022 |  | 18.0631 | 19.5938 | 38.9815 | 20 | 10 | 50
| 2023 |  | 18.5897 | 20.503 | 44.7377 | 20 | 10 | 50
| 2024 |  | 19.1163 | 21.4122 | 50.4938 | 20 | 10 | 50
| 2025 |  | 19.6429 | 22.3214 | 56.25 | 20 | 10 | 50
| 2026 |  | 20.7143 | 23.6905 | 60.8333 | 20 | 10 | 50
| 2027 |  | 21.7857 | 25.0595 | 65.4167 | 20 | 10 | 50
| 2028 |  | 22.8571 | 26.4286 | 70 | 20 | 10 | 50
| 2029 |  | 23.9286 | 27.7976 | 74.5833 | 20 | 10 | 50
| 2030 |  | 25 | 29.1667 | 79.1667 | 20 | 10 | 50
| 2031 |  | 26.0714 | 30.5357 | 83.75 | 20 | 10 | 50
| 2032 |  | 27.1429 | 31.9048 | 88.3333 | 20 | 10 | 50
| 2033 |  | 28.2143 | 33.2738 | 92.9167 | 20 | 10 | 50
| 2034 |  | 29.2857 | 34.6429 | 97.5 | 20 | 10 | 50
| 2035 |  | 30.3571 | 36.0119 | 102.0833 | 20 | 10 | 50
| 2036 |  | 31.4286 | 37.381 | 106.6667 | 20 | 10 | 50
| 2037 |  | 32.5 | 38.75 | 111.25 | 20 | 10 | 50
| 2038 |  | 33.5714 | 40.119 | 115.8333 | 20 | 10 | 50
| 2039 |  | 34.6429 | 41.4881 | 120.4167 | 20 | 10 | 50
| 2040 |  | 35.7143 | 42.8571 | 125 | 20 | 10 | 50
3.2.4 Heating values
|  | Heating value | Unit
| Reference | [5]
| Raw oil | 5.84 | GJ/barrel
| Raw oil (ton) | 43 | GJ/ton
| Natural gas | 39.53 | GJ/1000Nm3
| Coal | 24.7 | GJ/ton
| Fueloil | 40.65 | GJ/ton
| Gas-/Dieseloil | 42.7 | GJ/ton
| Biodiesel | 37.5 | GJ/ton
| Petrol | 43.8 | GJ/ton
| Bioethanol | 26.7 | GJ/ton
| JP1 | 43.5 | GJ/ton
| Straw (15 % water) | 14.5 | GJ/ton
| Wood chips (42,3 % water) | 10.05 | GJ/ton
| Wood pellets (7 % water) | 17.5 | GJ/ton
| Energy willow (50 % water) | 8 | GJ/ton
| Waste | 10.5 | GJ/ton
3.2.5 Storage volume
| Heat coverage by solar | Storage volume/collector area
| Reference | [1]
| % of total demand | m3/m2
| 0% | 0
| 5% | 0
| 10% | 0
| 15% | 0
| 20% | 0
| 25% | 0.1
| 30% | 0.25
| 35% | 0.75
| 40% | 1.25
| 45% | 1.5625
| 50% | 1.875
| 55% | 2.1875
| 60% | 2.5
| 65% | 2.6875
| 70% | 2.875
| 75% | 3.0625
| 80% | 3.25
| 85% | 3.4375
| 90% | 3.625
| 95% | 3.8125
| 100% | 4
3.2.6 Currency
| Country | Currency | Currency abbreviation | Currency factor
Reference
| Unit |  |  | Currency/€
| Australia | Australian Dollar | AUD | 1.48
| Brazil | Brazilian Real | BRL | 3.65
| Canada | Canadian Dollar | CAD | 1.51
| China | Chinese Yuan Renminbi | CNY | 7.6
| Denmark | Kroner | DKK | 7.44
| EU | Euro | EUR | 1
| Great Britain | Pound Sterling | GBP | 0.88
| India | Indian Rupee | INR | 71.9
| Indonesia | Indonesian Rupiah | IDR | 14869.48
| Japan | Japanese Yen | JPY | 123.39
| Kazakhstan | Kazakh Tenge | KZT | 352.98
| Malaysia | Malaysian Ringgit | MYR | 4.77
| Mexico | Mexican Peso | MXN | 20.39
| Philippines | Philippine Peso | PHP | 55.39
| Russia | Russian Rouble | RUB | 63.7
| Singapore | Singapore Dollar | SGD | 1.55
| South Africa | South African Rand | ZAR | 14.45
| Sweden | Swedish Kroner | SEK | 9.77
| Switzerland | Swiss Franc | CHF | 1.09
| Turkey | Turkish Lira | TRY | 3.95
| Ukraine | Ukrainian Grivnas | UAH | 29.24
| USA | US Dollar | USD | 1.12

## dropdown list (hidden)
Yes | 2019 | Natural gas | Natural gas | Black | Low voltage level | --- | Tank thermal storage | Solar PV | Current policies scenario | 1 | 2019
No | 2020 | Coal | Oil | Blue | High voltage level | Tank thermal storage | Pit thermal storage | --- | New policies scenario | 2 | 2020
| 2021 | Oil | Wood pellets | Green | --- | Pit thermal storage | --- |  | Sustainable development scenario | 3 | 2021
| 2022 | Straw | Local wood |  |  |  | Boiler - wood chips |  |  | 4 | 2022
| 2023 | Wood chips | 0 |  |  |  | Boiler - wood pellets |  |  | 5 | 2023
| 2024 | Wood pellets | 0 |  |  |  | Boiler - straw |  |  | 6 | 2024
|  | Waste | 0 |  |  |  | Boiler - natural gas |  |  | 7 | 2025
|  | 0 | 0 |  |  |  | Boiler - oil |  |  | 8 | 2026
|  | 0 | 0 |  |  |  | Electric boiler |  |  | 9 | 2027
|  | 0 | 0 |  |  |  | Boiler - coal |  |  | 10 | 2028
|  | 0 | 0 |  |  |  | Small CHP - waste |  |  | 11 | 2029
|  | 0 | 0 |  |  |  | Medium CHP - waste |  |  | 12 | 2030
|  | 0 | 0 |  |  |  | Large CHP - waste |  |  | 13 | 2031
|  | 0 | 0 |  |  |  | Boiler - waste |  |  | 14 | 2032
|  | Solar PV | Solar PV |  |  |  | Small CHP - wood chips |  |  | 15 | 2033
|  | Solar | Solar |  |  |  | Medium CHP - wood chips |  |  | 16 | 2034
|  | --- | --- |  |  |  | Large CHP - wood chips |  |  | 17 | 2035
|  | Electricity | Electricity |  |  |  | Small CHP - wood pellets |  |  | 18 | 2036
[7 empty] | Medium CHP - wood pellets |  |  | 19 | 2037
[7 empty] | Large CHP - wood pellets |  |  | 20 | 2038
[7 empty] | Small CHP - straw |  |  |  | 2039
[7 empty] | Medium CHP - straw |  |  |  | ---
Large CHP - straw
Large CHP - coal
Medium CHP - natural gas SC
Large CHP - natural gas SC
Medium CHP - natural gas CC
Large CHP - natural gas CC
Engine - natural gas
Large CHP - coal - carbon capture
Large CHP - wood chips - carbon capture
Electric heat pump
Geothermal
Solar PV
Solar - small
Solar - medium
Solar - large
Large onshore wind turbine

## 3.3 LCOE calculation
3.3 LCOE calculation
In this tab are the Levelized Cost Of Energy (LCOE) calculations performed
Discount rate |  | 5% | %
Calculation period |  | 1
Start year of calculation |  | 2022
Electricity price development |  | Green
Expected solar thermal production |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  | Sustainable development scenario
Country |  | EU
Currency abbreviation |  | EUR
Currency factor |  | 1
Equipment |  | 1
Installation |  | 1
3.3.1 District heating technologies
Unit |  |  | Technology 1 | Technology 2 | Technology 3 | Technology 4 | Technology 5 | Technology 6 | Technology 7 | Technology 8 | Technology 9 | Technology 10
|  |  | Solar - large | Geothermal | Boiler - straw | Large CHP - wood pellets | Boiler - natural gas | Small CHP - wood pellets | Electric heat pump | Boiler - coal | Boiler - oil | Large CHP - straw
Technical data | Fuel |  | Solar | Electricity | Straw | Wood pellets | Natural gas | Wood pellets | Electricity | Coal | Oil | Straw
| Lifetime | years | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 20 | 25 | 25
| Electric capacity | MW-e | --- | --- | --- | 261 | --- | 3 | --- | --- | --- | 41
| Heat capacity | MW-h | --- | 10 | 6 | 522 | 5.3 | 16 | 4 | 5 | 5 | 90
| Solar thermal size | m2 panel | 45000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Storage size | m3 storage | 120937.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Storage type |  | Pit thermal storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lifetime (storage) | years | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| Electric efficiency CHP | MW-el/MW-fuel | --- | --- | --- | 0.32 | --- | 0.15 | --- | --- | --- | 0.31
| Heat efficiency CHP | MW-h/MW-f | --- | --- | --- | 0.64 | --- | 0.82 | --- | --- | --- | 0.68
| Electric efficiency condensing | MW-e/MW-f | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| Heat efficiency | MW-h/MW-f | --- | 3.6 | 1.02 | --- | 1.03 | --- | 3.6 | 0.9 | 1.03 | ---
| CV |  | --- | --- | --- | 1 | --- | 1 | --- | --- | --- | 1
| CB |  | --- | --- | --- | 0.5 | --- | 0.18293 | --- | --- | --- | 0.45588
Operation | Full load hours | hours/year | --- | 5000 | 5000 | 3000 | 500 | 3000 | 3000 | 500 | 500 | 4000
| Expected solar production | kWh/m2/year | 500 | --- | --- | --- | --- | --- | --- | --- | --- | ---
Production | Electricity production | MWh-e/year | 0 | 0 | 0 | 783000 | 0 | 9000 | 0 | 0 | 0 | 164000
| Heat production | MWh-h/year | 22500 | 50000 | 30000 | 1566000 | 2650 | 48000 | 12000 | 2500 | 2500 | 360000
| Fuel consumption | MWh-f/MW-h/year | 0 | 13888.8889 | 29411.7647 | 2446875 | 2572.8155 | 58536.5854 | 3333.3333 | 2777.7778 | 2427.1845 | 529411.7647
Emissions from fuel | CO2 equivalent (CH4) | kg CO2/kg emission | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
| CO2 equivalent (N2O) | kg CO2/kg emission | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298
| CO2 emission | kg/MWh-f | --- | --- | 0 | 0 | 205.2 | 0 | --- | 338.4 | 266.4 | 0
| SO2 emission | g/MWh-f | --- | --- | 0.72 | 0 | 0 | 0 | --- | 0.972 | 0.252 | 0.72
| CO2 capture rate (amount of emission) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Emission factor CH4 | g/MWh-f | --- | --- | 39.6 | 0 | 10.8 | 0 | --- | 5.4 | 0 | 0
| Emission factor N2O | g/MWh-f | --- | --- | 10.8 | 3.6 | 3.6 | 3.6 | --- | 2.88 | 0 | 3.6
| Emission factor SO2 | g/MWh-f | --- | --- | --- | --- | 1.08 | --- | --- | 18 | 1.8 | ---
| SO2 (degree of desulphuring) | % | --- | --- | 96.4% | 98.3% | --- | 98.3% | --- | --- | --- | 96.4%
| Emission factor NOX | g/MWh-f | --- | --- | 259.2 | 75.6 | 32.4 | 194.4 | --- | 126 | 90 | 241.2
| Emission factor PM2.5 | g/MWh-f | --- | --- | 1.08 | 1.08 | 0 | 1.08 | --- | 1.8 | 0.72 | 1.08
Emissions from electricity | CO2 | kg/MWh-e | --- | 136 | --- | --- | --- | --- | 136 | --- | --- | ---
| CH4 | g/MWh-e | --- | 86.8085 | --- | --- | --- | --- | 86.8085 | --- | --- | ---
| N2O | g/MWh-e | --- | 2.5319 | --- | --- | --- | --- | 2.5319 | --- | --- | ---
| SO2 | g/MWh-e | --- | 65.8298 | --- | --- | --- | --- | 65.8298 | --- | --- | ---
| NOX | g/MWh-e | --- | 174.3404 | --- | --- | --- | --- | 174.3404 | --- | --- | ---
| PM2.5 | g/MWh-e | --- | 1.0128 | --- | --- | --- | --- | 1.0128 | --- | --- | ---
Emissions | CO2 | ton | 0 | 1888.8889 | 0 | 0 | 527.9417 | 0 | 453.3333 | 940 | 646.6019 | 0
| CH4 | kg CO2-equivalent | 0 | 30141.844 | 1164.7059 | 0 | 27.7864 | 0 | 7234.0426 | 15 | 0 | 0
| N2O | kg CO2-equivalent | 0 | 10479.3144 | 317.6471 | 8808.75 | 9.2621 | 210.7317 | 2515.0355 | 8 | 0 | 1905.8824
| SO2 | kg | 0 | 914.3026 | 0.76235 | 0 | 2.7786 | 0 | 219.4326 | 50 | 4.3689 | 13.7224
| NOX | kg | 0 | 2421.3948 | 7623.5294 | 184983.75 | 83.3592 | 11379.5122 | 581.1348 | 350 | 218.4466 | 127694.1176
| PM2.5 | kg | 0 | 14.0662 | 31.7647 | 2642.625 | 0 | 63.2195 | 3.3759 | 5 | 1.7476 | 571.7647
Investment | Investment (el) (eqiupment) | mil. EUR/MW-e | --- | --- | --- | 1.3 | --- | 4 | --- | --- | --- | 2.1
| Investment (el) (installation) | mil. EUR/MW-e | --- | --- | --- | 1 | --- | 2.2 | --- | --- | --- | 1.3
| Investment (heat) (equipment) | mil. EUR/MW-h | --- | 1.95 | 0.43 | --- | 0.04 | --- | 0.33 | 0.04 | 0.04 | ---
| Investment (heat) (installation) | mil. EUR/MW-h | --- | 0.65 | 0.46 | --- | 0.02 | --- | 0.33 | 0.02 | 0.02 | ---
| Investment (el) | mil. EUR/MW-h | 0 | 0 | 0 | 2.3 | 0 | 6.2 | 0 | 0 | 0 | 3.4
| Investment (heat) | mil. EUR/MW-h | 0 | 2.6 | 0.89 | 0 | 0.06 | 0 | 0.66 | 0.06 | 0.06 | 0
| Investment (solar) | mil. EUR/m2 panel | 0.00019 | --- | --- | --- | --- | --- | --- | --- | --- | ---
| Investment (storage) | mil. EUR/m3 storage | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Fixed O&M | Fixed O&M (el) | EUR/MW-e/year | --- | --- | --- | 64000 | --- | 275900 | --- | --- | --- | 124900
| Fixed O&M (heat) | EUR/MW-h/year | --- | 20000 | 51300 | --- | 1950 | --- | 2000 | 2140 | 1950 | ---
| Fixed O&M (solar) | EUR/m2 panel/year | 2 | --- | --- | --- | --- | --- | --- | --- | --- | ---
| Fixed O&M (storage) | EUR/m3 storage/year | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Var. O&M | Var. O&M (el) | EUR/MWh-e | --- | --- | --- | 1.6 | --- | 3.4 | --- | --- | --- | 1.9
| Var. O&M (heat) | EUR/MWh-h | --- | 3.5 | 0.6 | --- | 1.1 | --- | 3.2 | 1.6 | 1.1 | ---
Fuel price | Fuel price | EUR/MWh-f | 0 | 0 | 21.6041 | 32.0755 | 22.8672 | 32.0755 | 0 | 9.4536 | 41.3568 | 21.6041
Emission prices | CO2 | EUR/ton | 44.7377 | 44.7377 | 44.7377 | 44.7377 | 44.7377 | 44.7377 | 44.7377 | 44.7377 | 44.7377 | 44.7377
| SO2 | EUR/kg | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
| NOX | EUR/kg | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| PM2.5 | EUR/kg | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Electricity prices | Voltage connection level |  | --- | High voltage level | --- | --- | --- | --- | High voltage level | --- | --- | ---
| Tariff | EUR/MWh-e | 0 | 13.4 | 0 | 0 | 0 | 0 | 13.4 | 0 | 0 | 0
| Electricity price | EUR/MWh-h | 60.8137 | 60.8137 | 60.8137 | 60.8137 | 60.8137 | 60.8137 | 60.8137 | 60.8137 | 60.8137 | 60.8137
| Operation time | % of available time | --- | 57.0776 | 57.0776 | 34.2466 | 5.7078 | 34.2466 | 34.2466 | 5.7078 | 5.7078 | 45.6621
| Producing or consuming electricity |  | --- | Consuming | --- | Producing | --- | Producing | Consuming | --- | --- | Producing
| Electricity price factor |  | --- | 0.75248 | --- | 1.4114 | --- | 1.4114 | 0.60827 | --- | --- | 1.3016
| Electricity price (production) | EUR/MWh-h | --- | --- | --- | 85.8299 | --- | 85.8299 | --- | --- | --- | 79.1571
| Electricity price (consumption) | EUR/MWh-h | --- | 59.1612 | --- | --- | --- | --- | 50.3909 | --- | --- | ---
District heating price | DH price | EUR/MWh-h | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 0 | 0 | 40
Total cost | Capital cost | mil. EUR/year | 0.55619 | 1.8448 | 0.37889 | 42.5928 | 0.022563 | 1.3197 | 0.18731 | 0.024073 | 0.021286 | 9.8908
| Fixed O&M | mil. EUR/year | 0.09 | 0.2 | 0.3078 | 16.704 | 0.010335 | 0.8277 | 0.008 | 0.0107 | 0.00975 | 5.1209
| Var O&M | mil. EUR/year | 0 | 0.175 | 0.018 | 1.2528 | 0.002915 | 0.0306 | 0.0384 | 0.004 | 0.00275 | 0.3116
| Fuel cost | mil. EUR/year | 0 | 0.18611 | 0.63541 | 78.4847 | 0.058833 | 1.8776 | 0.044667 | 0.02626 | 0.10038 | 11.4375
| CO2 | mil. EUR/year | 0 | 0.084504 | 0 | 0 | 0.023619 | 0 | 0.020281 | 0.042053 | 0.028927 | 0
| CH4 | mil. EUR/year | 0 | 0.0013485 | 5.2106e-05 | 0 | 1.2431e-06 | 0 | 0.00032363 | 6.7107e-07 | 0 | 0
| N2O | mil. EUR/year | 0 | 0.00046882 | 1.4211e-05 | 0.00039408 | 4.1437e-07 | 9.4276e-06 | 0.00011252 | 3.579e-07 | 0 | 8.5265e-05
| SO2 | mil. EUR/year | 0 | 0.018286 | 1.5247e-05 | 0 | 5.5573e-05 | 0 | 0.0043887 | 0.001 | 8.7379e-05 | 0.00027445
| NOX | mil. EUR/year | 0 | 0.024214 | 0.076235 | 1.8498 | 0.00083359 | 0.1138 | 0.0058113 | 0.0035 | 0.0021845 | 1.2769
| PM2.5 | mil. EUR/year | 0 | 0.00070331 | 0.0015882 | 0.13213 | 0 | 0.003161 | 0.00016879 | 0.00025 | 8.7379e-05 | 0.028588
| DH revenue | mil. EUR/year | 0 | 0 | 0 | -62.64 | 0 | -1.92 | 0 | 0 | 0 | -14.4
| Electricity revenue | mil. EUR/year | 0 | 0 | 0 | -67.2048 | 0 | -0.77247 | 0 | 0 | 0 | -12.9818
|  | Unit | Solar - large (Pit thermal storage) (45000 m2) | Geothermal (10 MW-h) | Boiler - straw (6 MW-h) | Large CHP - wood pellets (522 MW-h) | Boiler - natural gas (5.3 MW-h) | Small CHP - wood pellets (16 MW-h) | Electric heat pump (4 MW-h) | Boiler - coal (5 MW-h) | Boiler - oil (5 MW-h) | Large CHP - straw (90 MW-h)
Heat production cost | Capital cost | TRUE | 24.7195 | 36.8953 | 12.6295 | 27.1984 | 8.5143 | 27.4941 | 15.6095 | 9.6291 | 8.5143 | 27.4744
| Fixed O&M | TRUE | 4 | 4 | 10.26 | 10.6667 | 3.9 | 17.2437 | 0.66667 | 4.28 | 3.9 | 14.2247
| Var O&M | TRUE | 0 | 3.5 | 0.6 | 0.8 | 1.1 | 0.6375 | 3.2 | 1.6 | 1.1 | 0.86556
| Fuel cost | TRUE | 0 | 3.7222 | 21.1805 | 50.1179 | 22.2012 | 39.1164 | 3.7222 | 10.504 | 40.1522 | 31.7707
| CO2 | TRUE | 0 | 1.6901 | 0 | 0 | 8.9128 | 0 | 1.6901 | 16.8214 | 11.571 | 0
| CH4 | TRUE | 0 | 0.02697 | 0.0017369 | 0 | 0.00046909 | 0 | 0.02697 | 0.00026843 | 0 | 0
| N2O | TRUE | 0 | 0.0093764 | 0.00047369 | 0.00025165 | 0.00015636 | 0.00019641 | 0.0093764 | 0.00014316 | 0 | 0.00023685
| SO2 | TRUE | 0 | 0.36572 | 0.00050824 | 0 | 0.020971 | 0 | 0.36572 | 0.4 | 0.034951 | 0.00076235
| NOX | TRUE | 0 | 0.48428 | 2.5412 | 1.1812 | 0.31456 | 2.3707 | 0.48428 | 1.4 | 0.87379 | 3.5471
| PM2.5 | TRUE | 0 | 0.014066 | 0.052941 | 0.084375 | 0 | 0.065854 | 0.014066 | 0.1 | 0.034951 | 0.079412
| Electricity revenue | TRUE | 0 | 0 | 0 | -42.915 | 0 | -16.0931 | 0 | 0 | 0 | -36.0605
Total LCOE | Levelized cost | EUR/MWh-h | 28.7195 | 50.708 | 47.2669 | 47.134 | 44.9644 | 70.8354 | 25.7889 | 44.7349 | 66.1812 | 41.9024
|  | Unit | Solar - large (Pit thermal storage) (45000 m2) | Geothermal (10 MW-h) | Boiler - straw (6 MW-h) | Large CHP - wood pellets (522 MW-h) | Boiler - natural gas (5.3 MW-h) | Small CHP - wood pellets (16 MW-h) | Electric heat pump (4 MW-h) | Boiler - coal (5 MW-h) | Boiler - oil (5 MW-h) | Large CHP - straw (90 MW-h)
Electricity production cost | Capital cost | TRUE | 0 | 0 | 0 | 54.3969 | 0 | 146.6351 | 0 | 0 | 0 | 60.3096
| Fixed O&M | TRUE | 0 | 0 | 0 | 21.3333 | 0 | 91.9667 | 0 | 0 | 0 | 31.225
| Var O&M | TRUE | 0 | 0 | 0 | 1.6 | 0 | 3.4 | 0 | 0 | 0 | 1.9
| Fuel cost | TRUE | 0 | 0 | 0 | 100.2359 | 0 | 208.621 | 0 | 0 | 0 | 69.7406
| CO2 | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O | TRUE | 0 | 0 | 0 | 0.0005033 | 0 | 0.0010475 | 0 | 0 | 0 | 0.00051991
| SO2 | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016735
| NOX | TRUE | 0 | 0 | 0 | 2.3625 | 0 | 12.6439 | 0 | 0 | 0 | 7.7862
| PM2.5 | TRUE | 0 | 0 | 0 | 0.16875 | 0 | 0.35122 | 0 | 0 | 0 | 0.17432
| DH revenue | TRUE | 0 | 0 | 0 | -80 | 0 | -213.3333 | 0 | 0 | 0 | -87.8049
Total LCOE | Levelized cost | EUR/MWh-e | 0 | 0 | 0 | 100.0978 | 0 | 250.2856 | 0 | 0 | 0 | 83.3331
|  |  | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1
|  | Unit | Electric heat pump (4 MW-h) | Solar - large (Pit thermal storage) (45000 m2) | Large CHP - straw (90 MW-h) | Boiler - coal (5 MW-h) | Boiler - natural gas (5.3 MW-h) | Large CHP - wood pellets (522 MW-h) | Boiler - straw (6 MW-h) | Geothermal (10 MW-h) | Boiler - oil (5 MW-h) | Small CHP - wood pellets (16 MW-h)
| Capital cost | EUR/MWh-h | 15.6095 | 24.7195 | 27.4744 | 9.6291 | 8.5143 | 27.1984 | 12.6295 | 36.8953 | 8.5143 | 27.4941
| Fixed O&M | EUR/MWh-h | 0.66667 | 4 | 14.2247 | 4.28 | 3.9 | 10.6667 | 10.26 | 4 | 3.9 | 17.2437
| Var O&M | EUR/MWh-h | 3.2 | 0 | 0.86556 | 1.6 | 1.1 | 0.8 | 0.6 | 3.5 | 1.1 | 0.6375
| Fuel cost | EUR/MWh-h | 3.7222 | 0 | 31.7707 | 10.504 | 22.2012 | 50.1179 | 21.1805 | 3.7222 | 40.1522 | 39.1164
| CO2 | EUR/MWh-h | 1.6901 | 0 | 0 | 16.8214 | 8.9128 | 0 | 0 | 1.6901 | 11.571 | 0
| CH4 | EUR/MWh-h | 0.02697 | 0 | 0 | 0.00026843 | 0.00046909 | 0 | 0.0017369 | 0.02697 | 0 | 0
| N2O | EUR/MWh-h | 0.0093764 | 0 | 0.00023685 | 0.00014316 | 0.00015636 | 0.00025165 | 0.00047369 | 0.0093764 | 0 | 0.00019641
| SO2 | EUR/MWh-h | 0.36572 | 0 | 0.00076235 | 0.4 | 0.020971 | 0 | 0.00050824 | 0.36572 | 0.034951 | 0
| NOX | EUR/MWh-h | 0.48428 | 0 | 3.5471 | 1.4 | 0.31456 | 1.1812 | 2.5412 | 0.48428 | 0.87379 | 2.3707
| PM2.5 | EUR/MWh-h | 0.014066 | 0 | 0.079412 | 0.1 | 0 | 0.084375 | 0.052941 | 0.014066 | 0.034951 | 0.065854
| Electricity revenue | EUR/MWh-h | 0 | 0 | -36.0605 | 0 | 0 | -42.915 | 0 | 0 | 0 | -16.0931
Total LCOE | Levelized cost | EUR/MWh-h | 25.7889 | 28.7195 | 41.9024 | 44.7349 | 44.9644 | 47.134 | 47.2669 | 50.708 | 66.1812 | 70.8354
|  | Unit | Electric heat pump (4 MW-h) | Solar - large (Pit thermal storage) (45000 m2) | Large CHP - straw (90 MW-h) | Boiler - coal (5 MW-h) | Boiler - natural gas (5.3 MW-h) | Large CHP - wood pellets (522 MW-h) | Boiler - straw (6 MW-h) | Geothermal (10 MW-h) | Boiler - oil (5 MW-h) | Small CHP - wood pellets (16 MW-h)
| Capital cost | EUR/MWh-e | 0 | 0 | 60.3096 | 0 | 0 | 54.3969 | 0 | 0 | 0 | 146.6351
| Fixed O&M | EUR/MWh-e | 0 | 0 | 31.225 | 0 | 0 | 21.3333 | 0 | 0 | 0 | 91.9667
| Var O&M | EUR/MWh-e | 0 | 0 | 1.9 | 0 | 0 | 1.6 | 0 | 0 | 0 | 3.4
| Fuel cost | EUR/MWh-e | 0 | 0 | 69.7406 | 0 | 0 | 100.2359 | 0 | 0 | 0 | 208.621
| CO2 | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O | EUR/MWh-e | 0 | 0 | 0.00051991 | 0 | 0 | 0.0005033 | 0 | 0 | 0 | 0.0010475
| SO2 | EUR/MWh-e | 0 | 0 | 0.0016735 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX | EUR/MWh-e | 0 | 0 | 7.7862 | 0 | 0 | 2.3625 | 0 | 0 | 0 | 12.6439
| PM2.5 | EUR/MWh-e | 0 | 0 | 0.17432 | 0 | 0 | 0.16875 | 0 | 0 | 0 | 0.35122
| DH revenue | EUR/MWh-e | 0 | 0 | -87.8049 | 0 | 0 | -80 | 0 | 0 | 0 | -213.3333
Total LCOE | Levelized cost | EUR/MWh-e | 0 | 0 | 83.3331 | 0 | 0 | 100.0978 | 0 | 0 | 0 | 250.2856
|  | Unit | Electric heat pump (4 MW-h) | Solar - large (Pit thermal storage) (45000 m2) | Large CHP - straw (90 MW-h) | Boiler - coal (5 MW-h) | Boiler - natural gas (5.3 MW-h) | Large CHP - wood pellets (522 MW-h) | Boiler - straw (6 MW-h) | Geothermal (10 MW-h) | Boiler - oil (5 MW-h) | Small CHP - wood pellets (16 MW-h)
| Capital cost | EUR/MWh-h | 15.6095 | 24.7195 | 27.4744 | 9.6291 | 8.5143 | 27.1984 | 12.6295 | 36.8953 | 8.5143 | 27.4941
| Fuel cost | EUR/MWh-h | 3.7222 | 0 | 31.7707 | 10.504 | 22.2012 | 50.1179 | 21.1805 | 3.7222 | 40.1522 | 39.1164
| O&M cost | EUR/MWh-h | 3.8667 | 4 | 15.0903 | 5.88 | 5 | 11.4667 | 10.86 | 7.5 | 5 | 17.8813
| CO2 emissions | EUR/MWh-h | 1.6901 | 0 | 0 | 16.8214 | 8.9128 | 0 | 0 | 1.6901 | 11.571 | 0
| Climate externalities | EUR/MWh-h | 0.036346 | 0 | 0.00023685 | 0.00041159 | 0.00062546 | 0.00025165 | 0.0022106 | 0.036346 | 0 | 0.00019641
| Air pollution | EUR/MWh-h | 0.86407 | 0 | 3.6272 | 1.9 | 0.33553 | 1.2656 | 2.5946 | 0.86407 | 0.94369 | 2.4366
| Electricity sale revenue | EUR/MWh-h | 0 | 0 | -36.0605 | 0 | 0 | -42.915 | 0 | 0 | 0 | -16.0931
Total LCOE | Total LCOE | EUR/MWh-h | 25.7889 | 28.7195 | 41.9024 | 44.7349 | 44.9644 | 47.134 | 47.2669 | 50.708 | 66.1812 | 70.8354
|  | Unit | Electric heat pump (4 MW-h) | Solar - large (Pit thermal storage) (45000 m2) | Large CHP - straw (90 MW-h) | Boiler - coal (5 MW-h) | Boiler - natural gas (5.3 MW-h) | Large CHP - wood pellets (522 MW-h) | Boiler - straw (6 MW-h) | Geothermal (10 MW-h) | Boiler - oil (5 MW-h) | Small CHP - wood pellets (16 MW-h)
| Capital cost | EUR/MWh-e | 0 | 0 | 60.3096 | 0 | 0 | 54.3969 | 0 | 0 | 0 | 146.6351
| Fuel cost | EUR/MWh-e | 0 | 0 | 69.7406 | 0 | 0 | 100.2359 | 0 | 0 | 0 | 208.621
| O&M cost | EUR/MWh-e | 0 | 0 | 33.125 | 0 | 0 | 22.9333 | 0 | 0 | 0 | 95.3667
| CO2 emissions | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Climate externalities | EUR/MWh-e | 0 | 0 | 0.00051991 | 0 | 0 | 0.0005033 | 0 | 0 | 0 | 0.0010475
| Air pollution | EUR/MWh-e | 0 | 0 | 7.9622 | 0 | 0 | 2.5312 | 0 | 0 | 0 | 12.9951
| DH revenue | EUR/MWh-e | 0 | 0 | -87.8049 | 0 | 0 | -80 | 0 | 0 | 0 | -213.3333
Total LCOE | Total LCOE | EUR/MWh-e | 0 | 0 | 83.3331 | 0 | 0 | 100.0978 | 0 | 0 | 0 | 250.2856
3.3.2 Individual technologies
|  | Unit | Solar heating | Gas boiler | Oil boiler | Wood pellet boiler | Wood stove | Heat pump - air to air | Heat pump - air to water | Heat pump - brine to water | Gas driven heat pump - brine to water | Electric heating
Technical data | Fuel |  | Solar | Natural gas | Oil | Wood pellets | Local wood | Electricity | Electricity | Electricity | Natural gas | Electricity
| Lifetime | years | 25 | 20 | 20 | 20 | 20 | 12 | 18 | 20 | 20 | 30
| Heat capacity | MW-h | --- | 0.01 | 0.015 | 0.01 | 0.005 | 0.004 | 0.01 | 0.01 | 0.03 | 0.003
| Solar thermal size | m2 panel | 5 | --- | --- | --- | --- | --- | --- | --- | --- | ---
| Heat efficiency | % | --- | 0.97 | 0.92 | 0.82 | 0.7 | 5.1 | 4.1 | 4.5 | 1.45 | 1
Operation | Full load hours | hours/year | --- | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
| Expected solar production | kWh/m2/year | 500 | --- | --- | --- | --- | --- | --- | --- | --- | ---
Production | Heat production | MW-h/year | 2.5 | 30 | 45 | 30 | 15 | 12 | 30 | 30 | 90 | 9
| Fuel consumption | MWh-f/year | 0 | 30.9278 | 48.913 | 36.5854 | 21.4286 | 2.3529 | 7.3171 | 6.6667 | 62.069 | 9
Emissions from fuel | CO2 equivalent (CH4) | kg CO2/kg emission | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
| CO2 equivalent (N2O) | kg CO2/kg emission | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298
| CO2 emission | kg/MWh-f | --- | 205.2 | 266.4 | 0 | 0 | --- | --- | --- | 205.2 | ---
| SO2 emission | kg/MWh-f | --- | 0 | 0.252 | 0 | 0 | --- | --- | --- | 0 | ---
| Emission factor CH4 | kg/MWh-f | --- | 3.6 | 0 | 7.2 | 450 | --- | --- | --- | 3.6 | ---
| Emission factor N2O | kg/MWh-f | --- | 0 | 0 | 14.4 | 14.4 | --- | --- | --- | 0 | ---
| Emission factor SO2 | kg/MWh-f | --- | 0 | 1.8 | 90 | 90 | --- | --- | --- | 0 | ---
| Emission factor NOX | kg/MWh-f | --- | 36 | 108 | 252 | 324 | --- | --- | --- | 36 | ---
| Emission factor PM2.5 | kg/MWh-f | --- | 0 | 0.072 | 54 | 144 | --- | --- | --- | 0 | ---
Emissions from electricity | CO2 | kg/MWh-e | --- | --- | --- | --- | --- | 136 | 136 | 136 | --- | 136
| CH4 | g/MWh-e | --- | --- | --- | --- | --- | 86.8085 | 86.8085 | 86.8085 | --- | 86.8085
| N2O | g/MWh-e | --- | --- | --- | --- | --- | 86.8085 | 86.8085 | 86.8085 | --- | 86.8085
| SO2 | g/MWh-e | --- | --- | --- | --- | --- | 86.8085 | 86.8085 | 86.8085 | --- | 86.8085
| NOX | g/MWh-e | --- | --- | --- | --- | --- | 86.8085 | 86.8085 | 86.8085 | --- | 86.8085
| PM2.5 | g/MWh-e | --- | --- | --- | --- | --- | 86.8085 | 86.8085 | 86.8085 | --- | 86.8085
Emissions | CO2 | ton | 0 | 6.3464 | 13.0304 | 0 | 0 | 0.32 | 0.99512 | 0.90667 | 12.7366 | 1.224
| CH4 | kg CO2-equivalent | 0 | 0.11134 | 0 | 0.26341 | 9.6429 | 5.1064 | 15.8796 | 14.4681 | 0.22345 | 19.5319
| N2O | kg CO2-equivalent | 0 | 0 | 0 | 0.52683 | 0.30857 | 60.8681 | 189.2849 | 172.4596 | 0 | 232.8204
| SO2 | kg | 0 | 0 | 0.088043 | 3.2927 | 1.9286 | 0.20426 | 0.63518 | 0.57872 | 0 | 0.78128
| NOX | kg | 0 | 1.1134 | 5.2826 | 9.2195 | 6.9429 | 0.20426 | 0.63518 | 0.57872 | 2.2345 | 0.78128
| PM2.5 | kg | 0 | 0 | 0.0035217 | 1.9756 | 3.0857 | 0.20426 | 0.63518 | 0.57872 | 0 | 0.78128
Investment | Investment (heat) | mil. EUR/MW-h | --- | 0.31 | 0.39 | 0.68 | 0.5 | 0.45 | 0.94 | 1.5 | 0.98 | 0.96
| Investment (solar) | mil. EUR/m2 panel | 0.0005 | --- | --- | --- | --- | --- | --- | --- | --- | ---
Fixed O&M | Fixed O&M (heat) | EUR/MW-heat/year | --- | 20500 | 16266 | 50400 | 29000 | 40500 | 27800 | 27800 | 15666 | 8000
| Fixed O&M (solar) | EUR/m2 panel/year | 9 | --- | --- | --- | --- | --- | --- | --- | --- | ---
Var. O&M | Var. O&M (heat) | EUR/MWh-h | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fuel price | Fuel price | EUR/MWh-f | 0 | 26.8672 | 45.3568 | 33.0755 | 50 | 0 | 0 | 0 | 26.8672 | 0
Emission prices | CO2 | EUR/ton | 44.7377 | 44.7377 | 44.7377 | 44.7377 | 44.7377 | 44.7377 | 44.7377 | 44.7377 | 44.7377 | 44.7377
| SO2 | EUR/kg | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
| NOX | EUR/kg | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| PM2.5 | EUR/kg | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Electricity prices | Voltage connection level |  | --- | --- | --- | --- | --- | Low voltage level | Low voltage level | Low voltage level | --- | Low voltage level
| Tariff | EUR/MWh-e | 0 | 0 | 0 | 0 | 0 | 23.4 | 23.4 | 23.4 | 0 | 23.4
| Electricity price | EUR/MWh-h | 60.8137 | 60.8137 | 60.8137 | 60.8137 | 60.8137 | 60.8137 | 60.8137 | 60.8137 | 60.8137 | 60.8137
| Electricity price (consumption) | EUR/MWh-h | --- | --- | --- | --- | --- | 84.2137 | 84.2137 | 84.2137 | --- | 84.2137
Total cost | Capital cost | mil. EUR/year | 0.00017738 | 0.00024875 | 0.00046942 | 0.00054565 | 0.00020061 | 0.00020309 | 0.00080413 | 0.0012036 | 0.0023591 | 0.00018735
| Fixed O&M | mil. EUR/year | 4.5e-05 | 0.000205 | 0.00024399 | 0.000504 | 0.000145 | 0.000162 | 0.000278 | 0.000278 | 0.00046998 | 2.4e-05
| Var O&M | mil. EUR/year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel cost | mil. EUR/year | 0 | 0.00083094 | 0.0022185 | 0.0012101 | 0.0010714 | 0.00019815 | 0.0006162 | 0.00056142 | 0.0016676 | 0.00075792
| CO2 | mil. EUR/year | 0 | 0.00028392 | 0.00058295 | 0 | 0 | 1.4316e-05 | 4.4519e-05 | 4.0562e-05 | 0.0005698 | 5.4759e-05
| CH4 | mil. EUR/year | 0 | 4.9811e-09 | 0 | 1.1785e-08 | 4.314e-07 | 2.2845e-07 | 7.1042e-07 | 6.4727e-07 | 9.9966e-09 | 8.7381e-07
| N2O | mil. EUR/year | 0 | 0 | 0 | 2.3569e-08 | 1.3805e-08 | 2.7231e-06 | 8.4682e-06 | 7.7154e-06 | 0 | 1.0416e-05
| SO2 | mil. EUR/year | 0 | 0 | 1.7609e-06 | 6.5854e-05 | 3.8571e-05 | 4.0851e-06 | 1.2704e-05 | 1.1574e-05 | 0 | 1.5626e-05
| NOX | mil. EUR/year | 0 | 1.1134e-05 | 5.2826e-05 | 9.2195e-05 | 6.9429e-05 | 2.0426e-06 | 6.3518e-06 | 5.7872e-06 | 2.2345e-05 | 7.8128e-06
| PM2.5 | mil. EUR/year | 0 | 0 | 1.7609e-07 | 9.878e-05 | 0.00015429 | 1.0213e-05 | 3.1759e-05 | 2.8936e-05 | 0 | 3.9064e-05
|  | Unit | Solar heating (5 m2) | Gas boiler (10 kW-h) | Oil boiler (15 kW-h) | Wood pellet boiler (10 kW-h) | Wood stove (5 kW-h) | Heat pump - air to air (4 kW-h) | Heat pump - air to water (10 kW-h) | Heat pump - brine to water (10 kW-h) | Gas driven heat pump - brine to water (30 kW-h) | Electric heating (3 kW-h)
Heat production cost | Capital cost | TRUE | 70.9525 | 8.2917 | 10.4315 | 18.1883 | 13.3738 | 16.9238 | 26.8045 | 40.1213 | 26.2126 | 20.8165
| Fixed O&M | TRUE | 18 | 6.8333 | 5.422 | 16.8 | 9.6667 | 13.5 | 9.2667 | 9.2667 | 5.222 | 2.6667
| Var O&M | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel cost | TRUE | 0 | 27.6981 | 49.3009 | 40.336 | 71.4286 | 16.5125 | 20.5399 | 18.7142 | 18.5291 | 84.2137
| CO2 | TRUE | 0 | 9.4641 | 12.9545 | 0 | 0 | 1.193 | 1.484 | 1.3521 | 6.3312 | 6.0843
| CH4 | TRUE | 0 | 0.00016604 | 0 | 0.00039282 | 0.02876 | 0.019037 | 0.023681 | 0.021576 | 0.00011107 | 0.09709
| N2O | TRUE | 0 | 0 | 0 | 0.00078564 | 0.00092032 | 0.22692 | 0.28227 | 0.25718 | 0 | 1.1573
| SO2 | TRUE | 0 | 0 | 0.03913 | 2.1951 | 2.5714 | 0.34043 | 0.42346 | 0.38582 | 0 | 1.7362
| NOX | TRUE | 0 | 0.37113 | 1.1739 | 3.0732 | 4.6286 | 0.17021 | 0.21173 | 0.19291 | 0.24828 | 0.86809
| PM2.5 | TRUE | 0 | 0 | 0.003913 | 3.2927 | 10.2857 | 0.85106 | 1.0586 | 0.96454 | 0 | 4.3404
Total LCOE | Levelized cost | EUR/MWh-h | 88.9525 | 52.6586 | 79.3258 | 83.8864 | 111.9844 | 49.737 | 60.0948 | 71.2762 | 56.5432 | 121.9803
|  |  | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1
|  | Unit | Heat pump - air to air (4 kW-h) | Gas boiler (10 kW-h) | Gas driven heat pump - brine to water (30 kW-h) | Heat pump - air to water (10 kW-h) | Heat pump - brine to water (10 kW-h) | Oil boiler (15 kW-h) | Wood pellet boiler (10 kW-h) | Solar heating (5 m2) | Wood stove (5 kW-h) | Electric heating (3 kW-h)
| Capital cost | EUR/MWh-h | 16.9238 | 8.2917 | 26.2126 | 26.8045 | 40.1213 | 10.4315 | 18.1883 | 70.9525 | 13.3738 | 20.8165
| Fixed O&M | EUR/MWh-h | 13.5 | 6.8333 | 5.222 | 9.2667 | 9.2667 | 5.422 | 16.8 | 18 | 9.6667 | 2.6667
| Var O&M | EUR/MWh-h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel cost | EUR/MWh-h | 16.5125 | 27.6981 | 18.5291 | 20.5399 | 18.7142 | 49.3009 | 40.336 | 0 | 71.4286 | 84.2137
| CO2 | EUR/MWh-h | 1.193 | 9.4641 | 6.3312 | 1.484 | 1.3521 | 12.9545 | 0 | 0 | 0 | 6.0843
| CH4 | EUR/MWh-h | 0.019037 | 0.00016604 | 0.00011107 | 0.023681 | 0.021576 | 0 | 0.00039282 | 0 | 0.02876 | 0.09709
| N2O | EUR/MWh-h | 0.22692 | 0 | 0 | 0.28227 | 0.25718 | 0 | 0.00078564 | 0 | 0.00092032 | 1.1573
| SO2 | EUR/MWh-h | 0.34043 | 0 | 0 | 0.42346 | 0.38582 | 0.03913 | 2.1951 | 0 | 2.5714 | 1.7362
| NOX | EUR/MWh-h | 0.17021 | 0.37113 | 0.24828 | 0.21173 | 0.19291 | 1.1739 | 3.0732 | 0 | 4.6286 | 0.86809
| PM2.5 | EUR/MWh-h | 0.85106 | 0 | 0 | 1.0586 | 0.96454 | 0.003913 | 3.2927 | 0 | 10.2857 | 4.3404
Total LCOE | Levelized cost | EUR/MWh-h | 49.737 | 52.6586 | 56.5432 | 60.0948 | 71.2762 | 79.3258 | 83.8864 | 88.9525 | 111.9844 | 121.9803
|  | Unit | Heat pump - air to air (4 kW-h) | Gas boiler (10 kW-h) | Gas driven heat pump - brine to water (30 kW-h) | Heat pump - air to water (10 kW-h) | Heat pump - brine to water (10 kW-h) | Oil boiler (15 kW-h) | Wood pellet boiler (10 kW-h) | Solar heating (5 m2) | Wood stove (5 kW-h) | Electric heating (3 kW-h)
| Capital cost | EUR/MWh-h | 16.9238 | 8.2917 | 26.2126 | 26.8045 | 40.1213 | 10.4315 | 18.1883 | 70.9525 | 13.3738 | 20.8165
| Fuel cost | EUR/MWh-h | 16.5125 | 27.6981 | 18.5291 | 20.5399 | 18.7142 | 49.3009 | 40.336 | 0 | 71.4286 | 84.2137
| O&M cost | EUR/MWh-h | 13.5 | 6.8333 | 5.222 | 9.2667 | 9.2667 | 5.422 | 16.8 | 18 | 9.6667 | 2.6667
| CO2 emissions | EUR/MWh-h | 1.193 | 9.4641 | 6.3312 | 1.484 | 1.3521 | 12.9545 | 0 | 0 | 0 | 6.0843
| Climate externalities | EUR/MWh-h | 0.24596 | 0.00016604 | 0.00011107 | 0.30595 | 0.27876 | 0 | 0.0011785 | 0 | 0.02968 | 1.2544
| Air pollution | EUR/MWh-h | 1.3617 | 0.37113 | 0.24828 | 1.6938 | 1.5433 | 1.217 | 8.561 | 0 | 17.4857 | 6.9447
Total LCOE | Total LCOE | EUR/MWh-h | 49.737 | 52.6586 | 56.5432 | 60.0948 | 71.2762 | 79.3258 | 83.8864 | 88.9525 | 111.9844 | 121.9803

## 4. Energy storage
Back to user guide
4. Energy storage
List of contents
4. Energy storage
4.1 Hot water tanks (pressure-less)
4.2 Hot water tanks (pressurized)
4.3 Pit thermal energy storage
4.4 Cold storage
4.5 Subsurface gas storage
4.6 Pumped hydro storage
4.7 Electric batteries
4.8 New technology 1
4.9 New technology 2
4.10 Energy storage technology output
Assumptions applied (selected in 3.1 LCOE results)
Discount rate |  |  |  |  | 5% | %
Calculation period |  |  |  |  | 1
Start year of calculation |  |  |  |  | 2022
Electricity price development |  |  |  |  | Green
Expected solar thermal production |  |  |  |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  |  |  |  | Sustainable development scenario
Country |  |  |  |  | EU
Currency abbreviation |  |  |  |  | EUR
Currency factor |  |  |  |  | 1
Equipment |  |  |  |  | 1
Installation |  |  |  |  | 1
4.1 Hot water tanks (pressure-less)
Figure 4-1: The pressureless directly connected tank operates in a | [5 empty] | Figure 4-2: The largest tank is probably the 75.000 m3 pressure
simple way. The tank compensates automatically for the difference | [5 empty] | less hot water storage tank in Odense Denmark owend by
in flow in the supply pump and the production pump. | [5 empty] | Fjernvarme Fyn.
4.1.1 Technical- and economic assumptions
The comparison of tanks in the table above show the economy of scale factor for tanks, e.g. that a tank at the building level is more expensive than a tank for DH.
Table 4-1: Technical- and economic assumptions for a pressure-less hot water tank [14]
Unit
Efficient volume |  |  | m3 |  | 0.5 | 1 | 10 | 100 | 1000 | 10000 | 20000 | 50000 | 100000
Diameter, if D/H=1 |  |  | m |  | 0.81932 | 1.0323 | 2.224 | 4.7914 | 10.3228 | 22.2398 | 28.0204 | 38.0295 | 47.9142
Type of use |  |  |  |  | Building | Building | Building | DH | DH | DH | DH | DH | DH
Maximal supply temperature |  |  | oC |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Return temperature |  |  | oC |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Energy capacity |  |  | MWh |  | 0.0319 | 0.0638 | 0.638 | 6.38 | 63.8 | 638 | 1276 | 3190 | 6380
Max load hours design size |  |  | h |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Normal load/unload capacity |  |  | MW |  | 0.0039875 | 0.007975 | 0.07975 | 0.7975 | 7.975 | 79.75 | 159.5 | 398.75 | 797.5
Heat losses stand-by |  |  | MWh/a |  | 13.7453 | 17.318 | 37.3105 | 80.383 | 173.1798 | 373.1047 | 470.0824 | 638 | 957
Stand-by losses per volume |  |  | MWh/MWh |  | 430.8869 | 271.4418 | 58.4804 | 12.5992 | 2.7144 | 0.5848 | 0.3684 | 0.2 | 0.15
Heat losses per load cycle |  |  | % |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Temperature losses per cycle |  |  | oC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Investment per energy content |  |  | 1000 EUR/MWh |  | 60.0649 | 60.0649 | 60.0649 | 6.2143 | 5.3571 | 4.4643 | 4.0179 | 4.0179 | 4.0179
Investment |  |  | 1000 EUR |  | 1.9161 | 3.8321 | 38.3214 | 39.6471 | 341.7857 | 2848.2143 | 5126.7857 | 12816.9643 | 25633.9286
Fixed O&M, pct. Of investment |  |  | % |  | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Variable O&M |  |  | EUR/MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Life time |  |  | years |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Investment per energy content |  |  | 1000 EUR/MWh |  | 60.0649 | 60.0649 | 60.0649 | 6.2143 | 5.3571 | 4.4643 | 4.0179 | 4.0179 | 4.0179
Investment |  |  | 1000 EUR |  | 1.9161 | 3.8321 | 38.3214 | 39.6471 | 341.7857 | 2848.2143 | 5126.7857 | 12816.9643 | 25633.9286
Variable O&M |  |  | EUR/MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.2 Hot water tanks (pressurized)
Figure 4-3: This tank is sectioned from the pressure in the network. | [5 empty] | Figure 4-4: Thermal storage at Avedøre CHP plant
The operater has to start and stop loading and unloading.
4.2.1 Technical- and economic assumptions
Table 4-2: Technical- and economic assumptions for a pressurized hot water tank [1]
Unit
Efficient volume |  |  | m3 |  | 1000 | 10000 | 20000 | 50000
Diameter, if D/H=1 |  |  | m |  | 10.3228 | 22.2398 | 28.0204 | 38.0295
Type of use |  |  |  |  | DH | DH | DH | DH
Maximal supply temperature |  |  | oC |  | 120 | 120 | 120 | 120
Return temperature |  |  | oC |  | 50 | 50 | 50 | 50
Energy capacity |  |  | MWh |  | 81.2 | 812 | 1624 | 4060
Max load hours design size |  |  | h |  | 8 | 8 | 8 | 8
Normal load/unload capacity |  |  | MW |  | 10.15 | 101.5 | 203 | 507.5
Heat losses stand-by |  |  | MWh/a |  | 275.5134 | 593.5756 | 747.8584 | 1015
Stand-by losses per volume |  |  | MWh/MWh |  | 3.393 | 0.731 | 0.4605 | 0.25
Heat losses per load cycle |  |  | % |  | 0% | 0% | 0% | 0%
Temperature losses per cycle |  |  | oC |  | 0 | 0 | 0 | 0
Investment per energy content |  |  | 1000 EUR/MWh |  | 6.0071 | 5.8 | 4.5571 | 4.4643
Investment |  |  | 1000 EUR |  | 487.78 | 4709.6 | 7400.8 | 18125
Fixed O&M, pct. Of investment |  |  | % |  | 1% | 1% | 1% | 1%
Variable O&M |  |  | EUR/MWh |  | 0 | 0 | 0 | 0
Life time |  |  | years |  | 60 | 60 | 60 | 60
Investment per energy content |  |  | 1000 EUR/MWh |  | 6.0071 | 5.8 | 4.5571 | 4.4643
Investment |  |  | 1000 EUR |  | 487.78 | 4709.6 | 7400.8 | 18125
Variable O&M |  |  | EUR/MWh |  | 0 | 0 | 0 | 0
4.3 Pit thermal energy storage
Figure 4-3: Pit thermal energy storage
4.3.1 Technical- and economic assumptions
Table 4-3: Technical- and economic assumptions for a pit thermal energy storage [1]
Unit
Efficient volume |  |  | m3 |  | 10000 | 20000 | 50000 | 100000 | 200000
Type of use |  |  |  |  | DH | DH | DH | DH | DH
Maximal supply temperature |  |  | oC |  | 85 | 85 | 85 | 85 | 85
Return temperature |  |  | oC |  | 40 | 40 | 40 | 40 | 40
Energy capacity |  |  | MWh |  | 522 | 1044 | 2610 | 5220 | 10440
Max load hours design size |  |  | h |  | 100 | 100 | 100 | 100 | 100
Normal load/unload capacity |  |  | MW |  | 5.22 | 10.44 | 26.1 | 52.2 | 104.4
Heat losses stand-by |  |  | MWh/a |  | 522 | 626.4 | 1044 | 1566 | 2088
Stand-by losses per volume |  |  | MWh/MWh |  | 1 | 0.6 | 0.4 | 0.3 | 0.2
Heat losses per load cycle |  |  | % |  | 0 | 0 | 0 | 0 | 0
Temperature losses per cycle |  |  | oC |  | 0 | 0 | 0 | 0 | 0
Investment per energy content |  |  | 1000 EUR/MWh |  | 1.25 | 1.1607 | 1.0714 | 0.98214 | 0.89286
Investment |  |  | 1000 EUR |  | 652.5 | 1211.7857 | 2796.4286 | 5126.7857 | 9321.4286
Fixed O&M, pct. Of investment |  |  | % |  | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Variable O&M |  |  | EUR/MWh |  | 0 | 0 | 0 | 0 | 0
Life time |  |  | years |  | 25 | 25 | 25 | 25 | 25
Investment per energy content |  |  | 1000 EUR/MWh |  | 1.25 | 1.1607 | 1.0714 | 0.98214 | 0.89286
Investment |  |  | 1000 EUR |  | 652.5 | 1211.7857 | 2796.4286 | 5126.7857 | 9321.4286
Variable O&M |  |  | EUR/MWh |  | 0 | 0 | 0 | 0 | 0
4.4 Cold storage
Figure 4-6: Steel tank, concrete chamber and ATES
4.4.1 Technical- and economic assumptions
Table 4-4: Technical- and economic assumptions for ATES [14]
Technology |  |  |  | ATES
|  |  |  | Unit |  | 2020
Energy/technical data
Heat generation capacity for one unit |  |  |  | MW-c |  | 1-10
COP ATES cooling | [5 empty] | 40
Financial data
Nominal investment |  |  |  | M€/drill hole pair |  | 0.5
Fixed O&M |  |  |  | €/MW-c/year |  | 0
Variable O&M (€/MWh) |  |  |  | €/MWh-c |  | 0
Investment per energy content |  |  |  | MEUR/drill hole pair |  | 0.5
Investment |  |  |  | EUR/MW-c/year |  | 0
Variable O&M |  |  |  | EUR/MWh-c |  | 0
4.5 Subsurface gas storage
4.5.1 Technical- and economic assumptions
Table 4-5: Technical- and economic assumptions for a gas cavern [1]
Plant for cavern leaching | [5 empty] | Plant for cavern leaching
|  |  |  | Mill. € | [5 empty] | Mill. EUR
Total |  |  |  | 9.9 |  | Total |  |  |  | 9.9
Establishment of one cavern, 100 million Nm3 (approx. 1.1 TWh) | [5 empty] | Establishment of one cavern, 100 million Nm3 (approx. 1.1 TWh)
|  |  |  | Mill. € | [5 empty] | Mill. EUR
Construction and equipment |  |  |  | 22 |  | Construction and equipment |  |  |  | 22
Cushion gas for one cavern (40% of total) |  |  |  | 14 |  | Cushion gas for one cavern (40% of total) |  |  |  | 14
Total cost, 100 mio Nm3 active volume |  |  |  | 36 |  | Total cost, 100 mio Nm3 active volume |  |  |  | 36
Process equipment; injection 200,000 Nm3/hour (approx. 2200 MW), withdrawal 600,000 nM3/hour (approx. 6600 MW) | [5 empty] | Process equipment; injection 200,000 Nm3/hour (approx. 2200 MW), withdrawal 600,000 nM3/hour (approx. 6600 MW)
|  |  |  | Mill. € | [5 empty] | Mill. EUR
Construction work |  |  |  | 2.8 |  | Construction work |  |  |  | 2.8
Compressors, incl. auxiliaries |  |  |  | 30 |  | Compressors, incl. auxiliaries |  |  |  | 30
Udtrækstog |  |  |  | 13 |  | Udtrækstog |  |  |  | 13
Withdrawal equipment |  |  |  | 4.5 |  | Withdrawal equipment |  |  |  | 4.5
Connections, transformer, regulation, and instruments |  |  |  | 13 |  | Connections, transformer, regulation, and instruments |  |  |  | 13
Total investment cost |  |  |  | 63 |  | Total investment cost |  |  |  | 63
A new greenfield store, equivalent to Lille Torup in Denmark, would require one leaching plant, 5 caverns, and one process plant. | [5 empty] | A new greenfield store, equivalent to Lille Torup in Denmark, would require one leaching plant, 5 caverns, and one process plant.
|  |  |  | Mill. € | [5 empty] | Mill. EUR
Total investment cost |  |  |  | 254 |  | Total investment cost |  |  |  | 254
Operation and maintenace, salt cavern, 400-500 million m3 working gas | [5 empty] | Operation and maintenace, salt cavern, 400-500 million m3 working gas
|  |  |  | Mill. € per year | [5 empty] | Mill. EUR
Electricity |  |  |  | 0.9 |  | Electricity |  |  |  | 0.9
Gas consumption to reheat extracted gas |  |  |  | 0.13 |  | Gas consumption to reheat extracted gas |  |  |  | 0.13
Total, incl. administration |  |  |  | 6.5 |  | Total, incl. administration |  |  |  | 6.5
4.6 Pumped hydro storage
4.6.1 Technical- and economic assumptions
Table 4-6: Technical- and economic assumptions for a pumped hydro storage [1]
Technology |  |  |  |  | Pumped hydro storage
|  |  | Unit |  | 2020
Energy/technical data
Generating capacity |  |  | MW |  | 10-1000
Total efficiency net |  |  | % |  | 70-80
Technical lifetime |  |  | years |  | 50
Construction time |  |  | years |  | 2-3
Financial data
Investment, pump part |  |  | M€/MW |  | 0.6
Investment, total, greenfield part |  |  | M€/MW |  | 4
Fixed O&M- 1-2 % of investment |  |  | €/MW/year |  | 9000
Variable O&M |  |  | €/MWh |  | Depends on power price
Investment, pump part |  |  | EUR/MW |  | 0.6
Investment, total, greenfield part |  |  | EUR/MW |  | 4
Fixed O&M- 1-2 % of investment |  |  | EUR/MW/year |  | 9000
4.7 Electric batteries
4.7.1 Technical- and economic assumptions
Table 4-7: Technical- and economic assumptions for a Sodium Sulphur (NaS) battery [1]
Technology |  |  |  |  | Sodium Sulphurs (NaS)
|  |  | Unit |  | 2020
Energy/technical data
Storage capacity |  |  | MWh |  | 100
Generating capacity |  |  | MW |  | 10
Charge-discharge ratio
Cell efficiency |  |  | % |  | 60
System efficiency, AC to AC, net
Lifetime in full charge-discharge cycles
Technical lifetime |  |  | years |  | 15
Construction time |  |  | months |  | 6-8
Financial data
Specific investment, storage capacity |  |  | k€/MWh |  | 136
Specific investment, output capacity |  |  | M€/MW |  | 1.7
Fixed O&M |  |  | €/MW/year |  | 51000
Variable O&M |  |  | €/MWh |  | 5.3
Specific investment, storage capacity |  |  | k€/MWh |  | 136
Specific investment, output capacity |  |  | M€/MW |  | 1.7
Fixed O&M |  |  | €/MW/year |  | 51000
Variable O&M |  |  | €/MWh |  | 5.3
Specific investment, storage capacity |  |  | kEUR/MWh |  | 136
Specific investment, output capacity |  |  | EUR/MW |  | 1.7
Fixed O&M |  |  | EUR/MW/year |  | 51000
Variable O&M |  |  | EUR/MWh |  | 5.3
Table 4-8: Technical- and economic assumptions for a Vanadium Redox Battery (VRB) [1]
Technology |  |  |  |  | Vanadium Redox (VRB)
|  |  | Unit |  | 2020
Energy/technical data
Storage capacity |  |  | MWh
Generating capacity |  |  | MW |  | 10
System efficiency, DC to DC, net |  |  | %
System efficiency, AC to AC, net |  |  | %
Lifetime in full charge-discharge cycles
Construction time |  |  | months |  | 6-8
Financial data
Specific investment, storage volume |  |  | k€/MWh |  | 51
Specific investment, output capacity |  |  | M€/MW |  | 1.1
Fixed O&M |  |  | €/MW/year |  | 54000
Variable O&M |  |  | €/MWh |  | 2.8
Specific investment, storage capacity |  |  | kEUR/MWh |  | 51
Specific investment, output capacity |  |  | EUR/MW |  | 1.1
Fixed O&M |  |  | EUR/MW/year |  | 54000
Variable O&M |  |  | EUR/MWh |  | 2.8
4.8 New technology 1
4.8.1 Technical and economic assumptions
4.9 New technology 2
4.9.1 Technical and economic assumptions
4.10 Energy storage technology output
Technology | Reference | Electric capacity | Heat capacity | Solar thermal size | Storage size | Fuel | Voltage connection level | Full load hours |  |  | Investment (el) (eqiupment) | Investment (el) (installation) | Investment (heat) (equipment)
|  | MW-e | MW-h | m2 panel | m3 storage |  |  | Black | Blue | Green | mil. EUR/MW-el | mil. EUR/MW-el | mil. EUR/MW-heat
Tank thermal storage | Ramboll | --- | --- | --- | 3000 | --- | --- | --- | --- | --- | --- | --- | ---
Pit thermal storage | Ramboll | --- | --- | --- | 120000 | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Technology | Investment (heat) (installation) | Investment (solar) | Investment (storage) | Fixed O&M (el) | Fixed O&M (heat) | Fixed O&M (solar) | Fixed O&M (storage) | Var. O&M (el) | Var. O&M (heat) | Lifetime | CV | CB | Electric efficiency CHP
| mil. EUR/MW-heat | EUR/m2 panel | EUR/m3 storage | EUR/MW-el/year | EUR/MW-heat/year | EUR/m2 panel/year | EUR/m3 storage/year | EUR/MWh-el | EUR/MWh-heat | year |  |  | MW-el/MW-fuel
Tank thermal storage | --- | --- | 175 | --- | --- | --- | 0.5 | --- | --- | 40 | --- | --- | ---
Pit thermal storage | --- | --- | 50 | --- | --- | --- | 0.2 | --- | --- | 20 | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Technology | Heat efficiency CHP | Electric efficiency condensing | Heat efficiency | CO2 capture rate (amount of emission) | SO2 (degree of desulphuring) | Emission factor SO2 | Emission factor NOX | Emission factor CH4 | Emission factor N2O | Emission factor PM2.5
| MW-heat/MW-fuel | MW-el/MW-fuel | MW-heat/MW-fuel | % | % | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f
Tank thermal storage | --- | --- | --- | 0% | --- | --- | --- | --- | --- | ---
Pit thermal storage | --- | --- | --- | 0% | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Technology | Reference | Cooling storage capacity | Electric storage capacity | Electric storage energy | Cooling storage investment | Electric storage investment | Fixed O&M (electric storage) | Var. O&M (electric storage) | Efficiency | Lifetime
|  | MW-c | MW-e | MWh-e | M€/drill hole pair | M€/MW-e | €/MW-e/year | €/MWh-e | % | years
ATES | [1] | 5 | --- | --- | 0.5 | --- | --- | --- | 100% | 50
Pumped hydro | [1] | --- | 500 | --- | --- | 4.6 | 9000 | --- | 75% | 50
NaS battery | [1] | --- | 10 | 100 | --- | 1.7 | 51000 | 5.3 | 60% | 15
The biggest challenge in developing Net Zero Communities is not to generate renewable energy, but to use it.
The available renewable energy or surplus energy sources, which can contribute to forming Net Zero Communities, are normally not available when needed, and it can even be more expensive to store the energy than to generate it. A good example is that the renewable energy sources wind, solar and hydro can generate electricity, as the wind blows, the sun chines and the rain falls, whereas the power grid it selv can not store the electricity.
Therefore energy storages will play an important role.
In order to identify the most cost effective storage it is necessary to look both at the production , the real end-use demand and how its fluctuations deviates from the production. The dynamic fluctuations of the production in seconds, hours (sun), days, weeks (wind), months and years (dry and wet year) has to be taken into account. Load management and energy transformation has to be considered. In case heating or cooling is the final end-use, it is e.g. much more cost effective to transform the electricity to hot or cold water the moment is it generated and use thermal storages instead of electric batteries. In case gas or oil is the final end-use, it is also much more cost effective to transform the electricity to hydrogen, gas and oil and then store the energy in the form of gas or oil.
In this section we will compare the cost of all relevant energy storages and in the design of energy systems we will show a number of conceptual design concepts of integrated systems, which can store the fluctuating renewable energy.
Hot water pressure less tanks is the most common energy storage. This is because hot water is the end-use for most heating systems and for hot tap water and because water is a very natural and environmental friendly storage media. The tanks are normally constructed in steel, but it could also be in concrete, fiberglass reinforced plastic. Steel tanks for storage of hot water is a well-established technology, both in small houses and for large DH systems. Typically, a tank used in district heating is insulated with about 2x150 mm insulation(mineral wool).
In the last decades steel tanks have been used as short term storage in combination with combined heat and power plants, to be able to offset production to a more favorable time. For extraction CHP plants (which can generate power only) the storage allows the plant to stop heat generation and generate maximal power only when electricity is most expensive. For back pressure CHP plants or engines (fixed ratio between heat and power), it allows the plant to generate electricity and heat when the electricity is most expensive.
In Denmark, a combined heat and power plant typically operates at full capacity during the peak- and high-load hours of the electricity market, about 75 hours a week. Still, the plants often have heat storage capacity to cover the heat load for a full week during the cold season. The largest tanks are above 50.000 m3.
For a biomass plant a typical capacity would be 10 – 12 hours full load at peak demand on a cold winter day (service time needed for small repairs) or 72 hours on Summer load to allow for weekend stop and/or boiler inspection.
Water is the most cost effective way of storing low (0-20) to medium (20-100) temperature heat, because it is relatively cheap and convinient. Moreover, water has a very high specific heat capacity as well as a high volumetric heat capacity, compared to other commo n storage materials. This is important for a compact storage system.
The tank can also level the daiy fluctuations of the heat demand and thus also offer peak capaicty and improve resilience. Finally the tank can maintain the pressure in te network and offer storage capacity for make-up water.
The simplepressure less tank can be more advanced to meet the demand in two ways:
1) The temperature can be increased above the 100 oC
2) The pressure of tank can be sectioned from the network pressure
In case the DH end-users need super heated water, e.g. at 170 oC in order to generate low pressure steam for industry or to generate cooling in an absorption chiller and in case the production fluctuates like a waste incinerator, it can be an option, however very expensive and each tank the diameter of the tank must be smaller.
In case the building need close to 100 oC, it may also be necessary and optimal to operate heat transmission systems at temperatures up to e.g. 120 oC. In that case the price increase is more modest and the tank can be large.
In case the tank can not be used for pressure maintenance due to pressure difference and location, it is possible to seperate the pressure in the tank from the pressure in the network. Pumps and turbines/trottlevalves on each pipe and a pressure expansion vessel stabilizes the pressure while loading and unloading the tank.
An alternative to pressure section valves could be a heat exchanger with ability to change direction, however that would cost a temperature loss and be more expensive.
The heat storage tanks at Avedøre CHP plant in Copenhagen has the following data:
- 2 x 24,000 m3
- 120 oC max. supply temperature
- 330 MW load/unload capacity
- 10 Bar pressure difference from tank to network
Large volumes of gas may be stored in underground reservoirs or as liquefied gas in tanks (e.g. LNG - liquefied natural gas). There are three types of underground storage:
Depleted gas reservoirs are the most prominent and common form of underground storage. They are the reservoir formations of natural gas fields that have produced all their economically recoverable gas. The depleted reservoir formation is readily capable of holding injected natural gas. Using such a facility is economically attractive because it allows the re-use, with suitable modification, of the extraction and distribution infrastructure remaining from the productive life of the gas field which reduces the start-up costs. Depleted reservoirs are also attractive because their geological and physical characteristics have already been studied by geologists and petroleum engineers and are usually well known. Consequently, depleted reservoirs are generally the cheapest and easiest to develop, operate, and maintain of the three types of underground storage. However, off-shore depleted gas fields are generally quite expensive.
Aquifer reservoirs are underground, porous and permeable rock formations that act as natural water reservoirs. In some cases they can be used for natural gas storage. Usually these facilities are operated on a single annual cycle as with depleted reservoirs. The geological and physical characteristics of aquifer formation are not known ahead of time and a significant investment has to go into investigating these and evaluating the aquifer’s suitability for natural gas storage.
Salt caverns allow no gas to escape from storage. The walls of a salt cavern are strong and impervious to gas over the lifespan of the storage facility. Once a suitable salt feature is discovered and found to be suitable for the development of a gas storage facility a cavern is created within the salt feature. This is done by the process of cavern leaching. Fresh water is pumped down a borehole into the salt. Some of the salt is dissolved leaving a void and the water, now saline, is pumped back to the surface. The process continues until the cavern is the desired size. Once created, a salt cavern offers an underground natural gas storage vessel with very high deliverability. Cushion gas requirements are low, typically about 33 percent of total gas capacity.
For bulk electricity storage in utility grids, pumped hydro power plants dominate, with approximately 100 GW in service around the globe.
A typical pumped hydro store (PHS) consists of two water reservoirs (lakes), tunnels that convey water from one reservoir to another, a reversible pump-turbine, a motor-generator, transformers, and transmission connection. The amount of stored electricity is proportional to the product of the volume of water and the height between the reservoirs. As an example, storing 1,000 MWh requires an elevation change of 300 m and a water volume of about 1.4 million m3.
A new PHS, including dams, has high capital expenditures and a long construction time. If an existing hydro plant is extended to also be a PHS, the investment per installed MW is significantly lower and the construction time between 2 and 3 years.
With this technology electricity is basically stored as potential energy. Others ways of storing electricity as potential energy may have similar characteristics.
There are several technologies available or being developed for storing electricity. To the right is a classification of a selection of these technologies regarding their capacities and discharge times.
The battery technology with the broadest base of applications today is the lithium-ion battery, used e.g. in laptop computers and electric vehicles. The ability of lithium-ion batteries to economically serve electric utility applications has not yet been demonstrated, except for some ancillary services provisions to independent system operators. Three main battery types are most relevant for large-scale electricity storage:
- Advanced lead acid batteries
- NaS (Sodium Sulphur) batteries
- Flow batteries, in particular:
o Vanadium Redox (VRB)
o Zinc-bromine (ZnBr)
The lead-acid battery is one of the oldest and most developed battery technologies. A lead-acid battery is an electrical storage device that uses a combination of lead plates or grids and an electrolyte. consisting of a diluted sulphuric acid to convert electrical energy into potential chemical energy and back again.
The sodium sulphur (NaS) battery is a high-temperature (about 300 °C) battery system that consists of a molten sulphur positive electrode and a molten sodium negative electrode separated by a solid ceramic electrolyte.
During discharge, positive sodium ions flow through the electrolyte and electrons flow in the external circuit of the battery, producing about 2 V. This process is reversible. Flow batteries utilize an active element in a liquid electrolyte that is pumped through a membrane similar to a fuel cell to produce an electrical current.
The system’s power rating is determined by the size and number of membranes, and the runtime (hours) is based on the volume of electrolyte pumped through the membranes. Pumping in one direction produces power from the battery, and reversing the flow charges the system.
The Vanadium redox battery (VRB) is based on vanadium as the only element, and is based on the reduction and oxidation of the different ionic forms of Vanadium. Energy can be stored indefinitely in a liquid – very low self-discharge. The Zinc-bromine (ZnBr) battery is based on cells with two different electrolytes flowing past carbon-plastic composite electrodes in two compartments separated by a microporous polyolefin membrane. For batteries to be practically applied in the utility grid, reliable power conversion systems (PCSs) that convert AC power to battery DC and back to AC are needed.
A cold water storage tank can be located next to the energy center. Usually, the size of the cold water storage tank is designed to even out daily fluctuations in the electricity price. So, whenthe electricity price (and distribution tariffs) are low, the chiller or combined heating and cooling heat pumps cna produce extra cooling that can be stored in the tank. In high price periods, the tank can be dischraged instead of production. The following tachnologies are relevant:
- A steel tank (similar to the district heating technology)
- A concrete chamber (similar to the water supply technology)
- ATES (Aquifer Thermal Energy Storage) also called ground source cooling
- A large pit storage filled with cold water instead of hot water
The financial costs for a cold water storage tank and a cold water storage pit are the same as for the hot water equivalent.
A cold water pit storage can be used in a factory with a large cooling demand and large differences between day and night charges of the electricity.
The hot water storage pit is developed in projects to district heating companies, who want to increase the share of solar water heating from around 20% to 50% or more. This technology has after the first 6 full scale demonstration plants in Denmark been developed to be commercial in Danish market conditions with tax on natural gas without subsidy.
This storage really benefits from economy of scale, as the relative heat losses and the capital costs are reduced for large plants up to a certain size. From around 200.000 m3 the unit costs are almost constant. The technology is a combination of heat storage tank technology and a protected landfill. The pit itself is like a protected landfill with water proof welded plastic-liner. The diffuser (which can be seen at the picture) is the same as we have in the heat storage tank, and the natural stratification actually take care of the distribution from one diffuser to the whole area. The floating cover is a new and sencitive component and several technologies have been tested in full scale at the first plants.

## 5. Boiler plants
Back to user guide
5. Boiler plants
List of contents
5. Boiler plants
5.1 Natural gas boiler
5.2 Biomass boiler
5.2.1 Wood pellet boiler
5.2.2 Wood chips boiler
5.2.3 Straw boiler
5.3 Electric boiler
5.4 Waste boiler
5.5 Coal boiler
5.6 Oil boiler
5.7 New technology 1
5.8 New technology 2
5.9 Boiler technology output
Assumptions applied (selected in 3.1 LCOE results)
Discount rate |  |  |  |  | 5% | %
Calculation period |  |  |  |  | 1
Start year of calculation |  |  |  |  | 2022
Electricity price development |  |  |  |  | Green
Expected solar thermal production |  |  |  |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  |  |  |  | Sustainable development scenario
Country |  |  |  |  | EU
Currency abbreviation |  |  |  |  | EUR
Currency factor |  |  |  |  | 1
Equipment |  |  |  |  | 1
Installation |  |  |  |  | 1
Figure 5-1: LCOE for disitrct heating boilers
5.1 Natural gas boiler
Figure 5-3: Natural gas boiler
5.1.1 Technical- and economic assumptions
Table 5-1: Technical- and economic assumptions for a district heating natural gas boiler [1]
Technology |  |  |  |  | New condensing boiler |  | Existing condensing boiler |  | New non-condensing boiler |  | Existing non-condensing boiler
Energy/technical data
Heat generation capacity for one unit (MJ/s) |  |  |  |  | 5 |  | 5
Total efficiency, net (%), nominel load |  |  |  |  | 105 |  | 84 |  | 84 |  | 84
Total efficiency , net (%), annual average |  |  |  |  | 103 |  | 82.4 |  | 82.4 |  | 82.4
Electricity consumption for pumps etc. (% of heat gen) |  |  |  |  | 0.14 |  | 0.14 |  | 0.14 |  | 0.14
Forced outage (%) |  |  |  |  | 1 |  | 1 |  | 1 |  | 1
Planned outage (weeks per year) |  |  |  |  | 0.4 |  | 0.4 |  | 0.4 |  | 0.4
Technical lifetime (years) |  |  |  |  | 25 |  |  |  | 25
Construction time (years) |  |  |  |  | 0.5 |  |  |  | 0.5
Space requirement (1000m2 per MJ/s) |  |  |  |  | 0.005 |  |  |  | 0.005
Plant Dynamic Capabilities
Primary regulation (% per 30 seconds) |  |  |  |  | - |  | - |  | - |  | -
Secondary regulation (% per minute) |  |  |  |  | - |  | - |  | - |  | -
Minimum load (% of full load) |  |  |  |  | 15 |  | 15 |  | 15 |  | 15
Warm start-up time (hours) |  |  |  |  | 0.1 |  | 0.1 |  | 0.1 |  | 0.1
Cold start-up time (hours) |  |  |  |  | 0.4 |  | 0.4 |  | 0.4 |  | 0.4
Environment
SO2 (g per GJ fuel) |  |  |  |  | 0.3 |  | 0.3 |  | 0.3 |  | 0.3
NOX (g per GJ fuel) |  |  |  |  | 9 |  | 9 |  | 9 |  | 9
CH4 (g per GJ fuel) |  |  |  |  | 3 |  | 3 |  | 3 |  | 3
N2O (g per GJ fuel) |  |  |  |  | 1 |  | 1 |  | 1 |  | 1
Financial data
Nominal investment (M€ per MJ/s) |  |  |  |  | 0.06 |  |  |  | 0.06
- of which equipment |  |  |  |  | 0.04 |  |  |  | 0.04
- of which installation |  |  |  |  | 0.02 |  |  |  | 0.02
Fixed O&M (€/MJ/s/year) |  |  |  |  | 1950 |  | 2437.5 |  | 1950 |  | 2437.5
Variable O&M (€/MWh) |  |  |  |  | 1.1 |  | 1.375 |  | 1.1 |  | 1.375
- of which is electricity costs (€/MWh) |  |  |  |  | 0.1 |  | 0.125 |  | 0.1 |  | 0.125
- of which is other O&M costs (€/MWh) |  |  |  |  | 1 |  | 1.25 |  | 1 |  | 1.25
Financial data (EUR) |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | 0.06 |  | 0 |  | 0.06 |  | 0
- of which equipment |  |  |  |  | 0.04 |  | 0 |  | 0.04 |  | 0
- of which installation |  |  |  |  | 0.02 |  | 0 |  | 0.02 |  | 0
Fixed O&M |  |  | EUR/MW/year |  | 1950 |  | 2437.5 |  | 1950 |  | 2437.5
Variable O&M (€/MWh) |  |  | EUR/MWh |  | 1.1 |  | 1.375 |  | 1.1 |  | 1.375
- of which is electricity costs (€/MWh) |  |  |  |  | 0.1 |  | 0.125 |  | 0.1 |  | 0.125
- of which is other O&M costs (€/MWh) |  |  |  |  | 1 |  | 1.25 |  | 1 |  | 1.25
New condensing boiler |  |  | Unit |  | New condensing boiler | Existing condensing boiler | New non-condensing boiler | Existing non-condensing boiler
Heat capacity |  |  | MW-h |  | 1 | 2 | 3 | 4 | 5 | 10 | 15 | 20 | 25
Nominal investment |  |  | MEUR/MW-h |  | 0.18511 | 0.11395 | 0.085792 | 0.070144 | 0.06 | 0.036934 | 0.027808 | 0.022736 | 0.019448
- of which equipment |  |  | MEUR/MW-h |  | 0.12341 | 0.075966 | 0.057194 | 0.046762 | 0.04 | 0.024623 | 0.018539 | 0.015157 | 0.012965
- of which installation |  |  | MEUR/MW-h |  | 0.061703 | 0.037983 | 0.028597 | 0.023381 | 0.02 | 0.012311 | 0.0092693 | 0.0075786 | 0.0064826
Figure 5-3: Economy of scale for new natural gas boiler (investment)
5.2 Biomass boiler
5.2.1 Wood pellet boiler
Table 5-2: Technical- and economic assumptions for wood pellet boiler [1]
Technology |  |  |  |  | New boiler |  | Existing boiler
Energy/technical data
Heat generation capacity for one unit (MW) |  |  |  |  | 6 |  | 6
Total efficiency, net (%), name plate |  |  |  |  | 100.1 |  | 80.08
Total efficiency , net (%), annual average |  |  |  |  | 100.1 |  | 80.08
Additional heat potential with heat pumps (% of thermal input) |  |  |  |  | 1.7 |  | 1.36
Auxiliary electricity consumption (% of heat gen) |  |  |  |  | 2.1 |  | 1.68
Forced outage (%) |  |  |  |  | 3 |  | 3
Planned outage (weeks per year) |  |  |  |  | 3 |  | 3
Technical lifetime (years) |  |  |  |  | 25 |  | 20
Construction time (years) |  |  |  |  | 1 |  | ---
Space requirement (1000 m2/MWth heat output) |  |  |  |  | 0.2 |  | 0.2
Primary regulation (% per 30 seconds) |  |  |  |  | NA |  | NA
Secondary regulation (% per minute) |  |  |  |  | 10 |  | 10
Minimum load (% of full load) |  |  |  |  | 40 |  | 40
Warm start-up time (hours) |  |  |  |  | 0.25 |  | 0.25
Cold start-up time (hours) |  |  |  |  | 0.5 |  | 0.5
Environment
SO2 (degree of desulphuring, %) |  |  |  |  | 98.3 |  | 98.3
NOX (g per GJ fuel) |  |  |  |  | 54 |  | 54
CH4 (g per GJ fuel) |  |  |  |  | 0 |  | 0
N2O (g per GJ fuel) |  |  |  |  | 1 |  | 1
Particles (g per GJ fuel) |  |  |  |  | 0.3 |  | 0.3
Financial data
Nominal investment (M€/MWth - heat output) |  |  |  |  | 0.72 |  | ---
- of which equipment |  |  |  |  | 0.44 |  | ---
- of which installation |  |  |  |  | 0.28 |  | ---
Fixed O&M (€/MWth/year), heat output |  |  |  |  | 33000 |  | 41250
Variable O&M (€/MWh) heat output |  |  |  |  | 0.5 |  | 0.625
Financial data (EUR) |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | 0.72 |  | #VALUE!
- of which equipment |  |  |  |  | 0.44 |  | #VALUE!
- of which installation |  |  |  |  | 0.28 |  | #VALUE!
Fixed O&M |  |  | EUR/MW/year |  | 33000 |  | 41250
Variable O&M (€/MWh) |  |  | EUR/MWh |  | 0.5 |  | 0.625
Technology specific data
Flue gas condensation |  |  |  |  | Yes |  | Yes
Combustion air humidification |  |  |  |  | Yes |  | Yes
Nominal investment (M€/MW fuel input) |  |  |  |  | 0.72 |  | ---
- of which equipment |  |  |  |  | 0.44 |  | ---
- of which installation |  |  |  |  | 0.28 |  | ---
Fixed O&M (€/MW input/year) |  |  |  |  | 33100 |  | ---
Variable O&M (€/MWh input) |  |  |  |  | 1.9 |  | ---
- of which is electricity costs (€/MWh) |  |  |  |  | 1.4 |  | ---
- of which is other O&M costs (€/MWh) |  |  |  |  | 0.5 |  | ---
Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) |  |  |  |  | 0.004 |  | ---
5.2.2 Wood chips boiler
Table 5-3: Technical- and economic assumptions for a wood chips boiler [1]
Technology |  |  |  |  | New boiler |  | Existing boiler
Energy/technical data
Heat generation capacity for one unit (MW) |  |  |  |  | 6.9 |  | 6.9
Total efficiency, net (%), name plate |  |  |  |  | 114.9 |  | 91.92
Total efficiency , net (%), annual average |  |  |  |  | 114.9 |  | 91.92
Additional heat potential with heat pumps (% of thermal input) |  |  |  |  | 2 |  | 1.6
Auxiliary electricity consumption (% of heat gen) |  |  |  |  | 2.3 |  | 1.84
Forced outage (%) |  |  |  |  | 3 |  | 3
Planned outage (weeks per year) |  |  |  |  | 2 |  | 2
Technical lifetime (years) |  |  |  |  | 25 |  | 25
Construction time (years) |  |  |  |  | 1 |  | ---
Space requirement (1000 m2/MWth heat output) |  |  |  |  | 0.2 |  | 0.2
Primary regulation (% per 30 seconds) |  |  |  |  | NA |  | NA
Secondary regulation (% per minute) |  |  |  |  | 10 |  | 10
Minimum load (% of full load) |  |  |  |  | 20 |  | 20
Warm start-up time (hours) |  |  |  |  | 0.25 |  | 0.25
Cold start-up time (hours) |  |  |  |  | 0.5 |  | 0.5
Environment
SO2 (degree of desulphuring, %) |  |  |  |  | 98 |  | 98
NOX (g per GJ fuel) |  |  |  |  | 63 |  | 63
CH4 (g per GJ fuel) |  |  |  |  | 11 |  | 11
N2O (g per GJ fuel) |  |  |  |  | 3 |  | 3
Particles (g per GJ fuel) |  |  |  |  | 0.3 |  | 0.3
Financial data
Nominal investment (M€/MWth - heat output) |  |  |  |  | 0.69 |  | ---
- of which equipment |  |  |  |  | 0.4 |  | ---
- of which installation |  |  |  |  | 0.29 |  | ---
Fixed O&M (€/MWth/year), heat output |  |  |  |  | 32200 |  | 40250
Variable O&M (€/MWh) heat output |  |  |  |  | 1 |  | 1.25
Financial data (EUR) |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | 0.69 |  | #VALUE!
- of which equipment |  |  |  |  | 0.4 |  | #VALUE!
- of which installation |  |  |  |  | 0.29 |  | #VALUE!
Fixed O&M |  |  | EUR/MW/year |  | 32200 |  | 40250
Variable O&M (€/MWh) |  |  | EUR/MWh |  | 1 |  | 1.25
Technology specific data
Flue gas condensation |  |  |  |  | Yes |  | Yes
Combustion air humidification |  |  |  |  | Yes |  | Yes
Nominal investment (M€/MW fuel input) |  |  |  |  | 0.79 |  | ---
- of which equipment |  |  |  |  | 0.46 |  | ---
- of which installation |  |  |  |  | 0.33 |  | ---
Fixed O&M (€/MW input/year) |  |  |  |  | 37100 |  | ---
Variable O&M (€/MWh input) |  |  |  |  | 2.7 |  | ---
- of which is electricity costs (€/MWh) |  |  |  |  | 1.6 |  | ---
- of which is other O&M costs (€/MWh) |  |  |  |  | 1.1 |  | ---
Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) |  |  |  |  | 0.02 |  | ---
5.2.3 Straw boiler
Table 5-4: Technical- and economic assumptions for a straw boiler [1]
Technology |  |  |  |  | New boiler |  | Existing boiler
Energy/technical data
Heat generation capacity for one unit (MW) |  |  |  |  | 6.1 |  | 6.1
Total efficiency, net (%), name plate |  |  |  |  | 102.1 |  | 81.68
Total efficiency , net (%), annual average |  |  |  |  | 102.1 |  | 81.68
Additional heat potential with heat pumps (% of thermal input) |  |  |  |  | 1.7 |  | 1.36
Auxiliary electricity consumption (% of heat gen) |  |  |  |  | 2.1 |  | 1.68
Forced outage (%) |  |  |  |  | 4 |  | 4
Planned outage (weeks per year) |  |  |  |  | 4 |  | 4
Technical lifetime (years) |  |  |  |  | 25 |  | 25
Construction time (years) |  |  |  |  | 1 |  | ---
Space requirement (1000 m2/MWe) |  |  |  |  | 0.2 |  | 0.2
Primary regulation (% per 30 seconds) |  |  |  |  | NA |  | NA
Secondary regulation (% per minute) |  |  |  |  | 10 |  | 10
Minimum load (% of full load) |  |  |  |  | 50 |  | 50
Warm start-up time (hours) |  |  |  |  | 0.25 |  | 0.25
Cold start-up time (hours) |  |  |  |  | 0.5 |  | 0.5
Environment
SO2 (degree of desulphuring, %) |  |  |  |  | 96.4 |  | 96.4
NOX (g per GJ fuel) |  |  |  |  | 72 |  | 72
CH4 (g per GJ fuel) |  |  |  |  | 11 |  | 11
N2O (g per GJ fuel) |  |  |  |  | 3 |  | 3
Particles (g per GJ fuel) |  |  |  |  | 0.3 |  | 0.3
Financial data
Nominal investment (M€/MWth - heat output) |  |  |  |  | 0.89 |  | ---
- of which equipment |  |  |  |  | 0.43 |  | ---
- of which installation |  |  |  |  | 0.46 |  | ---
Fixed O&M (€/MWth/year), heat output |  |  |  |  | 51300 |  | 64125
Variable O&M (€/MWh) heat output |  |  |  |  | 0.6 |  | 0.75
Financial data (EUR) |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | 0.89 |  | #VALUE!
- of which equipment |  |  |  |  | 0.43 |  | #VALUE!
- of which installation |  |  |  |  | 0.46 |  | #VALUE!
Fixed O&M |  |  | EUR/MW/year |  | 51300 |  | 64125
Variable O&M (€/MWh) |  |  | EUR/MWh |  | 0.6 |  | 0.75
Technology specific data
Flue gas condensation |  |  |  |  | Yes |  | Yes
Combustion air humidification |  |  |  |  | Yes |  | Yes
Nominal investment (M€/MW fuel input) |  |  |  |  | 0.9 |  | ---
- of which equipment |  |  |  |  | 0.44 |  | ---
- of which installation |  |  |  |  | 0.46 |  | ---
Fixed O&M (€/MW input/year) |  |  |  |  | 52400 |  | ---
Variable O&M (€/MWh input) |  |  |  |  | 2.1 |  | ---
- of which is electricity costs (€/MWh) |  |  |  |  | 1.5 |  | ---
- of which is other O&M costs (€/MWh) |  |  |  |  | 0.6 |  | ---
Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) |  |  |  |  | 0.078 |  | ---
Wood chips boiler |  |  | Unit |  | Wood pellet boiler | Wood chips boiler | Straw boiler
Heat capacity |  |  | MW-h |  | 1 | 2 | 3 | 4 | 5 | 10 | 15 | 20 | 25
Nominal investment |  |  | MEUR/MW-h |  | 2.6671 | 1.6418 | 1.2361 | 1.0107 | 0.8645 | 0.53216 | 0.40066 | 0.32758 | 0.28021
- of which equipment |  |  | MEUR/MW-h |  | 1.5462 | 0.95177 | 0.71659 | 0.58588 | 0.50116 | 0.3085 | 0.23227 | 0.1899 | 0.16244
- of which installation |  |  | MEUR/MW-h |  | 1.121 | 0.69004 | 0.51953 | 0.42477 | 0.36334 | 0.22366 | 0.16839 | 0.13768 | 0.11777
5.3 Electric boiler
5.3.1 Technical- and economic assumptions
Table 5-5: Technical- and economic assumptions for an electric boiler [1]
Technology |  |  |  |  | Electric boiler
Energy/technical data
Heat generation capacity for one unit (MW) |  |  |  |  | 5
Total efficiency, net (%), name plate |  |  |  |  | 99
Total efficiency , net (%), annual average |  |  |  |  | 99
Electricity consumption for pumps etc. (% of heat gen) |  |  |  |  | 0.5
Forced outage (%) |  |  |  |  | 1
Planned outage (weeks per year) |  |  |  |  | 0.2
Technical lifetime (years) |  |  |  |  | 20
Construction time (years) |  |  |  |  | 0.5
Regulation ability
Primary regulation (% per 30 seconds) |  |  |  |  | 100
Secondary regulation (% per minute) |  |  |  |  | 100
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Financial data (in 2015€)
Nominal investment (M€ per MW), 400/690 V; 1-5 MW |  |  |  |  | 0.15
- of which equipment |  |  |  |  | 0.12
- of which installation |  |  |  |  | 0.03
Nominal investment (M€ per MW); 10/15 kV; >10 MW |  |  |  |  | 0.07
- of which equipment |  |  |  |  | 0.06
- of which installation |  |  |  |  | 0.01
Fixed O&M (€/MW/year) |  |  |  |  | 1070
Variable O&M (€/MWh) |  |  |  |  | 0.9
- of which is electricity costs (€/MWh) |  |  |  |  | 0.3
- of which is other O&M costs (€/MWh) |  |  |  |  | 0.5
Technology specific data
Startup costs (€/MW/startup) |  |  |  |  | 0
Financial data (EUR) |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | 0.15
- of which equipment |  |  |  |  | 0.12
- of which installation |  |  |  |  | 0.03
Nominal investment |  |  | MEUR/MW |  | 0.07
- of which equipment |  |  |  |  | 0.06
- of which installation |  |  |  |  | 0.01
Fixed O&M |  |  | EUR/MW/year |  | 1070
Variable O&M (€/MWh) |  |  | EUR/MWh |  | 0.9
- of which is electricity costs (€/MWh) |  |  |  |  | 0.3
- of which is other O&M costs (€/MWh) |  |  |  |  | 0.5
Electric boiler |  |  | Unit |  | Wood pellet boiler | Wood chips boiler | Straw boiler
Heat capacity |  |  | MW-h |  | 1 | 2 | 3 | 4 | 5 | 10 | 15 | 20 | 25
Nominal investment |  |  | MEUR/MW-h |  | 0.46278 | 0.28487 | 0.21448 | 0.17536 | 0.15 | 0.07 | 0.052703 | 0.04309 | 0.036859
- of which equipment |  |  | MEUR/MW-h |  | 0.37022 | 0.2279 | 0.17158 | 0.14029 | 0.12 | 0.06 | 0.045174 | 0.036934 | 0.031593
- of which installation |  |  | MEUR/MW-h |  | 0.092555 | 0.056974 | 0.042896 | 0.035072 | 0.03 | 0.01 | 0.007529 | 0.0061557 | 0.0052655
5.4 Waste boiler
5.4.1 Technical- and economic assumptions
Table 5-6: Technical- and economic assumptions for a waste boiler [1]
Technology |  |  |  |  | Waste boiler
Energy/technical data
Heat generation capacity for one unit (MW) |  |  |  |  | 36.6
Incineration capacity (Fuel input) (tonnes/h) |  |  |  |  | 11.9
Total heat efficiency, net (%), ref. LHV, name plate |  |  |  |  | 104.7
Total heat efficiency , net (%), ref. LHV, annual average |  |  |  |  | 104.7
Additional heat potential with heat pumps (% of thermal input) |  |  |  |  | 4.1
Auxiliary electricity consumption (% of heat gen) |  |  |  |  | 2.6
Forced outage (%) |  |  |  |  | 1
Planned outage (weeks per year) |  |  |  |  | 2.9
Technical lifetime (years) |  |  |  |  | 25
Construction time (years) |  |  |  |  | 2
Space requirement (1000 m2/MWth heat output) |  |  |  |  | 0.55
Regulation ability
Primary regulation (% per 30 seconds) |  |  |  |  | NA
Secondary regulation (% per minute) |  |  |  |  | 1
Minimum load (% of full load) |  |  |  |  | 70
Warm start-up time (hours) |  |  |  |  | 8
Cold start-up time (hours) |  |  |  |  | 12
Environment
SO2 (degree of desulphuring, %) |  |  |  |  | 99.8
NOX (g per GJ fuel) |  |  |  |  | 67
CH4 (g per GJ fuel) |  |  |  |  | 0.1
N2O (g per GJ fuel) |  |  |  |  | 1
Particles (g per GJ fuel) |  |  |  |  | 0.3
Financial data
Nominal investment (M€/MWth - heat output) |  |  |  |  | 1.76
- of which equipment [%] |  |  |  |  | 1.01
- of which installation [%] |  |  |  |  | 0.75
Fixed O&M (€/MWth/year), heat output |  |  |  |  | 78600
Variable O&M (€/MWh) heat output |  |  |  |  | 5.5
Technology specific data
Flue gas condensation |  |  |  |  | Yes
Combustion air humidification |  |  |  |  | No
Nominal investment (M€/MW fuel input) |  |  |  |  | 1.84
- of which equipment |  |  |  |  | 1.05
- of which installation |  |  |  |  | 0.78
Fixed O&M (€/MW input/year) |  |  |  |  | 82300
Variable O&M (€/MWh input) |  |  |  |  | 7.6
- of which is electricity costs (€/MWh) |  |  |  |  | 1.8
- of which is other O&M costs (€/MWh) |  |  |  |  | 5.8
Nominal investment (€/(tonne/year)) |  |  |  |  | 676
Fixed O&M (€/tonne) |  |  |  |  | 30
Variable O&M (€/tonne) |  |  |  |  | 17
Financial data (EUR) |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | 1.76
- of which equipment |  |  |  |  | 1.01
- of which installation |  |  |  |  | 0.75
Fixed O&M |  |  | EUR/MW/year |  | 78600
Variable O&M (€/MWh) |  |  | EUR/MWh |  | 5.5
Waste boiler |  |  | Unit |  | Wood pellet boiler | Wood chips boiler | Straw boiler
Heat capacity |  |  | MW-h |  | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
Nominal investment |  |  | MEUR/MW-h |  | 2.6868 | 2.2982 | 2.0229 | 1.8159 | 1.6539 | 1.523 | 1.4147 | 1.3234 | 1.2452
- of which equipment |  |  | MEUR/MW-h |  | 1.5418 | 1.3189 | 1.1608 | 1.0421 | 0.94911 | 0.874 | 0.81186 | 0.75946 | 0.71458
- of which installation |  |  | MEUR/MW-h |  | 1.1449 | 0.97935 | 0.86201 | 0.77384 | 0.70478 | 0.64901 | 0.60286 | 0.56395 | 0.53063
5.5 Coal boiler
5.5.1 Technical and economic assumptions
Table 5-7: Technical- and economic assumptions for a coal boiler [1]
Technology |  |  |  |  | Wood pellet boiler 20: Coal boiler
Energy/technical data
Heat generation capacity for one unit (MJ/s) |  |  |  |  | Wood pellet boiler 20: 5
Total efficiency, net (%), nominel load |  |  |  |  | Wood pellet boiler 20: 90
Total efficiency , net (%), annual average |  |  |  |  | Wood pellet boiler 20: 90
Electricity consumption for pumps etc. (% of heat gen) |  |  |  |  | Wood pellet boiler 20: 0.14
Forced outage (%) | bar: Wood pellet boiler 20
Planned outage (weeks per year) |  |  |  |  | Wood pellet boiler 20: 0.4
Technical lifetime (years) |  |  |  |  | Wood pellet boiler 20: 20
Construction time (years) |  |  |  |  | Wood pellet boiler 20: 0.5
Space requirement (1000m2 per MJ/s) |  |  |  |  | Wood pellet boiler 20: 0.005
Plant Dynamic Capabilities | bar: Wood pellet boiler 20
Primary regulation (% per 30 seconds) | bar: Wood pellet boiler 20
Secondary regulation (% per minute) | bar: Wood pellet boiler 20
Minimum load (% of full load) |  |  |  |  | Wood pellet boiler 20: 15
Warm start-up time (hours) |  |  |  |  | Wood pellet boiler 20: 0.1
Cold start-up time (hours) |  |  |  |  | Wood pellet boiler 20: 0.4
Environment
SO2 (g per GJ fuel) |  |  |  |  | Wood pellet boiler 20: 5
NOX (g per GJ fuel) |  |  |  |  | Wood pellet boiler 20: 35
CH4 (g per GJ fuel) |  |  |  |  | Wood pellet boiler 20: 1.5
N2O (g per GJ fuel) |  |  |  |  | Wood pellet boiler 20: 0.8
Financial data
Nominal investment (M€ per MJ/s) |  |  |  |  | Wood pellet boiler 20: 0.06
- of which equipment |  |  |  |  | Wood pellet boiler 20: 0.04
- of which installation |  |  |  |  | Wood pellet boiler 20: 0.02
Fixed O&M (€/MJ/s/year) |  |  |  |  | Wood pellet boiler 20: 2140
Variable O&M (€/MWh) |  |  |  |  | Wood pellet boiler 20: 1.6
- of which is electricity costs (€/MWh) | bar: Wood pellet boiler 20
- of which is other O&M costs (€/MWh) | bar: Wood pellet boiler 20
Financial data (EUR) |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | Wood pellet boiler 20: 0.06
- of which equipment |  |  |  |  | Wood pellet boiler 20: 0.04
- of which installation |  |  |  |  | Wood pellet boiler 20: 0.02
Fixed O&M |  |  | EUR/MW/year |  | Wood pellet boiler 20: 2140
Variable O&M (€/MWh) |  |  | EUR/MWh |  | Wood pellet boiler 20: 1.6
- of which is electricity costs (€/MWh) |  |  |  |  | Wood pellet boiler 20: #VALUE!
- of which is other O&M costs (€/MWh) |  |  |  |  | Wood pellet boiler 20: #VALUE!
Coal boiler |  |  | Unit
Heat capacity |  |  | MW-h |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Nominal investment |  |  | MEUR/MW-h |  | 0.11395 | 0.085792 | 0.070144 | 0.06 | 0.052811 | 0.047409 | 0.043178 | 0.039761 | 0.036934
- of which equipment |  |  | MEUR/MW-h |  | 0.075966 | 0.057194 | 0.046762 | 0.04 | 0.035207 | 0.031606 | 0.028786 | 0.026508 | 0.024623
- of which installation |  |  | MEUR/MW-h |  | 0.037983 | 0.028597 | 0.023381 | 0.02 | 0.017604 | 0.015803 | 0.014393 | 0.013254 | 0.012311
5.6 Oil boiler
5.6.1 Technical and economic assumptions
Table 5-8: Technical- and economic assumptions for a oil boiler [1]
Technology |  |  |  |  | 2: Oil boiler
Energy/technical data
Heat generation capacity for one unit (MJ/s) |  |  |  |  | 2: 5
Total efficiency, net (%), nominel load |  |  |  |  | 2: 90
Total efficiency , net (%), annual average |  |  |  |  | 2: 90
Electricity consumption for pumps etc. (% of heat gen) |  |  |  |  | 2: 0.14
Forced outage (%) | bar: 2
Planned outage (weeks per year) |  |  |  |  | 2: 0.4
Technical lifetime (years) |  |  |  |  | 2: 20
Construction time (years) |  |  |  |  | 2: 0.5
Space requirement (1000m2 per MJ/s) |  |  |  |  | 2: 0.005
Plant Dynamic Capabilities | bar: 2
Primary regulation (% per 30 seconds) | bar: 2
Secondary regulation (% per minute) | bar: 2
Minimum load (% of full load) |  |  |  |  | 2: 15
Warm start-up time (hours) |  |  |  |  | 2: 0.1
Cold start-up time (hours) |  |  |  |  | 2: 0.4
Environment
SO2 (g per GJ fuel) |  |  |  |  | 2: 1.8
NOX (g per GJ fuel) |  |  |  |  | 2: 90
CH4 (g per GJ fuel) |  |  |  |  | 2: 0
N2O (g per GJ fuel) |  |  |  |  | 2: 0
Financial data
Nominal investment (M€ per MJ/s) |  |  |  |  | 2: 0.06
- of which equipment |  |  |  |  | 2: 0.04
- of which installation |  |  |  |  | 2: 0.02
Fixed O&M (€/MJ/s/year) |  |  |  |  | 2: 1950
Variable O&M (€/MWh) |  |  |  |  | 2: 1.1
- of which is electricity costs (€/MWh) | bar: 2
- of which is other O&M costs (€/MWh) | bar: 2
Financial data (EUR) |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | 2: 0.06
- of which equipment |  |  |  |  | 2: 0.04
- of which installation |  |  |  |  | 2: 0.02
Fixed O&M |  |  | EUR/MW/year |  | 2: 1950
Variable O&M (€/MWh) |  |  | EUR/MWh |  | 2: 1.1
- of which is electricity costs (€/MWh) |  |  |  |  | 2: #VALUE!
- of which is other O&M costs (€/MWh) |  |  |  |  | 2: #VALUE!
Oil boiler |  |  | Unit
Heat capacity |  |  | MW-h |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Nominal investment |  |  | MEUR/MW-h |  | 0.11395 | 0.085792 | 0.070144 | 0.06 | 0.052811 | 0.047409 | 0.043178 | 0.039761 | 0.036934
- of which equipment |  |  | MEUR/MW-h |  | 0.075966 | 0.057194 | 0.046762 | 0.04 | 0.035207 | 0.031606 | 0.028786 | 0.026508 | 0.024623
- of which installation |  |  | MEUR/MW-h |  | 0.037983 | 0.028597 | 0.023381 | 0.02 | 0.017604 | 0.015803 | 0.014393 | 0.013254 | 0.012311
5.7 New technology 1
5.7.1 Technical and economic assumptions
5.8 New technology 2
5.8.1 Technical and economic assumptions
5.9 Boiler technology output
Technology | Reference | Electric capacity | Heat capacity | Solar thermal size | Storage size | Fuel | Voltage connection level | Full load hours |  |  | Investment (el) (eqiupment) | Investment (el) (installation) | Investment (heat) (equipment)
|  | MW-e | MW-h | m2 panel | m3 storage |  |  | Black | Blue | Green | mil. EUR/MW-el | mil. EUR/MW-el | mil. EUR/MW-heat
Boiler - wood chips | [1] | --- | 7 | --- | --- | Wood chips | --- | 5000 | 5000 | 5000 | --- | --- | 0.4
Boiler - wood pellets | [1] | --- | 6 | --- | --- | Wood pellets | --- | 5000 | 5000 | 5000 | --- | --- | 0.44
Boiler - straw | [1] | --- | 6 | --- | --- | Straw | --- | 5000 | 5000 | 5000 | --- | --- | 0.43
Boiler - natural gas | [1] | --- | 5.3 | --- | --- | Natural gas | --- | 500 | 500 | 500 | --- | --- | 0.04
Boiler - oil | [1] | --- | 5 | --- | --- | Oil | --- | 500 | 500 | 500 | --- | --- | 0.04
Electric boiler | [1] | --- | 5 | --- | --- | Electricity | High voltage level | 200 | 200 | 200 | --- | --- | 0.12
Boiler - coal | [1] | --- | 5 | --- | --- | Coal | --- | 500 | 500 | 500 | --- | --- | 0.04
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Technology | Investment (heat) (installation) | Investment (solar) | Investment (storage) | Fixed O&M (el) | Fixed O&M (heat) | Fixed O&M (solar) | Fixed O&M (storage) | Var. O&M (el) | Var. O&M (heat) | Lifetime | CV | CB | Electric efficiency CHP
| mil. EUR/MW-heat | EUR/m2 panel | EUR/m3 storage | EUR/MW-el/year | EUR/MW-heat/year | EUR/m2 panel/year | EUR/m3 storage/year | EUR/MWh-el | EUR/MWh-heat | year |  |  | MW-el/MW-fuel
Boiler - wood chips | 0.29 | --- | --- | --- | 32200 | --- | --- | --- | 1 | 25 | --- | --- | ---
Boiler - wood pellets | 0.28 | --- | --- | --- | 33000 | --- | --- | --- | 0.5 | 25 | --- | --- | ---
Boiler - straw | 0.46 | --- | --- | --- | 51300 | --- | --- | --- | 0.6 | 25 | --- | --- | ---
Boiler - natural gas | 0.02 | --- | --- | --- | 1950 | --- | --- | --- | 1.1 | 25 | --- | --- | ---
Boiler - oil | 0.02 | --- | --- | --- | 1950 | --- | --- | --- | 1.1 | 25 | --- | --- | ---
Electric boiler | 0.03 | --- | --- | --- | 1070 | --- | --- | --- | 0.9 | 20 | --- | --- | ---
Boiler - coal | 0.02 | --- | --- | --- | 2140 | --- | --- | --- | 1.6 | 20 | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Technology | Heat efficiency CHP | Electric efficiency condensing | Heat efficiency | CO2 capture rate (amount of emission) | SO2 (degree of desulphuring) | Emission factor SO2 | Emission factor NOX | Emission factor CH4 | Emission factor N2O | Emission factor PM2.5
| MW-heat/MW-fuel | MW-el/MW-fuel | MW-heat/MW-fuel | % | % | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f
Boiler - wood chips | --- | --- | 1.15 | 0% | 98% | --- | 226.8 | 39.6 | 10.8 | 1.08
Boiler - wood pellets | --- | --- | 1 | 0% | 98.3% | --- | 194.4 | 0 | 3.6 | 1.08
Boiler - straw | --- | --- | 1.02 | 0% | 96.4% | --- | 259.2 | 39.6 | 10.8 | 1.08
Boiler - natural gas | --- | --- | 1.03 | 0% | --- | 1.08 | 32.4 | 10.8 | 3.6 | 0
Boiler - oil | --- | --- | 1.03 | 0% | --- | 1.8 | 90 | 0 | 0 | 0.72
Electric boiler | --- | --- | 1 | 0% | --- | --- | --- | --- | --- | ---
Boiler - coal | --- | --- | 0.9 | 0% | --- | 18 | 126 | 5.4 | 2.88 | 1.8
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Boiler plants are the simplest technology, which can be the baseline for all other alternatives in a low carbon and sustainable energy system.
The boiler plants can serve several purposes:
- Back-up and peak capacity for heating, e.g. from gas and oil boilers, which can increase the resilience
- Base load capacity for heating from biomass boilers, which use local ressources
- Electric boilers, which use low cost surplus electricity from fluctuating resources and offer services to the power grid, e.g. frequency stabilization
- Process energy in the form of superheated temperature, e.g. 160 oC or steam.
It is therefore important to look at the costs for capacity as well as the variable cost of generating energy per MWh. The boilers plants in this database are for supplying low temperature heating, with supply temperatures below 95-110 oC.
The fuel is burnt in the furnace section. Heat from the flame is transmitted via radiation (and convection) to the inner walls of the boiler and from there to the water to be heated. After the combustion part, the hot flue gasses are led through the convection parts of the boiler and heat is transmitted to the water to be heated.
Shell and flue gas tube type boilers are the most commonly used type of boilers at Danish district heating plants.
The boiler may be fitted with an external heat exchanger (economizer) to utilise any remaining heat (including latent heat) in flue gasses.
Boilers for district heating have been used for decades. Today, many gas fired district heating boilers are used for peak-load or back-up capacity. During periods with low electricity prices, gas fired district heating boilers have accounted for a relatively large part of the district heating production as it has been less feasible to operate the engines at CHP plants.
Typical flue gas tube boiler for the power range 1- 20 MW. Combustion takes place in the firetube (3). Flue gasses then passes inside a number of flue gas tubes ((5) & (7)) transmitting further heat to the boiler water around these. The water connections (forward/return) are on the top ((2) & (1)).
Advantages
Gas fired boilers are a proven and well-known technology. They can be supplied over a wide range of output capacities. Load response is good.
The boilers may also be used for heat extraction at medium- or high-temperature from waste process air.
Heat pumps, either electrical or absorption, may be added to utilize flue gas heat, thereby increasing the efficiency of the heat pump.
Disadvantages
When gas boilers are being fuelled with diesel or biogas, possibly in combination with natural gas, additional sulphur cleaning may be needed.
A biomass boiler is a boiler fired by wood-chips from forestry and/or from wood industry, wood pellets or straw.
If the moisture content of the fuel is above 30-35%, as with forest wood-chips, flue gas condensation should be employed. Thereby the thermal efficiency usually exceeds 100 % (based on lower heating value). The efficiency is primarily determined by the condensation temperature, which is little above the return temperature from the district heating network. In well-designed systems, this return temperature is below 40 oC, yielding efficiencies above 105 %.
For plants firing wood-chips with 45 – 55 % moisture content, the thermal efficiency exceeds 110 %. Some plants are equipped with cooling devices for full flue gas condensation and thermal efficiencies of more than 120 % are reached. Flue gas condensation should not be applied to plants below 1 - 2 MJ/s due to O&M costs. Such plants should only use fuels drier than 30 % moisture content.
Straw fired boilers are normally equipped with a bag filter for flue gas cleaning. Electro filters do not work with straw firing as they do with wood firing. Flue gas condensation is now available also for straw firing but must be combined with a bag filter to hold back calcium chlorine particles from the scrubber. The flue gas condensation raises the efficiency with 5-10 % and reduces SO2 emission to a minimum, when the pH value is kept above 6.5 – 7.0. Whether flue condensation is feasible is much dependent on taxes, e.g. on sulphur.
Wood chips are wood pieces of 5-50 mm in the fibre direction, longer twigs (slivers), and a fine fraction (fines). The quality description is based on three types of wood chips: Fine, coarse, and extra coarse. The names refer to the size distribution only, not to the quality. The wood-chips are often traded in two size qualities, coarse and fine. Other possible fuels are chipped energy crops (e.g. willow and poplar) and chipped park and garden waste.
Wood pellets are made from sawdust, wood shavings and other residues from sawmils and other wood manufacturers. Pellets are produced in several types and grades as fuels for electric power plants and district heating (low grade), and homes (high grade). Pellets are extremely dense and can be produced with a low humidity content (below 5 % for high grade products) that allows easy handling (incl. long-term storage) and to be burned with a high combustion efficiencies.
Straw is a waste product from the farming industry. Some of the straw is utilized in the farming industry, but in general there is a way to produce sustainable energy from the straw. In the long run it may be profitable to use straw to generate bio diesel or substitute oil for generating usefull materials instead of plastic, but until this technology has been further developed it makes sence that the energy market support a market for industrial production and handling of straw.
The simple industrialized collection for farming is the round bales, but the big bales (500 kg each) are suitable for energy plants. The plant can operate and feed in bales autimatically without staff at the plant. It also makes a good business for the local community to generate fuels locally, which was appreciated by the local politicians at the innagutation of this district heating boiler plant. Straw is however a difficult fuel. Therefore it is only acceptable for environmental reasons to use it in or near urban areas in large boiler plants, typically larger than 5 MW.
Electric boilers are devices in the MW size range using electricity for the production of hot water or steam for industrial or district heating purposes. They are usually installed as peak load units in the same way as an oil or gas boilers.
The conversion from electrical energy to thermal energy takes place at almost 100 % efficiency. However, from an exergetical point of view, this technology should be justified by its systemic advantages. Electric water heaters can be a part of the energy system facilitating utilization of wind energy and enabling efficient utilization of various heat energy sources.
Thus, the application of electric boilers in district heating systems is primarily driven by the demand for ancillary services rather than the demand for heat. Although, examples of electric boilers, that operate on the spot market can be found.
Generally, two types of electric boilers are available:
- Heating elements using electrical resistance (same principle as a hot water heater in a normal household). Typically, electrical resistance is used in smaller applications up to 1-2 MW. These electric boilers are connected at low voltage (e.g. 400 or 690 V, depending on the voltage level at the on-site distribution board).
- Heating elements using electrode boilers. Electrode systems are used for larger applications. Electrode boilers (larger than a few MW) are directly connected to the medium to high voltage grid at 10-15 kV (depending on the voltage in the locally available distribution grid).
WtE plants incinerate waste and produce energy. HOP’s produce only heat, while CHP’s also produce electricity.
Contrary to other fuels used for energy generation, waste has a negative price and is received at a gate fee. The primary objective of a waste-to-energy plant is the treatment of waste. Produced energy may be considered a useful by-product although with increasing importance for the future energy system with extensive use of district-heating and high power production from wind.
The total energy production from a WtE boiler can be varied by varying the fuel feed, although WtE facilities run at full load most of the time if the district-heating demand allows together with additional cooling opportunities. Operation of WtE CHP-unit as power-only may not be financially attractive, and often CHP facilities are constructed so that operation at power-only is not physically possible, as the necessary cooling facilities are not in place. The heat production can be changed also by starting or stopping the flue gas condensation.
Yet, for smaller scale plants a HOP may be a better solution than a CHP plant due to economic reasons.
In some parts of the world coal boilers are still present and used for heating of homes.
Oil boilers can be used for peak load heat production.

## 6. CHP and cond. power plants
Back to user guide
6. CHP and condensing power plants
List of contents
6. CHP and condensing power plants
6.1 Gas engine
6.2 Gas turbine combined cycle
6.3 Gas turbine simple cycle
6.4 Biomass CHP
6.4.1 Wood chips CHP
6.4.2 Wood pellets CHP
6.4.3 Straw CHP
6.5 Waste CHP
6.6 New technology 1
6.7 New technology 2
6.8 CHP technology output
Assumptions applied (selected in 3.1 LCOE results)
Discount rate |  |  |  |  | 5% | %
Calculation period |  |  |  |  | 1
Start year of calculation |  |  |  |  | 2022
Electricity price development |  |  |  |  | Green
Expected solar thermal production |  |  |  |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  |  |  |  | Sustainable development scenario
Country |  |  |  |  | EU
Currency abbreviation |  |  |  |  | EUR
Currency factor |  |  |  |  | 1
Equipment |  |  |  |  | 1
Installation |  |  |  |  | 1
6.1 Gas engine
6.1.1 Technical- and economic assumptions
Table 6-1: Technical- and economic assumptions for a spark ignition engine [1][13]
Technology |  |  |  |  | Spark ignition engine (natural gas) |  | Spark ignition engine (biogas) |  | Micro gas turbine
2020
Energy/technical data
Generating capacity for one unit (MW) |  |  |  |  | 5 |  | 5 |  | 0.1
Electricity efficiency (condensation mode for extraction plants), net (%) |  |  |  |  | 47 |  | 43 |  | 27
Electricity efficiency (condensation mode for extraction plants), net (%), annual average |  |  |  |  | 45 |  | 41 |  | 27
Cb coefficient (50oC/100oC) |  |  |  |  | 0.95 |  | 0.86 |  | 0.65854
Cv coefficient (50oC/100oC) |  |  |  |  | - |  | - |  | -
Forced outage (%) |  |  |  |  | 3 |  | 3 |  | 5
Planned outage (weeks per year) |  |  |  |  | 0.8 |  | 1 |  | 2
Technical lifetime (years) |  |  |  |  | 25 |  | 25 |  | 15
Construction time (years) |  |  |  |  | 1 |  | 1 |  | 0.5
Space requirement (1000m2/MW) |  |  |  |  | 0.04 |  | 0.04 |  | 0.04
Plant Dynamic Capabilities
Primary regulation (% per 30 seconds) |  |  |  |  | 30 |  | 30 |  | 30
Secondary regulation (% per minute) |  |  |  |  | 30 |  | 30 |  | 30
Minimum load (% of full load) |  |  |  |  | 50 |  | 50 |  | 50
Warm start-up time (hours) |  |  |  |  | 0.05 |  | 0.05 |  | 0.05
Cold start-up time (hours) |  |  |  |  | 0.3 |  | 0.3 |  | 0.3
Environment
SO2 (degree of desulphuring, %) |  |  |  |  | 0 |  | 0 |  | 0
NOX (g per GJ fuel) |  |  |  |  | 60 |  | 100 |  | 100
CH4 (g per GJ fuel) |  |  |  |  | 315 |  | 300 |  | 300
N2O (g per GJ fuel) |  |  |  |  | 0.6 |  | 1 |  | 1
Financial data (in 2015€)
Nominal investment (M€/MW) |  |  |  |  | 0.95 |  | 0.95 |  | 2.6786
- of which equipment |  |  |  |  | 0.57 |  | 0.57 |  | 1.6071
- of which installation |  |  |  |  | 0.38 |  | 0.38 |  | 1.0714
Fixed O&M (€/MW/year) |  |  |  |  | 9750 |  | 9750 |  | -
Variable O&M (€/MWh) |  |  |  |  | 5.4 |  | 7.5 |  | 10.7143
Financial data (EUR) |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | 0.95 |  | 0.95 |  | 2.6786
- of which equipment |  |  |  |  | 0.57 |  | 0.57 |  | 1.6071
- of which installation |  |  |  |  | 0.38 |  | 0.38 |  | 1.0714
Fixed O&M |  |  | EUR/MW/year |  | 9750 |  | 9750 |  | #VALUE!
Variable O&M (€/MWh) |  |  | EUR/MWh |  | 5.4 |  | 7.5 |  | 10.7143
Spark ignition engine (natural gas) |  |  | Unit |  | Spark ignition engine (natural gas) | Spark ignition engine (biogas) | ---
Electric capacity |  |  | MW-h |  | 1 | 2 | 3 | 4 | 5 | 10 | 15 | 20 | 25
Nominal investment |  |  | MEUR/MW-e |  | 2.9309 | 1.8042 | 1.3584 | 1.1106 | 0.95 | 0.58479 | 0.44029 | 0.35998 | 0.30792
- of which equipment |  |  | MEUR/MW-e |  | 1.7585 | 1.0825 | 0.81502 | 0.66636 | 0.57 | 0.35088 | 0.26417 | 0.21599 | 0.18475
- of which installation |  |  | MEUR/MW-e |  | 1.1724 | 0.72167 | 0.54335 | 0.44424 | 0.38 | 0.23392 | 0.17612 | 0.14399 | 0.12317
Table 6-2: Microturbine Performance Characteristics [13]
Description |  | System
|  | 1 | 2 | 3 | 4 | 5
Rated Power (kW) |  | 65 | 200 | 250 | 333 | 1000
Parasitic Load for Gas Compressor (kW) |  | 4 | 10 | 8 | 10 | 50
Net Electric Power (kW) |  | 61 | 190 | 242 | 323 | 950
Fuel Input (MMBtu/hr, HHV)3 |  | 0.84 | 2.29 | 3.16 | 3.85 | 11.43
Useful Thermal (MMBtu/hr) 4 |  | 0.39 | 0.87 | 1.2 | 1.6 | 4.18
Power to Heat Ratio5 |  | 0.53 | 0.75 | 0.69 | 0.69 | 0.77
Electric Efficiency (%, HHV) |  | 24.7% | 28.4% | 26.1% | 28.7% | 28.3%
Thermal Efficiency (%, HHV) |  | 46.9% | 38% | 38% | 41.6% | 36.6%
Overall Efficiency (%, HHV) |  | 71.6% | 66.3% | 64% | 70.2% | 64.9%
Note: Performance characteristics are average values and are not intended to represent a specific product. Performance Characteristics Table 2 summarizes technical performance characteristics for mi- croturbine CHP systems ranging in size from 65 to 1,000 kW. The values in the table are based on systems con- nected to low pressure (< 5 psig) natural gas. Microturbines typically require an inlet fuel
Table 6-3: Microturbine Capital and O&M Costs [13]
Description |  | System
|  | 1 | 2 | 3 | 4 | 5
Net Electric Power (kW) |  | 61 | 190 | 242 | 323 | 950
Complete Microturbine Package7 |  | 2120 | 2120 | 1830 | 1750 | 1710
Construction and Installation |  | 1100 | 1030 | 870 | 800 | 790
Installed Cost ($/kW) |  | 3220 | 3150 | 2700 | 2560 | 2500
Note: Costs are average values and are not intended to represent a specific product. available microturbines offer basic interconnection and paralleling
Table 6-4: Reciprocating Engine Performance Characteristics [13]
Description |  | System
|  | 1 | 2 | 3 | 4 | 5
Net Electric Power (kW)3 |  | 100 | 633 | 1141 | 3325 | 9341
Fuel Input (MMBtu/hr, HHV)4 |  | 1.15 | 6.26 | 10.37 | 27.73 | 76.06
Useful Thermal (MMBtu/hr) |  | 0.61 | 2.84 | 4.46 | 10.69 | 26.6
Power to Heat Ratio5 |  | 0.56 | 0.76 | 0.87 | 1.06 | 1.2
Electric Efficiency (%, HHV) |  | 29.6% | 34.5% | 37.6% | 40.9% | 41.9%
Thermal Efficiency (%, HHV) |  | 53.2% | 45.3% | 43% | 38.6% | 35%
Overall Efficiency (%, HHV) |  | 82.8% | 79.8% | 80.6% | 79.5% | 76.9%
Note: Performance characteristics are average values and are not intended to represent a specific product.
Table 6-5: Reciprocating Engine Capital and O&M Costs [13]
Description |  | System
|  | 1 | 2 | 3 | 4 | 5
Net Electric Power (kW) |  | 100 | 633 | 1141 | 3325 | 9341
Engine Type |  | Rich-burn | Lean-burn | Lean-burn | Lean-burn | Lean-burn
Engine and Generator ($/kW, including heat recovery and emission control) |  | 1650 | 1650 | 1380 | 1080 | 900
Construction and Installation |  | 1250 | 1190 | 990 | 720 | 530
Total Installed Cost |  | 2900 | 2840 | 2370 | 1800 | 1430
Total O&M Cost (¢/kWh) |  | 2.4 | 2.1 | 1.9 | 1.6 | 0.9
Note: Costs are average values and are not intended to represent a specific product.
6.2 Gas turbine combined cycle
6.2.1 Technical- and economic assumptions
Table 6-7: Technical- and economic assumptions for a gas turbine (combined cycle, extraction plant) [1]
Technology |  |  |  |  | Gas turbine (combined cycle, extraction plant) |  | Gas turbine (combined cycle, back-pressure)
[5 empty] | 2020 |  | 2020
Energy/technical data
Generating capacity for one unit (MW) |  |  |  |  | 300 |  | 300
Electricity efficiency (condensation mode for extraction plants), net (%), |  |  |  |  | 59 |  | 51
Electricity efficiency (condensation mode for extraction plants), net (%), annual average |  |  |  |  | 56 |  | 48
Cb coefficient (50oC/100oC) |  |  |  |  | 1.8 |  | 1.3
Cv coefficient (50oC/100oC) |  |  |  |  | 0.15 |  | -
Forced outage (%) |  |  |  |  | 3 |  | 3
Planned outage (weeks per year) |  |  |  |  | 2.3 |  | 2.3
Technical lifetime (years) |  |  |  |  | 25 |  | 25
Construction time (years) |  |  |  |  | 2.5 |  | 2
Space requirement (1000m2/MW) |  |  |  |  | 0.02 |  | 0.025
Plant Dynamic Capabilities
Primary regulation (% per 30 seconds) |  |  |  |  | - |  | -
Secondary regulation (% per minute) |  |  |  |  | 15 |  | 15
Minimum load (% of full load) |  |  |  |  | 40 |  | 40
Warm start-up time (hours) |  |  |  |  | 1 |  | 1
Cold start-up time (hours) |  |  |  |  | 2.5 |  | 2.5
Environment
SO2 (degree of desulphuring, %) |  |  |  |  | 0 |  | 0
NOX (g per GJ fuel) |  |  |  |  | 15 |  | 15
CH4 (g per GJ fuel) |  |  |  |  | 1.5 |  | 1.5
N2O (g per GJ fuel) |  |  |  |  | 1 |  | 1
Financial data (in 2015€)
Nominal investment (M€/MW) |  |  |  |  | 0.88 |  | 1.3
- of which equipment |  |  |  |  | 0.68 |  | 1
- of which installation |  |  |  |  | 0.2 |  | 0.3
Fixed O&M (€/MW/year) |  |  |  |  | 29300 |  | 29300
Variable O&M (€/MWh) |  |  |  |  | 4.4 |  | 4.4
Financial data (EUR) |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | 0.88 |  | 1.3
- of which equipment |  |  |  |  | 0.68 |  | 1
- of which installation |  |  |  |  | 0.2 |  | 0.3
Fixed O&M |  |  | EUR/MW/year |  | 29300 |  | 29300
Variable O&M (€/MWh) |  |  | EUR/MWh |  | 4.4 |  | 4.4
Gas turbine (combined cycle, extraction plant) |  |  | Unit |  | Gas turbine (combined cycle, extraction plant) | Gas turbine (combined cycle, back-pressure)
Electric capacity |  |  | MW-e |  | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500
Nominal investment |  |  | MEUR/MW-e |  | 1.8987 | 1.4296 | 1.1688 | 0.99979 | 0.88 | 0.78999 | 0.71949 | 0.66255 | 0.61544
- of which equipment |  |  | MEUR/MW-e |  | 1.4672 | 1.1047 | 0.90318 | 0.77257 | 0.68 | 0.61044 | 0.55597 | 0.51197 | 0.47557
- of which installation |  |  | MEUR/MW-e |  | 0.43153 | 0.3249 | 0.26564 | 0.22723 | 0.2 | 0.17954 | 0.16352 | 0.15058 | 0.13987
6.3 Gas turbine simple cycle
6.3.1 Technical- and economic assumptions
Table 6-8: Technical- and economic assumptions for a simple cycle gas turbine [1]
Technology |  |  |  |  | Gas turbine (simple cycle, large, back pressure) |  | Gas turbine (simple cycle, small and medium, back pressure)
[5 empty] | 2020 |  | 2020
Energy/technical data
Generating capacity for one unit (MW) |  |  |  |  | 80 |  | 25
Electricity efficiency (condensation mode for extraction plants), net (%) |  |  |  |  | 42 |  | 37
Electricity efficiency (condensation mode for extraction plants), net (%), annual average |  |  |  |  | 40 |  | 35
Cb coefficient (50oC/100oC) |  |  |  |  | 0.96 |  | 0.73
Cv coefficient (50oC/100oC) |  |  |  |  | - |  | -
Forced outage (%) |  |  |  |  | 2 |  | 2
Planned outage (weeks per year) |  |  |  |  | 3 |  | 2.8
Technical lifetime (years) |  |  |  |  | 25 |  | 25
Construction time (years) |  |  |  |  | 1.5 |  | 1.5
Space requirement (1000m2/MW) |  |  |  |  | 0.02 |  | 0.04
Plant Dynamic Capabilities
Primary regulation (% per 30 seconds) |  |  |  |  | 0 |  | 0
Secondary regulation (% per minute) |  |  |  |  | 20 |  | 20
Minimum load (% of full load) |  |  |  |  | 23 |  | 23
Warm start-up time (hours) |  |  |  |  | 0.23 |  | 0.23
Cold start-up time (hours) |  |  |  |  | 0.5 |  | 0.5
Environment
SO2 (degree of desulphuring, %) |  |  |  |  | 0 |  | 0
NOX (g per GJ fuel) |  |  |  |  | 15 |  | 15
CH4 (g per GJ fuel) |  |  |  |  | 1.5 |  | 1.5
N2O (g per GJ fuel) |  |  |  |  | 1 |  | 1
Financial data (in 2015€)
Nominal investment (M€/MW) |  |  |  |  | 0.59 |  | 0.73
- of which equipment |  |  |  |  | 0.4425 |  | 0.5475
- of which installation |  |  |  |  | 0.1475 |  | 0.1825
Fixed O&M (€/MW/year) |  |  |  |  | 19500 |  | 19500
Variable O&M (€/MWh) |  |  |  |  | 4.4 |  | 5.4
Financial data (EUR) |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | 0.59 |  | 0.73
- of which equipment |  |  |  |  | 0.4425 |  | 0.5475
- of which installation |  |  |  |  | 0.1475 |  | 0.1825
Fixed O&M |  |  | EUR/MW/year |  | 19500 |  | 19500
Variable O&M (€/MWh) |  |  | EUR/MWh |  | 4.4 |  | 5.4
Gas turbine (simple cycle, large, back pressure) |  |  | Unit |  | Gas turbine (simple cycle, large, back pressure) | Gas turbine (simple cycle, small and medium, back pressure)
Electric capacity |  |  | MW-e |  | 10 | 25 | 40 | 55 | 70 | 85 | 100 | 115 | 130
Nominal investment |  |  | MEUR/MW-e |  | 0 | 0 | 0.95846 | 0.76694 | 0.64781 | 0.56549 | 0.50468 | 0.45764 | 0.42001
- of which equipment |  |  | MEUR/MW-e |  | 0 | 0 | 0.71884 | 0.5752 | 0.48586 | 0.42411 | 0.37851 | 0.34323 | 0.315
- of which installation |  |  | MEUR/MW-e |  | 0 | 0 | 0.23961 | 0.19173 | 0.16195 | 0.14137 | 0.12617 | 0.11441 | 0.105
Table 6-9: Gas Turbine Performance Characteristics [13]
Description |  | System
|  | 1 | 2 | 3 | 4 | 5 | 6
Nominal Electric Power (kW) |  | 3515 | 4600 | 7965 | 11350 | 21745 | 43069
Net Electric Power (kW)4 |  | 3304 | 4324 | 7487 | 10669 | 20440 | 40485
Fuel Input (MMBtu/hr, HHV)5 |  | 47.5 | 59.1 | 87.6 | 130 | 210.8 | 389
Useful Thermal (MMBtu/hr) |  | 19.6 | 25.2 | 36.3 | 52.2 | 77.4 | 133.8
Power to Heat Ratio6 |  | 0.58 | 0.58 | 0.7 | 0.7 | 0.9 | 1.03
Electric Efficiency (%, HHV) |  | 23.7% | 25% | 29.2% | 28% | 33.1% | 35.5%
Thermal Efficiency (%, HHV)7 |  | 41.1% | 42.7% | 41.4% | 40.2% | 36.7% | 34.4%
Overall Efficiency (%, HHV) |  | 64.9% | 67.6% | 70.6% | 68.2% | 69.8% | 69.9%
Special site requirements, emissions control requirements, and prevailing labor rates. the table shows estimated capital costs for six representative gas turbine CHP systems used in typical applications. As indicated, there are economies of scale, with installed costs declining from $3,320/kW for a 3.3 MW system to $1,276/kW for a 40 MW system. Routine maintenance practices include online running maintenance, predictive maintenance, plotting trends, performance testing, vibration analysis, and preventive maintenance procedures. Typically, routine inspections are required every 4,000 hours to ensure that the turbine is free of excessive vibration due
Table 6-10: Gas Turbine Capital and O&M Costs [13]
Description |  | System 1: System
|  | 1 | 2 | 3 | 4 | 5 | 6
Net Electric Power (kW) |  | 3304 | 4324 | 7487 | 10669 | 20440 | 40485
Combustion Turbine ($/kW) |  | 908 | 860 | 683 | 619 | 563 | 477
Emissions Control ($/kW) |  | 208 | 174 | 126 | 92 | 74 | 65
Balance of Plant ($/kW) |  | 899 | 712 | 455 | 389 | 276 | 231
Construction and Installation ($/kW) |  | 1305 | 1072 | 753 | 698 | 562 | 503
Total Installed Cost ($/kW) |  | 3320 | 2817 | 2017 | 1798 | 1474 | 1276
Total O&M (¢/kWh) |  | 1.3 | 1.3 | 1.2 | 1.2 | 0.9 | 0.9
Note: Costs are average values and are not intended to represent a specific product.
6.4 Biomass CHP
Figure 6-1: Avedøre power plant
6.4.1 Wood chips CHP
Table 6-11: Technical- and economic assumptions for a wood chips CHP [1]
Technology |  | System 4: Large Wood Chips CHP (600 MW feed, back-pressure); System 6: Medium Wood Chips CHP (80 MW feed, back-pressure) |  | Small Wood Chips CHP (ORC, 20 MW feed, back-pressure)
|  | System 4: 2020; System 6: 2020 |  | 2020
Energy/technical data
Generating capacity for one unit (MWe) |  | System 4: 176.9; System 6: 23.1 |  | 2.9
Electricity efficiency, net (%), name plate |  | System 4: 29.5; System 6: 28.9 |  | 14.3
Electricity efficiency, net (%), annual average |  | System 4: 28; System 6: 27.4 |  | 13.5
Heat efficiency, net (%), name plate |  | System 4: 82.2; System 6: 82.1 |  | 97.3
Heat efficiency, net (%), annual average |  | System 4: 83.6; System 6: 83.5 |  | 98.1
Additional heat potential with heat pumps (% of thermal input) |  | System 4: 1.9; System 6: 2 |  | 2
Cb coefficient (40°C/80°C) |  | System 4: 0.36; System 6: 0.35 |  | 0.15
Cv coefficient (40°C/80°C) | [8 empty] | 1 | bar: System 4; System 6
Forced outage (%) |  | System 4: 3; System 6: 3 |  | 3
Planned outage (weeks per year) |  | System 4: 3; System 6: 3 |  | 3
Technical lifetime (years) |  | System 4: 25; System 6: 25 |  | 25
Construction time (years) |  | System 4: 5; System 6: 2.5 |  | 1
Space requirement (1000 m2/MWe) |  | System 4: 0.08; System 6: 0.2 |  | 0.7
Plant Dynamic Capabilities
Primary regulation (% per 30 seconds) |  | System 4: 2; System 6: NA |  | NA
Secondary regulation (% per minute) |  | System 4: 4; System 6: 4 |  | 10
Minimum load (% of full load) |  | System 4: 45; System 6: 20 |  | 20
Warm start-up time (hours) |  | System 4: 2; System 6: 2 |  | 0.25
Cold start-up time (hours) |  | System 4: 12; System 6: 8 |  | 0.5
Environment
SO2 (degree of desulphuring, %) |  | System 4: 98; System 6: 98 |  | 98
NOX (g per GJ fuel) |  | System 4: 24; System 6: 72 |  | 63
CH4 (g per GJ fuel) |  | System 4: 2; System 6: 2 |  | 11
N2O (g per GJ fuel) |  | System 4: 8; System 6: 1 |  | 1
Particles (g per GJ fuel) |  | System 4: 0.3; System 6: 0.3 |  | 0.3
Financial data
Nominal investment (M€/MWe) |  | System 4: 3.4; System 6: 3.6 |  | 6.5
- of which equipment |  | System 4: 2.2; System 6: 2.4 |  | 4
- of which installation |  | System 4: 1.2; System 6: 1.2 |  | 2.5
Fixed O&M (€/MWe/year) |  | System 4: 97600; System 6: 153600 |  | 288900
Variable O&M (€/MWh_e) |  | System 4: 3.8; System 6: 3.8 |  | 7.8
Financial data (EUR) |  | System 2: Unit
Nominal investment |  | System 2: MEUR/MW; System 4: 3.4; System 6: 3.6 |  | 6.5
- of which equipment |  | System 4: 2.2; System 6: 2.4 |  | 4
- of which installation |  | System 4: 1.2; System 6: 1.2 |  | 2.5
Fixed O&M |  | System 2: EUR/MW/year; System 4: 97600; System 6: 153600 |  | 288900
Variable O&M (€/MWh) |  | System 2: EUR/MWh; System 4: 3.8; System 6: 3.8 |  | 7.8
Technology specific data
Steam reheat |  | System 4: None; System 6: None |  | None
Flue gas condensation |  | System 4: Yes; System 6: Yes |  | Yes
Combustion air humidification |  | System 4: Yes; System 6: Yes |  | Yes
Nominal investment (M€/MW fuel input) |  | System 4: 1; System 6: 1.05 |  | 0.93
- of which equipment |  | System 4: 0.65; System 6: 0.71 |  | 0.58
- of which installation |  | System 4: 0.35; System 6: 0.35 |  | 0.35
Fixed O&M (€/MW input/year) |  | System 4: 28800; System 6: 44369 |  | 41200
Variable O&M (€/MWh input) |  | System 4: 1.1; System 6: 1.1 |  | 1.1
Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) |  | System 4: 0.01; System 6: 0.015 |  | 0.02
Large Wood Chips CHP (600 MW feed, back-pressure) |  |  | Unit |  | Large Wood Chips CHP (600 MW feed, back-pressure) | Medium Wood Chips CHP (80 MW feed, back-pressure) | Small Wood Chips CHP (ORC, 20 MW feed, back-pressure)
Electric capacity |  |  | MW-e |  | 5 | 7.5 | 10 | 15 | 20 | 25 | 150 | 200 | 250
Nominal investment |  |  | MEUR/MW-e |  | 0 | 0 | 0 | 0 | 0 | 0 | 3.8161 | 3.1201 | 2.6689
- of which equipment |  |  | MEUR/MW-e |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.4693 | 2.0189 | 1.7269
- of which installation |  |  | MEUR/MW-e |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.3469 | 1.1012 | 0.94196
6.4.2 Wood pellets CHP
Table 6-12: Technical- and economic assumptions for a large wood pellets CHP (800 MW feed, back-pressure) [1]
Technology |  | System 4: Large Wood Pellets CHP, 800 MW feed, back pressure; System 6: Medium Wood Pellets CHP, 80 MW feed, back pressure |  | Small Wood Pellets CHP, 20 MW feed, back pressure
|  | System 4: 2020; System 6: 2020 |  | 2020
Energy/technical data
Generating capacity for one unit (MWe) |  | System 4: 261.2; System 6: 24.1 |  | 3
Electricity efficiency, net (%), name plate |  | System 4: 32.6; System 6: 30.2 |  | 15.1
Electricity efficiency, net (%), annual average |  | System 4: 31; System 6: 28.6 |  | 14.4
Heat efficiency, net (%), name plate |  | System 4: 63.9; System 6: 66.5 |  | 82.2
Heat efficiency, net (%), annual average |  | System 4: 65.5; System 6: 68 |  | 83
Additional heat potential with heat pumps (% of thermal input) |  | System 4: 1.7; System 6: 1.7 |  | 1.7
Cb coefficient (40°C/80°C) |  | System 4: 0.51; System 6: 0.45 |  | 0.18
Cv coefficient (40°C/80°C) | [8 empty] | 1 | bar: System 4; System 6
Forced outage (%) |  | System 4: 3; System 6: 3 |  | 3
Planned outage (weeks per year) |  | System 4: 3; System 6: 3 |  | 3
Technical lifetime (years) |  | System 4: 25; System 6: 25 |  | 25
Construction time (years) | [8 empty] | 1 | bar: System 4; System 6
Space requirement (1000 m2/MWe) |  | System 4: 0.06; System 6: 0.19 |  | 0.5
Plant Dynamic Capabilities
Primary regulation (% per 30 seconds) |  | System 4: 2; System 6: NA |  | NA
Secondary regulation (% per minute) |  | System 4: 4; System 6: 10 |  | 10
Minimum load (% of full load) |  | System 4: 15; System 6: 15 |  | 20
Warm start-up time (hours) |  | System 4: 2; System 6: 0.25 |  | 0.25
Cold start-up time (hours) |  | System 4: 12; System 6: 8 |  | 0.5
Environment
SO2 (degree of desulphuring, %) |  | System 4: 98.3; System 6: 98.3 |  | 98.3
NOX (g per GJ fuel) |  | System 4: 21; System 6: 62 |  | 54
CH4 (g per GJ fuel) |  | System 4: 0; System 6: 0 |  | 0
N2O (g per GJ fuel) | [8 empty] | 1 | bar: System 4; System 6
Particles (g per GJ fuel) |  | System 4: 0.3; System 6: 0.3 |  | 0.3
Financial data
Nominal investment (M€/MWe) |  | System 4: 2.3; System 6: 3.1 |  | 6.1
- of which equipment |  | System 4: 1.3; System 6: 2 |  | 4
- of which installation |  | System 4: 1; System 6: 1.1 |  | 2.1
Fixed O&M (€/MWe/year) |  | System 4: 64000; System 6: 127100 |  | 275900
Variable O&M (€/MWh_e) |  | System 4: 1.6; System 6: 1.7 |  | 3.4
Financial data (EUR) |  | System 2: Unit
Nominal investment |  | System 2: MEUR/MW; System 4: 2.3; System 6: 3.1 |  | 6.1
- of which equipment |  | System 4: 1.3; System 6: 2 |  | 4
- of which installation |  | System 4: 1; System 6: 1.1 |  | 2.1
Fixed O&M |  | System 2: EUR/MW/year; System 4: 64000; System 6: 127100 |  | 275900
Variable O&M (€/MWh) |  | System 2: EUR/MWh; System 4: 1.6; System 6: 1.7 |  | 3.4
Technology specific data
Steam reheat |  | System 4: None; System 6: None |  | None
Flue gas condensation |  | System 4: Yes; System 6: Yes |  | Yes
Combustion air humidification |  | System 4: Yes; System 6: Yes |  | Yes
Nominal investment (M€/MW fuel input) |  | System 4: 0.75; System 6: 0.93 |  | 0.93
- of which equipment |  | System 4: 0.42; System 6: 0.59 |  | 0.61
- of which installation |  | System 4: 0.33; System 6: 0.33 |  | 0.32
Fixed O&M (€/MW input/year) |  | System 4: 20900; System 6: 38300 |  | 41700
Variable O&M (€/MWh input) |  | System 4: 0.51; System 6: 0.51 |  | 0.51
Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) |  | System 4: 0.002; System 6: 0.003 |  | 0.004
Small Wood Pellets CHP, 20 MW feed, back pressure |  |  | Unit |  | Large Wood Pellets CHP, 800 MW feed, back pressure | Medium Wood Pellets CHP, 80 MW feed, back pressure | Small Wood Pellets CHP, 20 MW feed, back pressure
Electric capacity |  |  | MW-e |  | 5 | 7.5 | 10 | 15 | 20 | 25 | 200 | 250 | 300
Nominal investment |  |  | MEUR/MW-e |  | 4.2661 | 3.212 | 2.6261 | 0 | 0 | 0 | 0 | 0 | 0
- of which equipment |  |  | MEUR/MW-e |  | 2.7975 | 2.1062 | 1.722 | 0 | 0 | 0 | 0 | 0 | 0
- of which installation |  |  | MEUR/MW-e |  | 1.4687 | 1.1058 | 0.90407 | 0 | 0 | 0 | 0 | 0 | 0
6.4.3 Straw CHP
Table 6-13: Technical- and economic assumptions for a large straw CHP (132 MW feed, back-pressure) [1]
Technology |  | System 4: Large Straw CHP (132 MW feed, back pressure); System 6: Medium Straw CHP (80 MW feed, back pressure) |  | Small Straw CHP (20 MW feed, back pressure)
|  | System 4: 2020; System 6: 2020 |  | 2020
Energy/technical data
Generating capacity for one unit (MWe) |  | System 4: 40.7; System 6: 24.4 |  | 3
Electricity efficiency, net (%), name plate |  | System 4: 30.9; System 6: 30.5 |  | 15
Electricity efficiency, net (%), annual average |  | System 4: 29.3; System 6: 29 |  | 14.2
Heat efficiency, net (%), name plate |  | System 4: 67.9; System 6: 67.7 |  | 84.2
Heat efficiency, net (%), annual average |  | System 4: 69.5; System 6: 69.3 |  | 85
Additional heat potential with heat pumps (% of thermal input) |  | System 4: 1.7; System 6: 1.7 |  | 1.7
Cb coefficient (40°C/80°C) |  | System 4: 0.45; System 6: 0.45 |  | 0.18
Cv coefficient (40°C/80°C) | [8 empty] | 1 | bar: System 4; System 6
Forced outage (%) |  | System 4: 3; System 6: 4 |  | 4
Planned outage (weeks per year) |  | System 4: 3; System 6: 4 |  | 4
Technical lifetime (years) |  | System 4: 25; System 6: 25 |  | 25
Construction time (years) |  | System 4: 3; System 6: 2.5 |  | 1
Space requirement (1000 m2/MWe) |  | System 4: 0.2; System 6: 0.3 |  | 1
Plant Dynamic Capabilities
Primary regulation (% per 30 seconds) |  | System 4: 2; System 6: NA |  | NA
Secondary regulation (% per minute) |  | System 4: 4; System 6: 4 |  | 10
Minimum load (% of full load) |  | System 4: 40; System 6: 40 |  | 50
Warm start-up time (hours) |  | System 4: 2; System 6: 2 |  | 0.25
Cold start-up time (hours) |  | System 4: 8; System 6: 8 |  | 0.5
Environment
SO2 (degree of desulphuring, %) |  | System 4: 96.4; System 6: 96.4 |  | 96.4
NOX (g per GJ fuel) |  | System 4: 67; System 6: 70 |  | 72
CH4 (g per GJ fuel) |  | System 4: 0; System 6: 0 |  | 11
N2O (g per GJ fuel) | [8 empty] | 1 | bar: System 4; System 6
Particles (g per GJ fuel) |  | System 4: 0.3; System 6: 0.3 |  | 0.3
Financial data
Nominal investment (M€/MWe) |  | System 4: 3.4; System 6: 3.8 |  | 6.8
- of which equipment |  | System 4: 2.1; System 6: 2.3 |  | 3.8
- of which installation |  | System 4: 1.3; System 6: 1.5 |  | 3
Fixed O&M (€/MWe/year) |  | System 4: 124900; System 6: 149900 |  | 318200
Variable O&M (€/MWh_e) |  | System 4: 1.9; System 6: 2 |  | 4
Financial data (EUR) |  | System 2: Unit
Nominal investment |  | System 2: MEUR/MW; System 4: 3.4; System 6: 3.8 |  | 6.8
- of which equipment |  | System 4: 2.1; System 6: 2.3 |  | 3.8
- of which installation |  | System 4: 1.3; System 6: 1.5 |  | 3
Fixed O&M |  | System 2: EUR/MW/year; System 4: 124900; System 6: 149900 |  | 318200
Variable O&M (€/MWh) |  | System 2: EUR/MWh; System 4: 1.9; System 6: 2 |  | 4
Technology specific data
Steam reheat |  | System 4: None; System 6: None |  | None
Flue gas condensation |  | System 4: Yes; System 6: Yes |  | Yes
Combustion air humidification |  | System 4: Yes; System 6: Yes |  | Yes
Nominal investment (M€/MW fuel input) |  | System 4: 1.07; System 6: 1.16 |  | 1.02
- of which equipment |  | System 4: 0.66; System 6: 0.71 |  | 0.58
- of which installation |  | System 4: 0.41; System 6: 0.45 |  | 0.44
Fixed O&M (€/MW input/year) |  | System 4: 38500; System 6: 45800 |  | 47700
Variable O&M (€/MWh input) |  | System 4: 0.6; System 6: 0.6 |  | 0.6
Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) |  | System 4: 0.063; System 6: 0.068 |  | 0.078
Medium Straw CHP (80 MW feed, back pressure) |  |  | Unit |  | Large Straw CHP (132 MW feed, back pressure) | Medium Straw CHP (80 MW feed, back pressure) | Small Straw CHP (20 MW feed, back pressure)
Electric capacity |  |  | MW-e |  | 5 | 7.5 | 10 | 15 | 20 | 25 | 40 | 50 | 60
Nominal investment |  |  | MEUR/MW-e |  | 0 | 0 | 0 | 5.3419 | 4.3675 | 3.7359 | 0 | 0 | 0
- of which equipment |  |  | MEUR/MW-e |  | 0 | 0 | 0 | 3.2332 | 2.6435 | 2.2612 | 0 | 0 | 0
- of which installation |  |  | MEUR/MW-e |  | 0 | 0 | 0 | 2.1086 | 1.724 | 1.4747 | 0 | 0 | 0
6.5 Waste CHP
6.5.1 Technical- and economic assumptions
Table 6-14: Technical- and economic assumptions for a WtE CHP [1]
Technology |  | System 4: Large Waste to Energy CHP (220 MW feed, back-pressure); System 6: Medium Waste to Energy CHP (80 MW feed, back-pressure) |  | Small Waste to Energy CHP (35 MW feed, back-pressure)
|  | System 4: 2020; System 6: 2020 |  | 2020
Energy/technical data
Generating capacity for one unit (MWe) |  | System 4: 51.2; System 6: 18.4 |  | 7.9
Incineration capacity (Fuel input) (tonnes/h) |  | System 4: 74.7; System 6: 27.2 |  | 11.9
Electricity efficiency, net (%), name plate |  | System 4: 23.3; System 6: 23 |  | 22.6
Electricity efficiency, net (%), annual average |  | System 4: 22.1; System 6: 21.9 |  | 21.4
Heat efficiency, net (%), name plate |  | System 4: 78.1; System 6: 78 |  | 78.5
Heat efficiency, net (%), annual average |  | System 4: 79.3; System 6: 79.1 |  | 79.6
Additional heat potential with heat pumps (% of thermal input) |  | System 4: 4.1; System 6: 4.1 |  | 4.1
Cb coefficient (40°C/80°C) |  | System 4: 0.3; System 6: 0.3 |  | 0.29
Cv coefficient (40°C/80°C) | [8 empty] | 1 | bar: System 4; System 6
Forced outage (%) | [8 empty] | 1 | bar: System 4; System 6
Planned outage (weeks per year) |  | System 4: 2.4; System 6: 2.9 |  | 3.3
Technical lifetime (years) |  | System 4: 25; System 6: 25 |  | 25
Construction time (years) |  | System 4: 3; System 6: 2.5 |  | 2.5
Space requirement (1000 m2/MWe) |  | System 4: 0.8; System 6: 1.6 |  | 2.5
Plant Dynamic Capabilities
Primary regulation (% per 30 seconds) |  | System 4: 5; System 6: 5 |  | NA
Secondary regulation (% per minute) |  | System 4: 10; System 6: 10 |  | 10
Minimum load (% of full load) |  | System 4: 20; System 6: 20 |  | 20
Warm start-up time (hours) |  | System 4: 0.5; System 6: 0.5 |  | 0.5
Cold start-up time (hours) |  | System 4: 2; System 6: 2 |  | 2
Environment
SO2 (degree of desulphuring, %) |  | System 4: 99.8; System 6: 99.8 |  | 99.8
NOX (g per GJ fuel) |  | System 4: 56; System 6: 56 |  | 67
CH4 (g per GJ fuel) |  | System 4: 0.1; System 6: 0.1 |  | 0.1
N2O (g per GJ fuel) | [8 empty] | 1 | bar: System 4; System 6
Particles (g per GJ fuel) |  | System 4: 0.3; System 6: 0.3 |  | 0.3
Financial data
Nominal investment (M€/MWe) |  | System 4: 7.8; System 6: 9.1 |  | 10.5
- of which equipment |  | System 4: 4.7; System 6: 5.5 |  | 6.5
- of which installation |  | System 4: 3.1; System 6: 3.6 |  | 4
Fixed O&M (€/MWe/year) |  | System 4: 188300; System 6: 264800 |  | 413600
Variable O&M (€/MWh_e) |  | System 4: 24.8; System 6: 25 |  | 25.6
Financial data (EUR) |  | System 2: Unit
Nominal investment |  | System 2: MEUR/MW; System 4: 7.8; System 6: 9.1 |  | 10.5
- of which equipment |  | System 4: 4.7; System 6: 5.5 |  | 6.5
- of which installation |  | System 4: 3.1; System 6: 3.6 |  | 4
Fixed O&M |  | System 2: EUR/MW/year; System 4: 188300; System 6: 264800 |  | 413600
Variable O&M (€/MWh) |  | System 2: EUR/MWh; System 4: 24.8; System 6: 25 |  | 25.6
Technology specific data
Steam reheat |  | System 4: None; System 6: None |  | None
Flue gas condensation |  | System 4: Yes; System 6: Yes |  | Yes
Combustion air humidification | [8 empty] | No | bar: System 4; System 6
Nominal investment (M€/MW fuel input) |  | System 4: 1.83; System 6: 2.1 |  | 2.36
- of which equipment |  | System 4: 1.1; System 6: 1.28 |  | 1.47
- of which installation |  | System 4: 0.72; System 6: 0.82 |  | 0.89
Fixed O&M (€/MW input/year) |  | System 4: 43900; System 6: 61000 |  | 93400
Variable O&M (€/MWh input) |  | System 4: 5.8; System 6: 5.8 |  | 5.8
Nominal investment (€/(tonne/year)) |  | System 4: 672; System 6: 773 |  | 869
Fixed O&M (€/tonne) |  | System 4: 16; System 6: 22 |  | 34
Variable O&M (€/tonne) |  | System 4: 17; System 6: 17 |  | 17
Medium Waste to Energy CHP (80 MW feed, back-pressure) |  |  | Unit |  | Large Waste to Energy CHP (220 MW feed, back-pressure) | Medium Waste to Energy CHP (80 MW feed, back-pressure) | Small Waste to Energy CHP (35 MW feed, back-pressure)
Electric capacity |  |  | MW-e |  | 5 | 7.5 | 10 | 15 | 20 | 25 | 40 | 50 | 60
Nominal investment |  |  | MEUR/MW-e |  | 0 | 0 | 0 | 10.499 | 8.5841 | 7.3427 | 0 | 0 | 0
- of which equipment |  |  | MEUR/MW-e |  | 0 | 0 | 0 | 6.3456 | 5.1882 | 4.4379 | 0 | 0 | 0
- of which installation |  |  | MEUR/MW-e |  | 0 | 0 | 0 | 4.1535 | 3.3959 | 2.9048 | 0 | 0 | 0
6.6 New technology 1
6.6.1 Technical- and economic assumptions
6.7 New technology 2
6.7.1 Technical- and economic assumptions
6.8 CHP technology output
Technology | Reference | Electric capacity | Heat capacity | Solar thermal size | Storage size | Fuel | Voltage connection level | Full load hours |  |  | Investment (el) (eqiupment) | Investment (el) (installation) | Investment (heat) (equipment)
|  | MW-e | MW-h | m2 panel | m3 storage |  |  | Black | Blue | Green | mil. EUR/MW-el | mil. EUR/MW-el | mil. EUR/MW-heat
Small CHP - waste | [1] | 8 | 30 | --- | --- | Waste | --- | 7000 | 7000 | 7000 | 6.5 | 4 | ---
Medium CHP - waste | [1] | 18 | 64 | --- | --- | Waste | --- | 7000 | 7000 | 7000 | 5.5 | 3.6 | ---
Large CHP - waste | [1] | 51 | 173 | --- | --- | Waste | --- | 7000 | 7000 | 7000 | 4.7 | 3.1 | ---
Boiler - waste | [1] | --- | 37 | --- | --- | Waste | --- | 7000 | 7000 | 7000 | --- | --- | 1.05
Small CHP - wood chips | [1] | 3 | 21 | --- | --- | Wood chips | --- | 5000 | 4500 | 4000 | 4 | 2.5 | ---
Medium CHP - wood chips | [1] | 23 | 65 | --- | --- | Wood chips | --- | 5000 | 4500 | 4000 | 2.4 | 1.2 | ---
Large CHP - wood chips | [1] | 177 | 484 | --- | --- | Wood chips | --- | 5000 | 4500 | 4000 | 2.2 | 1.2 | ---
Small CHP - wood pellets | [1] | 3 | 16 | --- | --- | Wood pellets | --- | 4000 | 3500 | 3000 | 4 | 2.2 | ---
Medium CHP - wood pellets | [1] | 24 | 54 | --- | --- | Wood pellets | --- | 4000 | 3500 | 3000 | 2 | 1.1 | ---
Large CHP - wood pellets | [1] | 261 | 522 | --- | --- | Wood pellets | --- | 4000 | 3500 | 3000 | 1.3 | 1 | ---
Small CHP - straw | [1] | 3 | 17 | --- | --- | Straw | --- | 5000 | 4500 | 4000 | 3.8 | 3 | ---
Medium CHP - straw | [1] | 24 | 53 | --- | --- | Straw | --- | 5000 | 4500 | 4000 | 2.3 | 1.5 | ---
Large CHP - straw | [1] | 41 | 90 | --- | --- | Straw | --- | 5000 | 4500 | 4000 | 2.1 | 1.3 | ---
Large CHP - coal | [1] | 550 | 655 | --- | --- | Coal | --- | 5000 | 4000 | 3000 | 1.9 | --- | ---
Medium CHP - natural gas SC | [1] | 27.5 | 38 | --- | --- | Natural gas | --- | 4000 | 3500 | 3000 | 0.73 | --- | ---
Large CHP - natural gas SC | [1] | 82.5 | 87 | --- | --- | Natural gas | --- | 4000 | 3500 | 3000 | 0.59 | --- | ---
Medium CHP - natural gas CC | [1] | 55 | 42 | --- | --- | Natural gas | --- | 4000 | 3500 | 3000 | 1 | 0.3 | ---
Large CHP - natural gas CC | [1] | 300 | 167 | --- | --- | Natural gas | --- | 4000 | 3500 | 3000 | 0.68 | 0.2 | ---
Engine - natural gas | [1] | 5.5 | 5.8 | --- | --- | Natural gas | --- | 4000 | 3500 | 3000 | 0.6 | 0.35 | ---
Large CHP - coal - carbon capture | Ramboll | 495 | 619 | --- | --- | Coal | --- | 5000 | 4000 | 3000 | 3.52 | --- | ---
Large CHP - wood chips - carbon capture | Ramboll | 159 | 572 | --- | --- | Wood chips | --- | 4000 | 3500 | 3000 | 5.3235 | 2.8665 | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Technology | Investment (heat) (installation) | Investment (solar) | Investment (storage) | Fixed O&M (el) | Fixed O&M (heat) | Fixed O&M (solar) | Fixed O&M (storage) | Var. O&M (el) | Var. O&M (heat) | Lifetime | CV | CB | Electric efficiency CHP
| mil. EUR/MW-heat | EUR/m2 panel | EUR/m3 storage | EUR/MW-el/year | EUR/MW-heat/year | EUR/m2 panel/year | EUR/m3 storage/year | EUR/MWh-el | EUR/MWh-heat | year |  |  | MW-el/MW-fuel
Small CHP - waste | --- | --- | --- | 413600 | --- | --- | --- | 25.6 | --- | 25 | 1 | 0.26582 | 0.21
Medium CHP - waste | --- | --- | --- | 264800 | --- | --- | --- | 25 | --- | 25 | 1 | 0.28205 | 0.22
Large CHP - waste | --- | --- | --- | 188300 | --- | --- | --- | 24.8 | --- | 25 | 1 | 0.29487 | 0.23
Boiler - waste | 0.78 | --- | --- | --- | 78600 | --- | --- | --- | 5.5 | 25 | --- | --- | ---
Small CHP - wood chips | --- | --- | --- | 288900 | --- | --- | --- | 7.8 | --- | 25 | 1 | 0.14433 | 0.14
Medium CHP - wood chips | --- | --- | --- | 153600 | --- | --- | --- | 3.8 | --- | 25 | 1 | 0.35366 | 0.29
Large CHP - wood chips | --- | --- | --- | 97600 | --- | --- | --- | 3.8 | --- | 25 | 1 | 0.36585 | 0.3
Small CHP - wood pellets | --- | --- | --- | 275900 | --- | --- | --- | 3.4 | --- | 25 | 1 | 0.18293 | 0.15
Medium CHP - wood pellets | --- | --- | --- | 127100 | --- | --- | --- | 1.7 | --- | 25 | 1 | 0.44776 | 0.3
Large CHP - wood pellets | --- | --- | --- | 64000 | --- | --- | --- | 1.6 | --- | 25 | 1 | 0.5 | 0.32
Small CHP - straw | --- | --- | --- | 318200 | --- | --- | --- | 4 | --- | 25 | 1 | 0.17857 | 0.15
Medium CHP - straw | --- | --- | --- | 149900 | --- | --- | --- | 2 | --- | 25 | 1 | 0.45588 | 0.31
Large CHP - straw | --- | --- | --- | 124900 | --- | --- | --- | 1.9 | --- | 25 | 1 | 0.45588 | 0.31
Large CHP - coal | --- | --- | --- | 31000 | --- | --- | --- | 2.9 | --- | 25 | 0.15 | 0.84 | 0.42
Medium CHP - natural gas SC | --- | --- | --- | 18600 | --- | --- | --- | 5.1 | --- | 25 | --- | 0.72727 | 0.32
Large CHP - natural gas SC | --- | --- | --- | 29500 | --- | --- | --- | 4.5 | --- | 25 | --- | 0.94595 | 0.35
Medium CHP - natural gas CC | --- | --- | --- | 29300 | --- | --- | --- | 4.4 | --- | 25 | --- | 1.3143 | 0.46
Large CHP - natural gas CC | --- | --- | --- | 29300 | --- | --- | --- | 4.4 | --- | 25 | --- | 1.8 | 0.54
Engine - natural gas | --- | --- | --- | 9750 | --- | --- | --- | 5.4 | --- | 25 | --- | 0.95455 | 0.42
Large CHP - coal - carbon capture | --- | --- | --- | 65666 | --- | --- | --- | 2.9 | --- | 25 | 0.15 | 0.8 | 0.32
Large CHP - wood chips - carbon capture | --- | --- | --- | 132266 | --- | --- | --- | 3.8 | --- | 25 | 1 | 0.27778 | 0.2
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Technology | Heat efficiency CHP | Electric efficiency condensing | Heat efficiency | CO2 capture rate (amount of emission) | SO2 (degree of desulphuring) | Emission factor SO2 | Emission factor NOX | Emission factor CH4 | Emission factor N2O | Emission factor PM2.5
| MW-heat/MW-fuel | MW-el/MW-fuel | MW-heat/MW-fuel | % | % | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f
Small CHP - waste | 0.79 | --- | --- | 0% | 99.8% | --- | 241.2 | 0.36 | 3.6 | 1.08
Medium CHP - waste | 0.78 | --- | --- | 0% | 99.8% | --- | 201.6 | 0.36 | 3.6 | 1.08
Large CHP - waste | 0.78 | --- | --- | 0% | 99.8% | --- | 201.6 | 0.36 | 3.6 | 1.08
Boiler - waste | --- | --- | 1.05 | 0% | 99.8% | --- | 241.2 | 0.36 | 3.6 | 1.08
Small CHP - wood chips | 0.97 | --- | --- | 0% | 98% | --- | 226.8 | 39.6 | 3.6 | 1.08
Medium CHP - wood chips | 0.82 | --- | --- | 0% | 98% | --- | 25920% | 720% | 360% | 1.08
Large CHP - wood chips | 0.82 | --- | --- | 0 | 0.98 | --- | 86.4 | 7.2 | 28.8 | 1.08
Small CHP - wood pellets | 0.82 | --- | --- | 0 | 0.983 | --- | 194.4 | 0 | 3.6 | 1.08
Medium CHP - wood pellets | 0.67 | --- | --- | 0 | 0.983 | --- | 223.2 | 0 | 3.6 | 1.08
Large CHP - wood pellets | 0.64 | --- | --- | 0 | 0.983 | --- | 75.6 | 0 | 3.6 | 1.08
Small CHP - straw | 0.84 | --- | --- | 0 | 0.964 | --- | 259.2 | 39.6 | 3.6 | 1.08
Medium CHP - straw | 0.68 | --- | --- | 0 | 0.964 | --- | 252 | 0 | 3.6 | 1.08
Large CHP - straw | 0.68 | --- | --- | 0 | 0.964 | --- | 241.2 | 0 | 3.6 | 1.08
Large CHP - coal | 0.5 | 0.49 | --- | 0 | 0.97 | --- | 126 | 5.4 | 2.88 | 0
Medium CHP - natural gas SC | 0.44 | 0.37 | --- | 0 | 0 | --- | 54 | 5.4 | 3.6 | 0
Large CHP - natural gas SC | 0.37 | 0.4 | --- | 0 | 0 | --- | 54 | 5.4 | 3.6 | 0
Medium CHP - natural gas CC | 0.35 | 0.51 | --- | 0 | 0 | --- | 54 | 5.4 | 3.6 | 0
Large CHP - natural gas CC | 0.3 | 0.59 | --- | 0 | 0 | --- | 54 | 5.4 | 3.6 | 0
Engine - natural gas | 0.44 | 0.47 | --- | 0 | 0 | --- | 216 | 1134 | 2.16 | 0
Large CHP - coal - carbon capture | 0.4 | 0.39 | --- | 0.9 | 0.97 | --- | 126 | 5.4 | 2.88 | 0
Large CHP - wood chips - carbon capture | 0.72 | --- | --- | 0.9 | 0.98 | --- | 86.4 | 7.2 | 28.8 | 1.08
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Combined Heat and Power Plants, CHP plants, are considered very important as they in a highly efficient way can generate heat and power in co-generation.
As all power plants also generates heat, which either is lost at lowest possible temperature in cooling towers or in the seawater, or can be utilized for heating or processes, we describe all power plants in this category. In order to analyze the cost of generating heat from power plants it is important to compare technologies for power only and CHP for each fuel. The fuel cost of heat from an engine which waste heat at a usefull temperature for heating is e.g. zero.
Like wise, the fuel cost of extracting heat from an extractio plant is equal to the cost of the lost electricity, in case the plant is on operation, and this cost depends on both temperatures, boiler load and heat load. In case the CHP plant can only generate heat and power in a fixed ratio like an angine or a back pressure plant, the cost of heat is equal to the total fuel costs minus the value of the generated electricity.
In the general case it is necessary to simulate the energy system, e.g. with Energy Pro based on load and electricity price profiles in order to analyze the optimal mode of operation, the cost of generating one more MWh heat or one more MWh electricity.
Therefore the description of power plants in this catogery will be simplified assuming that electricity, which is generated in combined production with one fuel e.g. gas else would be generated with the best available technology at a power only plant. The advanced integration of CHP plants into the energy system will be analyzed in the category for Energy Systems
A gas engine for co-generation of heat and power drives an electricity generator for the power production. Electrical efficiency up to 45- 48 % can be achieved. The engine cooling water (engine cooling, lube oil and turbocharger intercooling) and the hot exhaust gas can be used for heat generation, e.g. for district heating or low-pressure steam.
In district heating systems with low return temperatures both sensible and latent heat in the exhaust gas can be recovered by using a condensing cooler as the final cooling of the flue gasses and a total efficiency of approx. 96-98% can be reached. If applying heat pumps for extra cooling of the exhaust gas system, 5-7% higher total efficiency can be reached. The flue gas heat pumps can be electrical or absorption type.
Two combustion concepts are available for spark ignition engines; lean-burn and stoichiometric combustion engines. Lean-burn engines have a high air/fuel-ratio. The combustion temperature and hence the NOx emission is thereby reduced. The engines can be equipped with oxidation catalysts for CO-reduction.
In stoichiometric combustion engines, the amount of air is just sufficient for (theoretically) complete combustion. For this technology, the NOx emission must be reduced in a 3-way catalyst. These engines are usually in the lowest power range (< 150 kWe).
Pre-chamber lean-burn combustion system is a common technology for engines with a bore size typically larger than 200 mm. This technology helps to maximize electrical efficiency and increases combustion stability along with low NOx emissions.
Another ignition technology is used in dual-fuel engines. A dual-fuel engine (diesel-gas) with pilot oil injection is a gas engine that - instead of spark plugs - uses a small amount of light oil (1 - 6% ) to ignite the air-gas mix by compression (as in a diesel engine). Dual fuel engines can often operate on diesel oil alone as well as on gas with pilot oil for ignition.
Main components of combined-cycle gas turbine (CC-GT) plants include: a gas turbine, a steam turbine, a gear (if needed), a generator, and a heat recovery steam generator (HRSG)/flue gas heat exchanger.
The gas turbine and the steam turbine are shown driving a shared generator. In real plants, the two turbines might drive separate generators. Where the single-shaft configuration contributes with higher reliability, the multi-shaft has a slightly better overall performance.
The condenser is cooled by the return water from the district heating network. Since this water is afterwards heated by the flue gas from the gas turbine, the condensation temperature can be fairly low.
The overall energy efficiency depends on the flue gas stack temperature, while the electricity efficiency depends, besides the technical characteristics and the ambient conditions, on the district heating flow temperature. However, some plants do not have the option to sell district heating, and the condenser is therefore cooled by a sea/river/lake or a cooling tower.
If applying heat pumps for extra cooling of the exhaust gas, even higher total fuel efficiency can be reached. Depending on priorities, the flue gas heat pumps can be electrical or absorption type.
The heat recovery steam generator (HRSG) is defined through the number of pressure levels, each producing steam for the steam turbine. Small, medium and large scale units usually have one or two steam pressure stages whereas very large units may have three steam pressure stages. Steam is fed to the turbine both at the inlet and at a later stage between the two adjacent steam turbine sections; this is one of the special features of steam turbines in CC-GT.
Plants being able to shift between condensation mode (power only) and back-pressure mode (power and district heat) include a so-called extraction steam turbine. Such turbines are not available in small sizes, and dual-mode plants are therefore only feasible in large scale.
The power generated by the gas turbine is typically two to three times the power generated by the steam turbine. An extraction steam turbine shifting from full condensation mode at sea temperature to full back-pressure mode at district heat return temperature will typically lose about 10% of its electricity generation capacity. For example, a 40 MW gas turbine combined with a 20 MW steam turbine (condensation mode), loses 2 MW, (10% of 20 MW) or 3% of the total generating capacity (60 MW)
The major components of a simple-cycle (or open-cycle) gas turbine power unit are: a gas turbine, a gear (when needed) and a generator. For cogeneration (combined heat and power production), a flue gas heat exchanger (hot water or steam) is also installed
If applying heat pumps for extra cooling of the exhaust gas, even higher total fuel efficiency can be reached. Depending on priorities, the flue gas heat pumps can be electrical or absorption type.
Simple cycle gas turbines can be used for preheating the feed water of steam power plants. There are in general two types of gas turbines;
1. Industrial turbines (also called heavy duty)
2. Aero-derivative turbine
Industrial gas turbines differ from aero-derivative turbines in the way that the frames, bearings and blading are of heavier construction. Additionally, industrial gas turbines have longer intervals between services compared to the aero-derivatives.
Aero-derivative turbines benefit from higher efficiency than industrial ones and the most servicedemanding module of the aero-derivative gas turbine can normally be replaced in a couple of days, thus keeping a high availability.
Gas turbines can be equipped with compressor intercoolers where the compressed air is cooled to reduce the power needed for compression. The use of integrated recuperators (preheating of the combustion air) to increase efficiency can also be made by using air/air heat exchangers - at the expense of an increased exhaust pressure loss. Gas turbine plants can have direct steam injection in the burner to increase power output through expansion in the turbine section (Cheng Cycle).
Small (radial) gas turbines below 100 kWe are now on the market, the so-called micro-turbines. These are often equipped with preheating of combustion air based on heat from gas turbine exhaust (integrated recuperator) to achieve reasonable electrical efficiency (25 - 30 %).
Energy conversion in CHP or HOP of biomass is the combustion of wood-chips from forestry and/or from wood industry, wood pellets or straw. The main technical differences between the two are the electricity production, which is produced in a CHP but not a HOP, and the resulting necessary operating temperatures.
CHP production from biomass has been used in an increasing scale for many years in Denmark utilizing different technologies. The typical implementation is combustion in a biomass boiler feeding a steam turbine. The energy output from the boiler is either hot water to be used directly for district heating or it could be (high pressure) steam to be expanded through a turbine.
Application of flue gas condensation for further energy generation is customary at biomass fired boilers, except at small plants below 1 - 2 MWth input due to the additional capital and O&M costs. Plants without flue gas condensation should only use fuels with less than 30% moisture content.
WtE plants incinerate waste and produce energy. HOP’s produce only heat, while CHP’s also produce electricity. The flue gas condensation technology was introduced at WtE plants in Denmark in 2004 and has been installed in every new built WtE line in Denmark since 2007. It recovers the heat of condensation of the flue gas content of water vapour. The heat i.e. recovered as low temperature heat and thereby increases the energy efficiency by additional 10-25%-points for mixed waste.
The fuels used in WtE plants include mainly municipal solid waste (MSW) and other combustible non-recyclable wastes. Biomass may be used mainly for starting up and closing down. Some plants in Denmark are feeding green waste from gardens and parks and challenging forest residues such as stubs. In addition, imported Refuse Derived Fuel (RDF) may be used as fuel. Other fuels include gasoil or natural gas for burners used mainly for start-up.
The fuel, waste, is characterised by being heterogeneous having large variation in physical appearance, heating value and chemical composition. The heating value of the waste fed to the furnace is a result of controlled mixing of available waste sources fed to the bunker of the WtE facility. It is usually in the range 7-15 MJ/kg, typically averaging 10-11 MJ/kg, referring to the lower heating value, LHV. For instance, the average heating value was 9.5 MJ/kg varying from 8-11 MJ/kg in 2014 in the WtE facility owned by Amager Resource Center (ARC) in the Copenhagen area. At the time ARC had about 50% waste from trade and industry, which is a high ratio in Denmark. The table below shows the trend of the heating value at Vestforbrænding I/S – the largest MSW plant in Denmark, and also located in the Copenhagen area.
Year 2011 2012 2013 2014 2015
MJ/kg 10.32 10.30 9.80 10.0 10.4
The heating value of the waste received at the WtE plants may be affected by increased focus on recycling, which on one hand may divert organic waste with relatively low heating value and on the other hand divert plastics, paper and wood with relatively high heating value. Many Danish WtE plants are importing RDF waste with relatively high heating value.

## 7. Heat pumps and chillers
Back to user guide
7. Heat pumps and chillers
List of contents
7. Heat pumps and chillers
7.1 Electric heat pump
7.2 Absorption heat pump
7.3 Electric chiller
7.4 New technology 1
7.5 New technology 2
7.6 Heat pump technology output
Assumptions applied (selected in 3.1 LCOE results)
Discount rate |  |  |  |  | 5% | %
Calculation period |  |  |  |  | 1
Start year of calculation |  |  |  |  | 2022
Electricity price development |  |  |  |  | Green
Expected solar thermal production |  |  |  |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  |  |  |  | Sustainable development scenario
Country |  |  |  |  | EU
Currency abbreviation |  |  |  |  | EUR
Currency factor |  |  |  |  | 1
Equipment |  |  |  |  | 1
Installation |  |  |  |  | 1
7.1 Electric heat pump
7.1.1 Technical- and economic assumptions
Table 7-1: Technical- and economic assumptions for a electrical compression heat pumps for district heating [1]
Technology |  |  |  |  | Electrical compression heat pumps - district heating
2020
Energy/technical data
Heat generation capacity for one unit (MWheat) |  |  |  |  | 4
Total efficiency, net (%), name plate |  |  |  |  | N/A
Total eff., net (%), annual average, ambient heat source, no dev. in supply temp. |  |  |  |  | 360
Total eff., net (%), annual average, ambient heat source, reduced supply temp. |  |  |  |  | 400
Total eff., net (%), annual average, waste heat 20° C, reduced supply temp. |  |  |  |  | 500
Total eff., net (%), annual average, waste heat 40° C, reduced supply temp. |  |  |  |  | 900
Electricity consumption for pumps etc. (% of heat gen) |  |  |  |  | 2
Forced outage (%) |  |  |  |  | 0
Planned outage (weeks per year) |  |  |  |  | 0.5
Technical lifetime (years) |  |  |  |  | 25
Construction time (years) |  |  |  |  | 0.5
Space requirement (1000m2 per MWheat) |  |  |  |  | 0.02
Regulation ability
Primary regulation (% per 30 seconds) |  |  |  |  | 10
Secondary regulation (% per minute) |  |  |  |  | 20
Minimum load (% of full load) |  |  |  |  | 10
Warm start-up time (hours) |  |  |  |  | 0
Cold start-up time (hours) |  |  |  |  | 6
Environment
SO2 (g per GJ fuel) |  |  |  |  | 0
NOX (g per GJ fuel) |  |  |  |  | 0
CH4 (g per GJ fuel) |  |  |  |  | 0
N2O (g per GJ fuel) |  |  |  |  | 0
Financial data (in 2015€)
Nominal investment (M€ per MWheat) |  |  |  |  | 0.658
- of which equipment |  |  |  |  | 0.329
- of which installation |  |  |  |  | 0.329
Fixed O&M (€/MWheat/year) |  |  |  |  | 2000
Variable O&M (€/MWhheat) |  |  |  |  | 3.2
- of which is electricity costs (€/MWhheat) |  |  |  |  | 1.4
- of which is other O&M costs (€/MWhheat) |  |  |  |  | 1.8
Financial data (EUR) |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | 0.658
- of which equipment |  |  |  |  | 0.329
- of which installation |  |  |  |  | 0.329
Fixed O&M |  |  | EUR/MW/year |  | 2000
Variable O&M (€/MWh) |  |  | EUR/MWh |  | 3.2
- of which is electricity costs |  |  | EUR/MWh |  | 1.4
- of which is other O&M costs |  |  | EUR/MWh |  | 1.8
Electrical compression heat pumps - district heating |  |  | Unit |  | 0 | 0 | 0
Heat capacity |  |  | MW-h |  | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6
Nominal investment |  |  | MEUR/MW-h |  | 1.0689 | 0.91434 | 0.80479 | 0.72247 | 0.658 | 0.60593 | 0.56285 | 0.52652 | 0.49541
- of which equipment |  |  | MEUR/MW-h |  | 0.53446 | 0.45717 | 0.4024 | 0.36124 | 0.329 | 0.30296 | 0.28142 | 0.26326 | 0.2477
- of which installation |  |  | MEUR/MW-h |  | 0.53446 | 0.45717 | 0.4024 | 0.36124 | 0.329 | 0.30296 | 0.28142 | 0.26326 | 0.2477
7.2 Absorption heat pump
Figure 7-1: Arbsorption heat pump
7.2.1 Technical- and economic assumptions
Table 7-2: Technical- and economic assumptions for an absorption heat pumps for district heating [1]
Technology |  |  |  |  | Absorption heat pumps - district heating |  | Absorption heat pumps - single stage hot water |  | Absorption heat pumps - two stage hot water
[5 empty] | 2020 |  | 2020 |  | 2020
Energy/technical data
Heat generation capacity for one unit (MWheat) (excluding drive energy) |  |  |  |  | 12 |  | 5.3 |  | 15.8
Total efficiency, net (%), name plate |  |  |  |  | N/A |  | N/A |  | N/A
Total efficiency , net (%), annual average |  |  |  |  | 171 |  | 74 |  | 142
Electricity consumption for pumps etc. (% of heat gen) |  |  |  |  | 1 |  | 1 |  | 1
Forced outage (%) |  |  |  |  | 0 |  | 0 |  | 0
Planned outage (weeks per year) |  |  |  |  | 0 |  | 0 |  | 0
Technical lifetime (years) |  |  |  |  | 25 |  | 25 |  | 25
Construction time (years) |  |  |  |  | 0.5 |  | 0.5 |  | 0.5
Space requirement (1000m2 per MW) |  |  |  |  | 0.01 |  | 0.01 |  | 0.01
Regulation ability
Primary regulation (% per 30 seconds) |  |  |  |  | N/A |  | N/A |  | N/A
Secondary regulation (% per minute) |  |  |  |  | N/A |  | N/A |  | N/A
Minimum load (% of full load) |  |  |  |  | 10 |  | 10 |  | 10
Warm start-up time (hours) |  |  |  |  | 0 |  | 0 |  | 0
Cold start-up time (hours) |  |  |  |  | 0.5 |  | 0.5 |  | 0.5
Environment
SO2 (g per GJ fuel) |  |  |  |  | 0 |  | 0 |  | 0
NOX (g per GJ fuel) |  |  |  |  | 0 |  | 0 |  | 0
CH4 (g per GJ fuel) |  |  |  |  | 0 |  | 0 |  | 0
N2O (g per GJ fuel) |  |  |  |  | 0 |  | 0 |  | 0
Financial data
Nominal investment (M€ per MWheat excluding drive energy) |  |  |  |  | 0.564 |  | 0.17113 |  | 0.22321
- of which equipment |  |  |  |  | 0.282 |  | 0.069196 |  | 0.088542
- of which installation |  |  |  |  | 0.282 |  | 0.10193 |  | 0.13467
Fixed O&M (€/MWheat/year) |  |  |  |  | 2000 |  | --- |  | ---
Variable O&M (€/MWhheat) |  |  |  |  | 0.982 |  | 14.881 |  | 22.3214
- of which is electricity costs (€/MWhheat) |  |  |  |  | 0.7 |  | --- |  | ---
- of which is other O&M costs (€/MWhheat) |  |  |  |  | 0.282 |  | 14.881 |  | 22.3214
Financial data (EUR) |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | 0.564 |  | 0.17113 |  | 0.22321
- of which equipment |  |  |  |  | 0.282 |  | 0.069196 |  | 0.088542
- of which installation |  |  |  |  | 0.282 |  | 0.10193 |  | 0.13467
Fixed O&M |  |  | EUR/MW/year |  | 2000 |  | #VALUE! |  | #VALUE!
Variable O&M (€/MWh) |  |  | EUR/MWh |  | 0.982 |  | 14.881 |  | 22.3214
- of which is electricity costs |  |  | EUR/MWh |  | 0.7 |  | #VALUE! |  | #VALUE!
- of which is other O&M costs |  |  | EUR/MWh |  | 0.282 |  | 14.881 |  | 22.3214
Absorption heat pumps - district heating |  |  | Unit |  | Absorption heat pumps - district heating | Absorption heat pumps - single stage hot water | Absorption heat pumps - two stage hot water
Heat capacity |  |  | MW-h |  | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
Nominal investment |  |  | MEUR/MW-h |  | 0.64078 | 0.59942 | 0.564 | 0.53327 | 0.50631 | 0.48244 | 0.46113 | 0.44197 | 0.42463
- of which equipment |  |  | MEUR/MW-h |  | 0.32039 | 0.29971 | 0.282 | 0.26663 | 0.25315 | 0.24122 | 0.23056 | 0.22098 | 0.21232
- of which installation |  |  | MEUR/MW-h |  | 0.32039 | 0.29971 | 0.282 | 0.26663 | 0.25315 | 0.24122 | 0.23056 | 0.22098 | 0.21232
Table 7-3: Absorption Chiller Performance Characteristics (typical values for water/lithium bromide chillers) [13]
Description |  | System | bar: Absorption heat pumps - district heating 10 to Absorption heat pumps - two stage hot water 13
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7
Design |  | System 1: Single stage; System 4: Two stage
Heat Source |  | System 1: Hot Water; System 3: Steam (low pressure); System 4: Steam (high pressure); System 6: Exhaust Fired
Nominal Cooling Capacity (tons) |  | 50 | 440 | 1320 | 330 | 1320 | 330 | 1000
Thermal Energy Input
Hot Water Inlet Temp (°F) |  | 190 | 208 | n/a | n/a | n/a | n/a | n/a
Hot Water Outlet Temp (°F) |  | 181 | 190 | n/a | n/a | n/a | n/a | n/a
Steam Pressure (psig) |  | n/a | n/a | 14.5 | 116 | 116 | n/a | n/a
Exhaust Gas Temperature (°F) |  | n/a | n/a | n/a | n/a | n/a | 530 | 850
Heat Required (MMBtu/hr)2 |  | 0.85 | 7.1 | 20.1 | 2.8 | 11.2 | 2.9 | 8.7
Energy Output (chilled water)
Inlet Temperature (°F) |  | System 1: 54
Outlet Temperature (°F) |  | System 1: 44
Cooling COP (full load) |  | 0.7 | 0.74 | 0.79 | 1.42 | 1.42 | 1.35 | 1.38
Note: Performance characteristics are based on multiple sources, including vendor data and discussions with industry experts. The characteristics are intended to illustrate typical absorption chillers, and are not intended to represent performance of specific products. 2 For the hot water and steam examples, the boiler efficiency is not considered in the calculations.
Table 7-4: Absorption Chiller Capital and O&M Costs (typical values for water/lithium bromide chillers) [13]
Description |  | System 1: System
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7
Design |  | System 1: Single stage; System 4: Two stage
Heat Source |  | System 1: Hot Water; System 3: Steam (low pressure); System 4: Steam (high pressure); System 6: Exhaust Fired
Nominal Cooling Capacity (tons) |  | 50 | 440 | 1320 | 330 | 1320 | 330 | 1000
Equipment Cost ($/ton) |  | 2010 | 930 | 820 | 1190 | 1000 | 1330 | 930
Construction and Installation ($/ton) |  | 3990 | 1370 | 980 | 1810 | 1200 | 1970 | 1070
Installed Cost ($/ton) |  | 6000 | 2300 | 1800 | 3000 | 2200 | 3300 | 2000
O&M Costs (¢ / ton-hr) |  | 0.6 | 0.2 | 0.1 | 0.3 | 0.1 | 0.3 | 0.1
Note: Costs are based on multiple sources, including vendor data and discussions with industry experts. The values shown are composite results, and are not intended to represent a specific product.
7.3 Electric chiller
Figure 7-2: Electric chiller and air coolers
7.3.1 Technical- and economic assumptions
Table 7-5: Cost of air coolers and electric chiller [14]
Reference |  | System 1: Rambøll; System 5: Reference; System 7: Rambøll
Cost |  | System 1: m€/MW-h; System 5: Cost; System 7: mEUR/MW-h
Air (dry) coolers |  | System 1: 0.3; System 5: Air (dry) coolers; System 7: 0.3
Electric chiller |  | System 1: 0.4; System 5: Electric chiller; System 7: 0.4
7.4 New technology 1
7.4.1 Technical and economic assumptions
7.5 New technology 2
7.5.1 Technical and economic assumptions
7.6 Heat pump technology output
Technology | Reference | Electric capacity | Heat capacity | Solar thermal size | Storage size | Fuel | Voltage connection level | Full load hours |  |  | Investment (el) (eqiupment) | Investment (el) (installation) | Investment (heat) (equipment)
|  | MW-e | MW-h | m2 panel | m3 storage |  |  | Black | Blue | Green | mil. EUR/MW-el | mil. EUR/MW-el | mil. EUR/MW-heat
Electric heat pump | [1] | --- | 4 | --- | --- | Electricity | High voltage level | 3000 | 3000 | 3000 | --- | --- | 0.33
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Technology | Investment (heat) (installation) | Investment (solar) | Investment (storage) | Fixed O&M (el) | Fixed O&M (heat) | Fixed O&M (solar) | Fixed O&M (storage) | Var. O&M (el) | Var. O&M (heat) | Lifetime | CV | CB | Electric efficiency CHP
| mil. EUR/MW-heat | EUR/m2 panel | EUR/m3 storage | EUR/MW-el/year | EUR/MW-heat/year | EUR/m2 panel/year | EUR/m3 storage/year | EUR/MWh-el | EUR/MWh-heat | year |  |  | MW-el/MW-fuel
Electric heat pump | 0.33 | --- | --- | --- | 2000 | --- | --- | --- | 3.2 | 25 | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Technology | Heat efficiency CHP | Electric efficiency condensing | Heat efficiency | CO2 capture rate (amount of emission) | SO2 (degree of desulphuring) | Emission factor SO2 | Emission factor NOX | Emission factor CH4 | Emission factor N2O | Emission factor PM2.5
| MW-heat/MW-fuel | MW-el/MW-fuel | MW-heat/MW-fuel | % | % | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f
Electric heat pump | --- | --- | 3.6 | 0% | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
The electric heat pump is a key technology in the low carbon energy system, as it can integrate three of the energy carriers, electricity, DH and DC.
Moreover, in the general concept the heat pump can also operate as a heat only heat pump, which waste the cooling (e.g. ground source heat pumps) or as a cooling-only heat pump, which waste the heat (e.g. chiller).
As the technologies for these three types of heat pumps are similar we include them all in this category in order to make comparison, e.g. additional cost of generating cold from a ground source heat pump or additional cost of generating heat from an upgraded chiller.
Also for comparison we include absorption heat pumps in this category, both for cooling only and for combined heating and cooling.
As the operation and cost of generating heat and cold form heat pumps as well as the value of the generated heat and cold depends on the market prices for power heat and cold, the performance of heat pumps is analysed in the energy system analysis.
Heat pumps employ the same technology as refrigerators, moving heat from a low-temperature level to a higher temperature level. Heat pumps draw heat from a heat source (input heat) and convert the heat to a higher temperature (output heat) through a closed process; either compression type heat pumps (using electricity) or absorption heat pumps (using heat; e.g. steam, hot water or oil).
An important point regarding heat pumps is the ability to “produce” both heating and cooling. Hence, the “product” of a heat pump can be both heating and cooling – and at the same time.
When applied with the primary purpose of cooling, the cooling demand defines the capacity. When installed for cooling the heat pump will typically be the only cooling source, whereas when installed for heating it will in many cases be in combination with other sources that can provide the heat energy (e.g. at a district heating plant). However, the primary purpose of the heat pumps in the technology catalogue is heating. In this chapter the unit MW is referring to the heat output (also MJ/s) unless otherwise noted.
Heat pumps are utilized for industrial processes, individual space heating and district heat production.
For compression heat pumps, the practical heat output is usually 3 to 5 times (the coefficient of performance (COP)) the drive energy. This factor depends on the efficiency of the specific heat pump, the temperature of the heat source and the heat sink and the temperature difference between heat source and heat sink.
In absorption heat pumps, high temperature heat is used to regenerate a refrigerant that can evaporate at a low temperature level and hereby utilize low grade energy. Energy from both drive heat and the low temperature heat source is delivered at a temperature in between.
In theory 1 kJ of heat can regenerate around 1 kJ of refrigerant meaning that an absorption heat pump has a theoretical maximum COP of around 2. Due to losses in the system the practical COP is around 1.7. For absorption heat pumps, COP is not affected by temperature levels. Certain temperature differences is required to have the process going, but as long as these are met the COP will be around 1.7 and not affected by further temperature increase of the drive energy.
A chiller is a machine that removes heat from a liquid via a vapor-compression or absorption refrigeration cycle. This liquid can then be circulated through a heat exchanger to cool equipment, or another process stream (such as air or process water). As a necessary by-product, refrigeration creates waste heat that must be exhausted to ambience, or for greater efficiency, recovered for heating purposes. Chilled water is used to cool and dehumidify air in mid- to large-size commercial, industrial, and institutional facilities. Water chillers can be water-cooled, air-cooled, or evaporatively cooled. Water-cooled systems can provide efficiency and environmental impact advantages over air-cooled systems.
Important specifications to consider when searching for industrial chillers include the total life cycle cost, the power source, chiller IP rating, chiller cooling capacity, evaporator capacity, evaporator material, evaporator type, condenser material, condenser capacity, ambient temperature, motor fan type, noise level, internal piping materials, number of compressors, type of compressor, number of fridge circuits, coolant requirements, fluid discharge temperature, and COP (the ratio between the cooling capacity in RT to the energy consumed by the whole chiller in KW). For medium to large chillers this should range from 3.5 to 7.0, with higher values meaning higher efficiency. Chiller efficiency is often specified in kilowatts per refrigeration ton (kW/RT). Process pump specifications that are important to consider include the process flow, process pressure, pump material, elastomer and mechanical shaft seal material, motor voltage, motor electrical class, motor IP rating and pump rating. If the cold water temperature is lower than −5 °C, then a special pump needs to be used to be able to pump the high concentrations of ethylene glycol. Other important specifications include the internal water tank size and materials and full load current. Control panel features that should be considered when selecting between industrial chillers include the local control panel, remote control panel, fault indicators, temperature indicators, and pressure indicators.
Additional features include emergency alarms, hot gas bypass, city water switchover, and casters. Demountable chillers are also an option for deployment in remote areas and where the conditions may be hot and dusty.
The remaining technical and economic assumptions can be taken from the description of the electrical heat pump.

## 8. Renewable energy
Back to user guide
8. Renewable energy
List of contents
8. Renewable energy
8.1 Solar heating
8.2 High temperature solar heating (no data)
8.3 Solar PV
8.4 Wind turbine
8.5 Deep geothermal
8.6 Biogas plant
8.7 Solar PVT
8.8 Fuel cells
8.9 New technology 1
8.10 New technology 2
8.11 Renewable energy technology output
Assumptions applied (selected in 3.1 LCOE results)
Discount rate |  |  |  |  | 5% | %
Calculation period |  |  |  |  | 1
Start year of calculation |  |  |  |  | 2022
Electricity price development |  |  |  |  | Green
Expected solar thermal production |  |  |  |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  |  |  |  | Sustainable development scenario
Country |  |  |  |  | EU
Currency abbreviation |  |  |  |  | EUR
Currency factor |  |  |  |  | 1
Equipment |  |  |  |  | 1
Installation |  |  |  |  | 1
8.1 Solar heating
Figure 8-1: Solar heating
8.1.1 Technical- and economic assumptions
Table 8-1: Production from 10,000 m2 DH solar heating plant, field [14]
Temperatures in panels |  |  |  | Low DH Temperature |  |  | High DH Temperature
Climate Zone |  |  |  | Mild | Warm | Hot | Mild | Warm | Hot
Annual solar radiation |  |  | kWh/m2 panel | 1150 | 1350 | 2300 | 1150 | 1350 | 2300
Average outdoor temperature |  |  | °C | 9 | 13 | 16 | 9 | 13 | 16
Supply temperature |  |  | °C | 60 | 60 | 90 | 90 | 90 | 90
Return temperature |  |  | °C | 40 | 40 | 40 | 70 | 70 | 70
Expected production |  |  | kWh/m2 panel | 550 | 850 | 1500 | 450 | 700 | 1300
Investment in plant 10,000 m2 |  |  | EUR/m2 panel | 200 | 200 | 200 | 200 | 200 | 200
Annual O&M cost 10,000 m2 |  |  | EUR/m2 panel | 2 | 2 | 2 | 2 | 2 | 2
Ivestment in plant 10,000 m2 |  |  | EUR/MWh/a | 364 | 235 | 133 | 444 | 286 | 154
Capital costs, 30 year 3% |  |  | EUR/MWh | 19 | 12 | 7 | 23 | 15 | 8
Annual operation costs |  |  | EUR/MWh | 4 | 2 | 1 | 4 | 3 | 2
Average production cost |  |  | EUR/MWh | 22 | 14 | 8 | 27 | 17 | 9
Investment in plant 10,000 m2 |  |  | EUR/m2 panel | 200 | 200 | 200 | 200 | 200 | 200
Annual O&M cost 10,000 m2 |  |  | EUR/m2 panel | 2 | 2 | 2 | 2 | 2 | 2
Ivestment in plant 10,000 m2 |  |  | EUR/MWh/a | 364 | 235 | 133 | 444 | 286 | 154
Capital costs, 30 year 3% |  |  | EUR/MWh | 19 | 12 | 7 | 23 | 15 | 8
Annual operation costs |  |  | EUR/MWh | 4 | 2 | 1 | 4 | 3 | 2
Average production cost |  |  | EUR/MWh | 22 | 14 | 8 | 27 | 17 | 9
Table 8-2: Economy of scale for solar heating, warm climate zone, low DH temperature [14]
Typical heat consumer |  |  |  | Building, roof top |  |  | District Heating, field
Size of consumer |  |  |  | Small | Medium | Large | Small | Medium | Large
Solar panel area |  |  | m2 | 5 | 200 | 2000 | 2000 | 10000 | 20000
Expected production |  |  | kWh/m2 panel | 750 | 800 | 850 | 850 | 850 | 850
Total annual investment |  |  | EUR/m2 panel | 1000 | 450 | 400 | 380 | 200 | 190
Annual O&M cost |  |  | EUR/m2 panel | 9 | 7 | 5 | 4 | 2 | 2
Investment in plant |  |  | EUR/MWh/a | 1333 | 563 | 471 | 447 | 235 | 224
Capital costs, 30 year 3% |  |  | EUR/MWh | 68 | 29 | 24 | 23 | 12 | 11
Annual operation costs |  |  | EUR/MWh | 12 | 9 | 6 | 5 | 2 | 2
Average production cost |  |  | EUR/MWh | 80 | 37 | 30 | 28 | 14 | 13
Investment in plant 10,000 m2 |  |  | EUR/m2 panel | 1000 | 450 | 400 | 380 | 200 | 190
Annual O&M cost 10,000 m2 |  |  | EUR/m2 panel | 9 | 7 | 5 | 4 | 2 | 2
Ivestment in plant 10,000 m2 |  |  | EUR/MWh/a | 1333 | 563 | 471 | 447 | 235 | 224
Capital costs, 30 year 3% |  |  | EUR/MWh | 68 | 29 | 24 | 23 | 12 | 11
Annual operation costs |  |  | EUR/MWh | 12 | 9 | 6 | 5 | 2 | 2
Average production cost |  |  | EUR/MWh | 80 | 37 | 30 | 28 | 14 | 13
Table 8-3: Technical- and economic assumptions for a solar district heating plant [1]
Technology |  |  |  |  | Solar District Heating Plant
2020
Energy/technical data
Typical plant size (collector area), m2 |  |  |  |  | 13000
Collector input, kWh/m2/year |  |  |  |  | 1046
Collector output, kWh/m2/year |  |  |  |  | 472.955
Total efficiency , net (%), annual average |  |  |  |  | 0.45
Auxilary electricity consumption (share of heat gen.) |  |  |  |  | 0.003
Forced outage (%) |  |  |  |  | 0.005
Technical lifetime (years) |  |  |  |  | 30
Construction time (years) |  |  |  |  | 0.25
Space requirement (1000m2 per MWh/year) |  |  |  |  | 6.3
Regulation ability
Primary regulation (% per 30 seconds) |  |  |  |  | N/A
Secondary regulation (% per minute) |  |  |  |  | N/A
Minimum load (% of full load) |  |  |  |  | N/A
Warm start-up time (hours) |  |  |  |  | N/A
Cold start-up time (hours) |  |  |  |  | N/A
Environment
SO2 (g per GJ fuel) |  |  |  |  | 0
NOX (g per GJ fuel) |  |  |  |  | 0
CH4 (g per GJ fuel) |  |  |  |  | 0
N2O (g per GJ fuel) |  |  |  |  | 0
Financial data
Investment cost of total solar systems excluding diurnal heat storage, €/MWhoutput/year |  |  |  |  | 395.3865
- of which is equipment |  |  |  |  | 336.0785
- of which is installation |  |  |  |  | 59.308
Investment cost of diurnal heat storage, €/MWhoutput/year |  |  |  |  | 57
Total investment cost of total solar system including diurnal heat storage, €/MWhoutput/year |  |  |  |  | 452.3865
Fixed O&M €/(MWhoutput/year)/year |  |  |  |  | 0.09
Variable O&M €/MWhoutput |  |  |  |  | 0.21
- of which is electricity costs, €/MWhoutput |  |  |  |  | 0.21
- of which is other O&M costs, €/MWhoutput |  |  |  |  | 0
Technology specific data
Investment cost of total solar systems excluding diurnal heat storage, €/m2 (collector area) |  |  |  |  | 187
Fixed O&M, €/m2/year (collector area) |  |  |  |  | 0.042566
Financial data
Investment cost of total solar systems excluding diurnal heat storage, €/MWhoutput/year |  |  |  |  | 395.3865
- of which is equipment |  |  |  |  | 336.0785
- of which is installation |  |  |  |  | 59.308
Investment cost of diurnal heat storage, €/MWhoutput/year |  |  |  |  | 57
Total investment cost of total solar system including diurnal heat storage, €/MWhoutput/year |  |  |  |  | 452.3865
Fixed O&M €/(MWhoutput/year)/year |  |  |  |  | 0.09
Variable O&M €/MWhoutput |  |  |  |  | 0.21
- of which is electricity costs, €/MWhoutput |  |  |  |  | 0.21
- of which is other O&M costs, €/MWhoutput |  |  |  |  | 0
Technology specific data
Investment cost of total solar systems excluding diurnal heat storage, €/m2 (collector area) |  |  |  |  | 187
Fixed O&M, €/m2/year (collector area) |  |  |  |  | 0.042566
Solar District Heating Plant |  |  | Unit |  | #REF! | #REF! | #REF!
Solar panel area |  |  | m2 |  | 5 | 200 | 2000 | 2000 | 10000 | 20000
Average production cost |  |  | EUR/MWh |  | 80 | 37 | 30 | 28 | 14 | 13
8.2 High temperature solar heating (no data)
8.2.1 Technical- and economic assumptions
8.3 Solar PV
8.3.1 Technical- and economic assumptions
Table 8-4: Technical- and economic assumptions for a small residential photovoltaics system [1]
Technology |  |  |  |  | Photovoltaics: SMALL residential systems |  | Photovoltaics: MEDIUM sized commercial systems |  | Photovoltaics: LARGE scale utility systems
[5 empty] | 2020 |  | 2020 |  | 2020
Input
Global horizontal irradiance (kWh/m2/y) |  |  |  |  | 1068 |  | 1068 |  | 1068
Energy/technical data
Typical capacity for one installation (kW)(plant capacity) |  |  |  |  | 6 |  | 100 |  | 4000
Typical peak capacity for one installation at STC (kWp) |  |  |  |  | 6.3 |  | 110 |  | 5400
Energy/technical data - system design
DC/AC sizing factor (Wp/W) |  |  |  |  | 1.05 |  | 1.1 |  | 1.35
Transposition Factor for fixed tilt system |  |  |  |  | 1.1 |  | 1.1 |  | 1.15
Incident Angle Modifier Loss (%) |  |  |  |  | 0.025 |  | 0.025 |  | 0.025
PV systems losses and non-STC corrections (%) |  |  |  |  | 0.12 |  | 0.09 |  | 0.09
Inverter loss (%) |  |  |  |  | 0.015 |  | 0.015 |  | 0.026
AC grid losses (%) |  |  |  |  | 0 |  | 0 |  | 0.01
PV module conversion efficiency (%) |  |  |  |  | 0.19 |  | 0.19 |  | 0.19
Availability (%) |  |  |  |  | 1 |  | 1 |  | 1
Technical lifetime of total system (years) |  |  |  |  | 35 |  | 35 |  | 35
Inverter lifetime (years) |  |  |  |  | 15 |  | 15 |  | 15
Output
Full load hours (kWh/kW) |  |  |  |  | 1042.5017 |  | 1129.3768 |  | 1420
Peak power full load hours (kWh/kWp) |  |  |  |  | 992.8587 |  | 1026.7062 |  | 1050
Financial data
PV module cost (2015-€/Wp) |  |  |  |  | 0.31188 |  | 0.28589 |  | 0.2599
Balance Of Plant cost (2015-€/Wp) |  |  |  |  | 0.76 |  | 0.44475 |  | 0.045924
Specific investment, total system (2015-€/Wp) |  |  |  |  | 1.07 |  | 0.73064 |  | 0.31072
Specific investment, total system (2015-M€/MW) |  |  |  |  | 1.1284 |  | 0.80371 |  | 0.61655
Fixed O&M (2015€/MWp/y) |  |  |  |  | 12800 |  | 10400 |  | 0.35086
Fixed O&M (2015€/MW/y) |  |  |  |  | 13440 |  | 11440 |  | 0.061997
Financial data |  |  | Unit
PV module cost |  |  | EUR/Wp |  | 0.31188 |  | 0.28589 |  | 0.2599
Balance Of Plant cost |  |  | EUR/Wp |  | 0.76 |  | 0.44475 |  | 0.045924
Specific investment, total system |  |  | MEUR/Wp |  | 1.07 |  | 0.73064 |  | 0.31072
Specific investment, total system |  |  | MEUR/MW |  | 1.1284 |  | 0.80371 |  | 0.61655
Fixed O&M |  |  | EUR/MWp |  | 12800 |  | 10400 |  | 0.35086
Fixed O&M |  |  | EUR/MW |  | 13440 |  | 11440 |  | 0.061997
Photovoltaics: MEDIUM sized commercial systems |  |  | Unit |  | Photovoltaics: SMALL residential systems | Photovoltaics: MEDIUM sized commercial systems | Photovoltaics: LARGE scale utility systems
Electric capacity |  |  | kW-e |  | 5 | 10 | 15 | 100 | 200 | 300 | 4000 | 5000 | 6000
Specific investment, total system |  |  | MEUR/MW-e |  | 0 | 0 | 0 | 0.80371 | 0.49474 | 0.37249 | 0 | 0 | 0
8.4 Wind turbine
8.4.1 Technical- and economic assumptions
Table 8-7: Technical- and economic assumptions for wind turbines [1]
Technology |  |  |  |  | On-shore wind turbine |  | Small wind turbines, grid connected (< 25 kW) |  | Large wind turbine off-shore |  | Large offshore wind turbine near-shore
[5 empty] | 2020 |  | 2020 |  | 2020 |  | 2020
Energy/technical data
Generating capacity for one unit (MW) |  |  |  |  | 4.2 |  | 0.025 |  | 10 |  | 10
Average annual full-load hours |  |  |  |  | 3400 |  | 1600 |  | 4500 |  | 4500
Forced outage (%) |  |  |  |  | 2.5% |  | 3% |  | 3% |  | 3%
Planned outage (%) |  |  |  |  | 0.3% |  | 0.3% |  | 0.3% |  | 0.3%
Technical lifetime (years) |  |  |  |  | 27 |  | 20 |  | 27 |  | 27
Construction time (years) |  |  |  |  | 1.5 |  | 1 |  | 2.5 |  | 2
Space requirement (1000m2/MW) |  |  |  |  | --- |  | 0.8 |  | 220 |  | 220
Regulation ability
Primary regulation (% per 30 seconds) |  |  |  |  | --- |  | --- |  | --- |  | ---
Secondary regulation (% per minute) |  |  |  |  | --- |  | --- |  | --- |  | ---
Financial data (in 2015€)
Nominal investment (M€/MW) |  |  |  |  | 1.12 |  | 3.8 |  | 2.13 |  | 1.75
- of which equipment |  |  |  |  | 0.71 |  | 3.42 |  | 0.79 |  | 0.67
- of which installation |  |  |  |  | 0.41 |  | 0.38 |  | 1.34 |  | 1.08
Fixed O&M (€/MW/year) |  |  |  |  | 14000 |  | 95000 |  | 40059 |  | 36053
Variable O&M (€/MWh) |  |  |  |  | 1.5 |  | --- |  | 3 |  | 2.67
Technology specific data
Rotor diameter |  |  |  |  | 130 |  | 8 |  | 190 |  | 190
Hub height |  |  |  |  | 85 |  | 18 |  | 115 |  | 115
Specific power (W/m2) |  |  |  |  | 316 |  | --- |  | 353 |  | 353
Average capacity factor |  |  |  |  | 39% |  | --- |  | 51% |  | 51%
Average availability (%) |  |  |  |  | 97% |  | --- |  | 97% |  | 97%
Specific area coverage (MW/km2) |  |  |  |  | --- |  | --- |  | 4.5 |  | 4.5
Financial data |  |  | Unit
Nominal investment |  |  | MEUR/MW |  | 1.12 |  | 3.8 |  | 2.13 |  | 1.75
- of which equipment |  |  | MEUR/MW |  | 0.71 |  | 3.42 |  | 0.79 |  | 0.67
- of which installation |  |  | MEUR/MW |  | 0.41 |  | 0.38 |  | 1.34 |  | 1.08
Fixed O&M |  |  | EUR/MW/year |  | 14000 |  | 95000 |  | 40059 |  | 36053
Variable O&M |  |  | EUR/MWh |  | 1.5 |  | #VALUE! |  | 3 |  | 2.67
Large offshore wind turbine near-shore |  |  | Unit |  | On-shore wind turbine | Small wind turbines, grid connected (< 25 kW) | Large wind turbine off-shore | Large offshore wind turbine near-shore
Electric capacity |  |  | MW-e |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Nominal investment |  |  | MEUR/MW-e |  | 5.399 | 4.0649 | 3.3235 | 2.8429 | 2.5023 | 2.2463 | 2.0459 | 1.8839 | 1.75
- of which equipment |  |  | MEUR/MW-e |  | 2.0671 | 1.5563 | 1.2724 | 1.0884 | 0.95801 | 0.86002 | 0.78327 | 0.72128 | 0.67
- of which installation |  |  | MEUR/MW-e |  | 3.332 | 2.5086 | 2.0511 | 1.7545 | 1.5443 | 1.3863 | 1.2626 | 1.1627 | 1.08
8.5 Deep geothermal
8.5.1 Technical- and economic assumptions
Table 8-11: Technical- and economic assumptions for a geothermal plant [1]
Technology |  |  |  |  | 2: Geothermal heat-only plant with steam-driven absorption heat pump; 4: Geothermal heat-only plant with steam-driven absorption heat pump, Denmark; 6: Geothermal heat-only plant with electric heat pump, Denmark
[5 empty] | 2020 |  | 2020 |  | 2020
Energy/technical data
Temperature of geothermal heat (degrees C)
Heat from geothermal source (%) |  |  |  |  | 2: 100; 4: 100; 6: 100
Steam demand, heat pump (%) |  |  |  |  | 2: 76; 4: 107.6923; 6: 17.3228
Heat generation capacity (%) |  |  |  |  | 2: 176; 4: 207.6923; 6: 117.1654
District heat forward temperature, winter (C) |  |  |  |  | 2: 80; 4: 80; 6: 85
Electricity consumption for pumps etc. (%) |  |  |  |  | 2: 8; 4: 4.6923; 6: 8.0315
Technical lifetime (years) |  |  |  |  | 2: 25; 4: 25; 6: 25
Construction time (years) |  |  |  |  | 2: 4-5; 4: 4-5; 6: 4-5
Financial data
Specific investment (M€ per MJ/s geothermal heat) |  |  |  |  | 2: 1.7622; 4: 1.9987; 6: 1.6
O&M excl. electricity consumption (€/year per MJ/s geothermal heat) |  |  |  |  | 2: 47000; 4: 49000; 6: 34000
Financial data |  |  | Unit
Specific investment |  |  | EUR/MW |  | 2: 1.7622; 4: 1.9987; 6: 1.6
O&M excl. electricity consumption |  |  | EUR/MW/year |  | 2: 47000; 4: 49000; 6: 34000
8.6 Biogas plant
Figure 8-2: Biogas plant
8.6.1 Technical- and economic assumptions
Table 8-14: Technical- and economic assumptions for a biogas plant (basic configuration) [1]
Technology |  |  |  |  | 2: Biogas plant (basic configuration)
2020
Energy/technical data
Typical capacity (tons/year input)
Typical total plant size (MW output) |  |  |  |  | 2: 8.6829
Inputs
Biomass (tons/year) |  |  |  |  | 2: 365000
Aux. electricity (% of output energy) |  |  |  |  | 2: 3.8196
Aux. electricity (kWh/ton input) |  |  |  |  | 2: 7.9596
Aux. process heat (% of output energy) |  |  |  |  | 2: 8.9256
Aux. process heat (kWh/ton input)) |  |  |  |  | 2: 18.6
Outputs
Biogas (%) |  |  |  |  | 2: 100
Biogas (GJ/ton input) |  |  |  |  | 2: 0.7502
Biogas production, (MJ/S heating value)
Forced outage (%) |  |  |  |  | 2: 0
Planned outage (days per year) |  |  |  |  | 2: 10
Technical lifetime (years) |  |  |  |  | 2: 20
Construction time (years) | bar: 2
Financial data
Specific investment (mio €/MW output) |  |  |  |  | 2: 1.7107
- of which equipment | bar: 2
- of which installation | bar: 2
Total O&M (€/MW/year) |  |  |  |  | 2: 194715.0214
Total O&M (€/(ton input/year)) |  |  |  |  | 2: 4.632
- of which O&M, excl el. and heat (€/(ton input/year)) |  |  |  |  | 2: 3.6728
- of which electricity (€/(ton input/year)) |  |  |  |  | 2: 0.54922
- of which heat (€/(ton input/year)) |  |  |  |  | 2: 0.41
Technology Specific data
Methane emission (Nm3 CH4/ton input/year) |  |  |  |  | 2: 0.42
Financial data |  |  | Unit
Specific investment |  |  | MEUR/MW |  | 2: 1.7107
- of which equipment |  |  | MEUR/MW |  | 2: #VALUE!
- of which installation |  |  | MEUR/MW |  | 2: #VALUE!
Total O&M |  |  | EUR/MW/year |  | 2: 194715.0214
Total O&M |  |  | EUR/ton input/year |  | 2: 4.632
- of which O&M, excl el. and heat |  |  | EUR/ton input/year |  | 2: 3.6728
- of which electricity |  |  | EUR/ton input/year |  | 2: 0.54922
- of which heat |  |  | EUR/ton input/year |  | 2: 0.41
8.7 Solar PVT
Figure 8-3: left: © IfE GmbH, Hochschule Amberg-Weiden / right: ©Oberfeld, Institut für Solartechnik SPF, for 'energie schweiz'
8.7.1 Technical- and economic assumptions
Table 8-15: Solar PV panel products description
Product Name |  |  | Capacity(W) | Size (m2) | 2: Material; 4: Company; 6: Website; 9: Type
2Power HM 260 |  |  | 260 | 1.6 | 2: mono cSi; 4: PA-ID Process (GE); 6: http://www.2power-hybrid.com/de/; 9: flat plate water, insulation
3F Solar One Hybrid - kollektor |  |  | 265 | 1.6 | 2: mono cSi; 4: 3F Solar (AT); 6: http://www.3f-solar.at; 9: flat plate water, insulation
Alius Solar Volthera |  |  | 260-275 | 1.6 | 2: Poly/mono cSi; 4: Alius Solar (NL); 6: http://aliusenergy.nl; 9: flat plate water, insulation
3S HYBRID 240-900 |  |  | 285 | 1.6 | 2: mono cSi; 4: MeyerBurger (CH); 6: http://www.meyerburger.com; 9: flat plate water
Building Energy Hybride PV/T 2 |  |  | 250 | 1.6 | 2: Poly/mono cSi; 4: Building Energy (BE); 6: http://buildingenergy.be; 9: flat plate water, with/without insulation
Optisolar PVT-Thermodule 2.0 |  |  |  |  | 4: Optisolar PVT (NL); 6: http://www.optisolarpvt.nl; 9: flat plate water, insulation
Solarus Power Collector |  |  | 250 | 2.5 | 2: cSi; 4: Solarus (NL/SE); 6: http://www.solarus.com; 9: concentarting sunlight
Solarduct PV/T |  |  | 100 |  | 4: Conserval Engineering; 6: http://solarwall.com/en/home.php; 9: ventilated PV modeule with heat recovery system for ventilation system
8.8 Fuel cells
8.8.1 Technical and economic assumptions
Table 8-16: Technical- and economic assumptions for fuel cells [1]
Technology |  |  |  |  | 2: SOEC (Solid Oxide Electrolyzer Cell); 4: LT PEM EC (Low Temperature Proton Exchange Membrane Electrolyser Cell )
[5 empty] | 2020 |  | 2020
Energy/technical data
Typical total plant size (MW input) |  |  |  |  | 2: 1; 4: 10
Inputs
A) Electricity input (% total size) |  |  |  |  | 2: 85; 4: 100
B) Heat input (% total size) |  |  |  |  | 2: 15; 4: 0
Outputs
A) Hydrogen output (% total size) |  |  |  |  | 2: 76; 4: 58
B) Heat output (% total size) |  |  |  |  | 2: 3; 4: 0
Forced outage (%)
Planned outage (weeks per year)
Technical lifetime (years) |  |  |  |  | 2: 20; 4: 15
Construction time (years) |  |  |  |  | 2: 0.5; 4: 0.5
Financial data
Specific investment (M€-2015 per MW input) |  |  |  |  | 2: 2.2; 4: 1.1
- hereof equipment (%) |  |  |  |  | 2: 0.99; 4: 0.825
- hereof installation (%) |  |  |  |  | 2: 1.21; 4: 0.275
Fixed O&M (€-2015 per MW input per year) |  |  |  |  | 2: 66000; 4: 55000
Variable O&M (€-2015 per MWh input) |  |  |  |  | 2: 0; 4: 0
Technology specific data
Operating temperature (degC) |  |  |  |  | 2: 750; 4: 80
Stack lifetime (years) |  |  |  |  | 2: 5; 4: -
Ramp up time, linear to full load (minutes) |  |  |  |  | 2: 1; 4: 0.03
Ramp down time, linear to full load (minutes) |  |  |  |  | 2: 1; 4: 0.02
Start-up time (minutes) |  |  |  |  | 2: 60; 4: 0.5
Financial data |  |  | Unit
Specific investment |  |  | MEUR/MW |  | 2: 2.2; 4: 1.1
- of which equipment |  |  | MEUR/MW |  | 2: 0.99; 4: 0.825
- of which installation |  |  | MEUR/MW |  | 2: 1.21; 4: 0.275
Fixed O&M |  |  | EUR/MW/year |  | 2: 66000; 4: 55000
Variable O&M |  |  | EUR/MWh |  | 2: 0; 4: 0
8.9 New technology 1
8.9.1 Technical and economic assumptions
8.10 New technology 2
8.10.1 Technical and economic assumptions
8.11 Renewable energy technology output
Technology | Reference | Electric capacity | Heat capacity | Solar thermal size | Storage size | Fuel | Voltage connection level | Full load hours |  |  | Investment (el) (eqiupment) | Investment (el) (installation) | Investment (heat) (equipment)
|  | MW-e | MW-h | m2 panel | m3 storage |  |  | Black | Blue | Green | mil. EUR/MW-el | mil. EUR/MW-el | mil. EUR/MW-heat
Geothermal | [1] | --- | 10 | --- | --- | Electricity | High voltage level | 5000 | 5000 | 5000 | --- | --- | 1.95
Solar PV | [1] | 10 | --- | --- | --- | Solar PV | --- | 1050 | 1050 | 1050 | 0.62 | --- | ---
Solar - small | Ramboll | --- | --- | 2000 | --- | Solar | --- | --- | --- | --- | --- | --- | ---
Solar - medium | Ramboll | --- | --- | 10000 | --- | Solar | --- | --- | --- | --- | --- | --- | ---
Solar - large | Ramboll | --- | --- | 20000 | --- | Solar | --- | --- | --- | --- | --- | --- | ---
Large onshore wind turbine | [1] | 4.2 | --- | --- | --- | --- | --- | 3400 | 3400 | 3400 | 0.71 | 0.41 | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Technology | Investment (heat) (installation) | Investment (solar) | Investment (storage) | Fixed O&M (el) | Fixed O&M (heat) | Fixed O&M (solar) | Fixed O&M (storage) | Var. O&M (el) | Var. O&M (heat) | Lifetime | CV | CB | Electric efficiency CHP
| mil. EUR/MW-heat | EUR/m2 panel | EUR/m3 storage | EUR/MW-el/year | EUR/MW-heat/year | EUR/m2 panel/year | EUR/m3 storage/year | EUR/MWh-el | EUR/MWh-heat | year |  |  | MW-el/MW-fuel
Geothermal | 0.65 | --- | --- | --- | 20000 | --- | --- | --- | 3.5 | 25 | --- | --- | ---
Solar PV | --- | --- | --- | 8100 | --- | --- | --- | --- | --- | 20 | --- | --- | ---
Solar - small | --- | 380 | --- | --- | --- | 4 | --- | --- | --- | 30 | --- | --- | ---
Solar - medium | --- | 200 | --- | --- | --- | 2 | --- | --- | --- | 30 | --- | --- | ---
Solar - large | --- | 190 | --- | --- | --- | 2 | --- | --- | --- | 30 | --- | --- | ---
Large onshore wind turbine | --- | --- | --- | 14000 | --- | --- | --- | 1.5 | --- | 27 | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Technology | Heat efficiency CHP | Electric efficiency condensing | Heat efficiency | CO2 capture rate (amount of emission) | SO2 (degree of desulphuring) | Emission factor SO2 | Emission factor NOX | Emission factor CH4 | Emission factor N2O | Emission factor PM2.5
| MW-heat/MW-fuel | MW-el/MW-fuel | MW-heat/MW-fuel | % | % | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f
Geothermal | --- | --- | 3.6 | 0% | --- | --- | --- | --- | --- | ---
Solar PV | --- | --- | --- | 0% | --- | --- | --- | --- | --- | ---
Solar - small | --- | --- | --- | 0 | --- | --- | --- | --- | --- | ---
Solar - medium | --- | --- | --- | 0 | --- | --- | --- | --- | --- | ---
Solar - large | --- | --- | --- | 0 | --- | --- | --- | --- | --- | ---
Large onshore wind turbine | --- | --- | --- | 0 | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
--- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
In this category we include all relevant renewable energy soruces, except biomass fuels, which are incorporated in the boiler and CHP categories.
As the world is looking for affordable renewable energy this category is important and we will compare cost of generating energy, in the form of electricity, gas or heat taking into account the economy of scale.
Solar water heating is a natural and simpel way to utilize the energy from the sun to provide hot water for heating and hot tap water and the technology is simple.
Due to economy of scale and mass producion, it is in particular cost effective to supply large heat demand with large plants mounted on the ground.
Due to the daily fluctuations, it can be necessary to level the production with a heat storage tank in order to cover the summer load, and more storage capacity is necessary in order to cover a larter share of the heat demand. That was the driver for developing the heat storage pit .
The anti freeze liquid in the plant is seperated from the district heating and the storages with heat exchangers.
The world record on large-scale solar water heating is almost doubled every year. Three recent world records:
20.000 m2 Marstal DH in Denmark, the company who tested the concept
44.000 m2 Cobber mining industry in Chille, 80% of hot water production to the process
70.000 m2 Vojens DH, 50% of the annual heat production in combination with a heat storage pit
156.000 m2 Silkeborg DH, 20% of the annual heat production in combination with gas CC and heat pump
The solar panels absorbs allmost all the solar energy, but the net production is the difference between the absorbed solar energy and the heat losses.
The production is not only depending on the solar radiation. It also depends on the ambient temperature and the temperature of the DH water.
The table on top shows that there can even be a factor betwen the production in a hot climate like in Chile and in a mild clima like Northern Europe.
The table below illustrates the economy of scale showing that solar heat from a small roof-top plant is 6 times more expensive than solar heat from a large-scale plant.
In case only part of heat is utilized from the small plant, due to lack of demand in vacation etc. the difference can be even larger.
PVT collector is a solar energy device that uses PV as a thermal absorber and produces both electrical and thermal energy. A wide variety of PVT module configurations exist. Several previous market surveys have been published and include a classification. The attention for PVT systems and the number of suppliers is steadily growing.
On the one hand PVT collectors are used in the well-known fields of application of solar thermal energy such as domestic hot water heating, domestic hot water heating with heating support and supply of warm air eg for heating schwimming halls. However, non-covered liquid-cooled PVT collectors are also used in heat pump systems where their low-temperature heat is primarily used at the source side of the heat pump. In particular, mention should be made of the use for the regeneration of geothermal probes. First demonstration projects with PVT ("Hybrid") collectors have been realized since around 2010. One example is the swimming hall of Kümmersbruck with 120 m² collector field. There are quite a few projects in Switzerland, where water PVT is increasingly used to regenerate geothermal heat sources and support the heat pump. Examples range from single family homes to building compounds with hunderts of appartments.
Main characteristics: Renewable heat and electricity generation
Technology interdepencies: Similar to sole solar thermal and photovoltaic installations
Advantages: Compactness and yields, good combination of PVT with heat pump Disadvantages: Complexity of system design and installation, difficulties in optimization, low economic profitability and high investment costs
Recommended for: Buildings with a high heat demand throughout the year, e.g. hotels, dormitories, hospitals,pools, residential buildings.
- Electric performance can be higher or lower than that of pure PV, depending on operationg conditions (temperature)
- Thermal performance is similar to that of solar collectors
- Costs are higher than for usual PV systems. As first approximation one could use the sum of corresponding PV and solar thermal fields costs.
- Installation costs depend on availability of experienced experts, usually higher than for single purpose, can reach 40% of total costs
Since there are so many technological solutions, costs vary. Costs are expected to fall, as the technology is still strongly developing.
Monitoring data from realized facilities show that a 5% rise in electric efficiency can be reached, and a COP increase by 1,5 (if heat is used as source for heat pump)
References:
https://www.seac.cc/wp-content/uploads/2018/01/SEAC_PVTinSHaPeBenchmark_final.pdf
http://www.bine.info/publikationen/publikation/solardaecher-doppelt-nutzen/
https://www.solarthermalworld.org/sites/gstec/files/news/file/2017-06-01/pvt_switzerland_final.pdf
https://www.ise.fraunhofer.de/en/research-projects/pvtgen2.html
http://task60.iea-shc.org/
©Institut für Solartechnik SPF , for 'energie schweiz'
A solar cell is a semiconductor component that generates electricity when exposed to light. For practical reasons several solar cells are typically interconnected and laminated to (or deposited on) a glass pane in order to obtain a mechanical ridged and weathering protected solar module. The photovoltaic (PV) modules are typically 1 – 2 m2 in size and have a power density in the range 100 - 210 Wp pr. m2. They are sold with a product guarantee of typically two-five years, a power warranty of minimum 25 years and an expected lifetime of more than 30 years.
PV modules are characterised according to the type of absorber material used:
Crystalline silicon (c-Si); the most widely used substrate material is made from purified solar-grade silicon and come in the form of mono- or multi-crystalline silicon wafers. Currently more than 90 pct. of all PV modules are wafer-based divided between multi- and mono-crystalline with a 60:40 share of the market size (this division is expected to level out towards a 50:50 ratio over the coming years). This technology platform is expected to dominate the world market for decades due to significant cost and performance advantages.
Thin film solar cells; where the absorber can be an amorphous/microcrystalline layer of silicon (a-Si/μc-Si), Cadmium telluride (CdTe) or Copper Indium Gallium (di)Selenide (CIGS). These semiconductor materials are deposited on the top cover glass of the solar module in a micrometre thin layer. Tandem junction and triple junction thin film modules are commercially available. In these modules several layers are deposited on top of each other in order to increase the efficiency.
Monolithic III-V solar cells; that are made from compounds of group III and group V elements (Ga, As, In and P), often deposited on a Ge substrate. These materials can be used to manufacture highly efficient multi-junction solar cells that are mainly used for space applications or in Concentrated Photovoltaic (CPV) systems. CPV mainly utilises the direct beam component of the solar irradiation. Dye-Sensitized solar Cells (DSC) and Polymer/Organic Solar Cells; are emerging technologies where significant research activities are among others currently addressing efficiency and lifetime issues. These cells are expected to develop into commercial products by 2020-2030, but are currently not considered candidates for grid-connected systems. The general view on polymer/organic solar cells has been, and still is, that they are suited for low-demanding applications (typically recharging of batteries) but will face challenge in large-scaled, grid-connected installations. This view is, however, presently questioned as a consequence of significant R&D achievements in recent years; breaking of the 10pct. efficiency limit (achieved for small laboratory cells) and a demonstration of large-scale power production with a competitive energy payback and prospects for cost competitiveness.
Perovskite material PV cells; Perovskite solar cells are in principle a DSC cell with an organo-metal salt applied as the absorber material. Perovskites can also be used as an absorber in modified (hybrid) organic/polymer solar cells. The potential to apply perovskite solar cells in a multi-stacked cell on e.g. a traditional c-Si device provides interesting opportunities. Perovskite-based solar cells have, under lab conditions, shown a remarkable progress over the years when rated with respect to efficiency. Within five years the efficiency has increased quite significantly from about 5 pct. to almost 20 pct. The perovskites potential is, however, paired with serious concerns related to their toxicity. The best perovskite absorbers contain soluble organic lead compounds that are toxic and environmentally hazardous at a level that calls for extraordinary precautions. Therefore the perovskite’s health and environmental impact shall be analyzed before they are eventually considered as a viable absorber material in solar cells. Furthermore challenges in industrial scale manufacturing are presently not solved.
In addition to PV modules, a grid connected PV system also includes Balance of System (BOS) consisting of a mounting system, dc-to-ac inverter(s), cables, combiner boxes, optimizers, monitoring/surveillance equipment and for larger PV power plants also transformer(-s).
The typical large onshore wind turbine being installed today is a horizontal-axis, three bladed, upwind, grid connected turbine using active pitch, variable speed and yaw control to optimize generation at varying wind speeds.
Wind turbines work by capturing the kinetic energy in the wind with the rotor blades and transferring it to the drive shaft. The drive shaft is connected either to a speed-increasing gearbox coupled with a medium- or high-speed generator, or to a low-speed, direct-drive generator. The generator converts the rotational energy of the shaft into electrical energy. In modern wind turbines, the pitch of the rotor blades is controlled to maximize power production at low wind speeds, and to maintain a constant power output and limit the mechanical stress and loads on the turbine at high wind speeds.
Wind turbines are designed to operate within a wind speed range which is bounded by a low “cut-in” wind speed and a high “cut-out” wind speed. When the wind speed is below the cut-in speed the energy in the wind is too low to be utilized. When the wind reaches the cut-in speed, the turbine begins to operate and produce electricity. As the wind speed increases, the power output of the turbine increases, and at a certain wind speed the turbine reaches its rated power. At higher wind speeds, the blade pitch is controlled to maintain the rated power output. When the wind speed reaches the cut-out speed, the turbine is shut down or operated in a reduced power mode to prevent mechanical damage.
Onshore wind turbines can be installed as single turbines, clusters or in larger wind farms.
Commercial wind turbines are operated unattended, and are monitored and controlled by a supervisory control and data acquisition (SCADA) system.
The winning price in the tenders for the offshore wind farms in Denmark has decreased substantially from 2012 to 2016. The same trend has been seen in e.g. the Netherlands and Great Britain.
There are several reasons for the reduction in the winning bids. The costs of the wind turbine technology itself, as well as for installation, operation and maintenance have fallen sharply in recent years. In general, more experience has been gained in this area, making the collaboration between the different players on the market more efficient. Moreover, there are better opportunities for optimizing project plans and the volume of the offshore wind market. In addition, interest rates are low and technological and economic risks are assessed lower by investors, therefore low returns are accepted and competition has been increasing. Expectations for the electricity price after expiry of the grant period and other possible income from e.g. certificates of origin also affect the bid price.
Geothermal energy is energy located in underground water reservoirs of the earth. On average the temperature of the reservoir increases with around 3 ºC per 100 m depth. Recent definitions of geothermal energy include all heat from the ground. Here, only heat produced through deep wells is described including the option to use the wells for heat storage.
Heat from deep reservoirs can be utilized directly through a heat exchanger. However, both the temperature and the pumping costs increase with the depth. From Danish experiences it is thus economically more attractive to use heat pumps and extract heat from shallower reservoirs, typically at 800-3000 m depth, where temperatures are 30-90 oC . The heat pumps can either be compressor heat pumps driven with electricity or absorption heat pumps driven by heat. The geothermal water has a high salinity - often 10-20%. For comparison, sea water has a typical level of salinity around 3.5%.
Different concepts for extraction of the geothermal heat exist. In the doublet system, warm geothermal water is pumped to the surface from a production well and the heat depleted brine pumped back into the source reservoir via an injection well in order to maintain the pressure; the bottom-hole spacing is designed to delay premature cooling of the production well.
Several boreholes may also be drilled from one site. This will decrease the cost of heat. Also, one or more of the boreholes may then be used for heat storage, e.g. seasonal, by injection of hot water during the summer and production during winter. However, injection of hot water into the boreholes may cause permeability reductions and change reservoir properties.
Absorption heat pumps driven by district heating biomass boilers can be used to elevate the temperature of the produced heat and increase the heat extraction. Extracting more heat can lower the temperature of the geothermal water to 10-20 oC before it is pumped back to the reservoir via the injection well. In some cases the cooling by heat pumps can help to reduce gas separation (from the water) and avoid precipitation, which may clog the reinjection well.
GDH provides almost all of Reykjavik’s district heating demand with an installed capacity of 830 MJ/s serving 180,000 people, 60 million m3/year of water at an average 75°C (user inlet) temperature. An important part of the hot water supply is piped from distant wells and there is no reinjection of the heat depleted water (ca 35°C) underground.
The Paris Basin GDH system is based on a sedimentary resource and on a doublet system for heat extraction. Here, hot water at an average temperature of 70°C is pumped from depths of 1500 to 1800 m. The system consist of thirty-four geothermal doublets (and as many heating grids), it has been operating since the early 1980’s in the Paris area, the total installed power and generating capacities is 230 MJ/s and 1,000 GWh/year respectively.
Biogas plants produce a methane rich gas on the basis of biodegradable organic material. The feedstock is transported to the plant by road or pumped in pipelines. At the plant, it undergoes an anaerobic process, which generates biogas.
The technology data sheet covers larger plants. It does not include biogas from wastewater treatment plants and landfill sites.
The residual biological material can be recycled as a fertilizer in agriculture and may be separated into solids and fluids.
The biogas can be used directly in a natural gas engine for local CHP generation, in a local gas boiler or it can be upgraded to bio SNG (synthetic natural gas). Upgrading of biogas to bio SNG is treated in a separate chapter of the technology catalogue.
The biomass is received and stored in pre-storage tanks and later processed in digestion reactor tanks. The digesters are normally heated to either 35 - 40 oC (mesophilic digestion), or 50 - 55 oC (thermophilic digestion). After being processed in the main reactor, the material is stored in postprocessing tanks where further gas is produced and collected.
Some plants use continuous digestion in fully stirred digesters. This implies removing a quantity of digested biomass from the digesters and replacing it with a corresponding quantity of fresh biomass, typically several times a day.
Finally, the gas is treated to reduce water and sulphur contents to the desired concentrations.
Fuel cells use an electrochemical process to convert the chemical energy in a fuel to electricity. In contrast to reciprocating engines and gas turbines, fuel cells generate electricity without combusting the fuel. The first practical application for fuel cells emerged in the 1950s when fuel cells were used to provide onboard power for spacecraft. Fuel cells continue to be used in space exploration, but over the past few decades the technology has migrated to other applications, including vehicle transportation and stationary power generation. For stationary power, fuel cells are used for distributed generation (electricity only) and are also configured for combined heat and power (CHP). Table 1 provides an overview of fuel cell operation in CHP applications.
Fuel cells produce direct current electricity through an electrochemical process, much like a standard battery. Unlike a standard battery, a fuel supply continuously replenishes the fuel cell. A single fuel cell element consists of a cathode (positively charged electrode), an anode (negatively charged electrode), and an electrolyte. Hydrogen and oxygen are fed to the anode and cathode, respectively, and chemical reactions occur in the presence of catalysts at the anode and cathode. The chemical reactions generate ions and electrons that produce direct current (DC) electricity and water. The voltage generated from a single fuel cell element is low (< 1 volt DC). For practical applications, over a hundred cells are typically combined (“stacked”) in series to generate voltages in the range of 200 to 400 volts DC.
Several electrolytes have been successfully developed, and fuel cells are often categorized by the type of electrolyte, or in some cases, the type of fuel. Six leading fuel cell technologies are alkaline (AFC), direct methanol (DMFC), phosphoric acid (PAFC), proton exchange membrane (PEMFC), molten carbonate (MCFC), and solid oxide (SOFC). Four of these technologies – PAFC, PEMFC, MCFC, and SOFC – have been used for CHP.
In addition to the fuel cell stack, commercially available fuel cells are typically packaged with two other integrated subsystems: a fuel processor and a power conditioner. The fuel processor, or reformer, converts the fuel (e.g., natural gas or biogas) into a hydrogen rich feed stream for the fuel cell stack. The power conditioner regulates the DC electricity generated from the stack and converts this DC power to alternating current (AC).

## 9. District heating network
Back to user guide
9. District heating network
List of contents
9. District heating network
9.1 Capacities and losses
9.2 Prices
9.3 Hydraulic network analysis
9.4 Pre-insulated pipes
9.5 District heating development
9.6 Two-pipe active beam system
9.7 Steam pipes
9.8 New technology 1
9.9 New technology 2
Assumptions applied (selected in 3.1 LCOE results)
Discount rate |  |  |  |  | 5% | %
Calculation period |  |  |  |  | 1
Start year of calculation |  |  |  |  | 2022
Electricity price development |  |  |  |  | Green
Expected solar thermal production |  |  |  |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  |  |  |  | Sustainable development scenario
Country |  |  |  |  | EU
Currency abbreviation |  |  |  |  | EUR
Currency factor |  |  |  |  | 1
Equipment |  |  |  |  | 1
Installation |  |  |  |  | 1
9.1 Capacities and losses
Table 9-1: Pre-insulated pipes [14]
|  |  | Unit |  | DN15 | DN20 | DN25 | DN32 | DN40 | DN50 | DN65 | DN80 | DN100
Inner diameter |  |  | mm |  | 17.3 | 22.9 | 29.1 | 37.2 | 43.1 | 54.5 | 70.3 | 82.5 | 107.1
Velocity at 10 mm/m |  |  | m/s |  | 0.29 | 0.36 | 0.42 | 0.5 | 0.55 | 0.64 | 0.76 | 0.84 | 1
Water flow |  |  | m3/h |  | 0.24544 | 0.53385 | 1.0057 | 1.9566 | 2.8891 | 5.3755 | 10.6212 | 16.1672 | 32.436
Maximal supply temperature |  |  | oC |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
Return temperature |  |  | oC |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Heat loss capacity |  |  | W/m |  | 8.68 | 9.92 | 9.92 | 9.92 | 12.4 | 12.4 | 13.64 | 14.88 | 14.88
Heat loss energy per year |  |  | MWh/m/a |  | 0.076037 | 0.086899 | 0.086899 | 0.086899 | 0.10862 | 0.10862 | 0.11949 | 0.13035 | 0.13035
Capacity |  |  | MW |  | 0.011388 | 0.024771 | 0.046666 | 0.090787 | 0.13406 | 0.24942 | 0.49282 | 0.75016 | 1.505
Annual max load hours |  |  | h |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
Anual heat transfer |  |  | MWh/a |  | 22.7765 | 49.5416 | 93.3323 | 181.5735 | 268.1105 | 498.8496 | 985.6459 | 1500.3198 | 3010.0632
Annual heat losses/km |  |  | %/km |  | 76.95% | 63.69% | 48.22% | 32.37% | 28.83% | 17.88% | 10.81% | 7.994% | 4.151%
Cost per meter |  |  | EUR/m |  | 373.9446 | 373.9446 | 400.5702 | 419.3946 | 434.8272 | 465.0141 | 507.5811 | 566.7678 | 653.9367
Cost per MWh/a per km |  |  | EUR/MWh/a/km |  | 16418.0062 | 7548.0914 | 4291.8709 | 2309.7781 | 1621.8206 | 932.173 | 514.973 | 377.7646 | 217.2502
|  |  | Unit |  | DN125 | DN150 | DN200 | DN250 | DN300 | DN350 | DN400 | DN450 | DN500
Inner diameter |  |  | mm |  | 132.5 | 160.3 | 210.1 | 263 | 312.7 | 344.4 | 393.8 | 444.4 | 495.4
Velocity at 10 mm/m |  |  | m/s |  | 1.14 | 1.29 | 1.52 | 1.75 | 1.95 | 2.07 | 2.25 | 2.42 | 2.59
Water flow |  |  | m3/h |  | 56.5959 | 93.7358 | 189.7337 | 342.2932 | 539.1866 | 694.2971 | 986.6943 | 1351.4879 | 1797.4651
Maximal supply temperature |  |  | oC |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
Return temperature |  |  | oC |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Heat loss capacity |  |  | W/m |  | 15.5 | 17.36 | 18.6 | 34.72 | 39.432 | 38.068 | 39.432 | 44.392 | 49.476
Heat loss energy per year |  |  | MWh/m/a |  | 0.13578 | 0.15207 | 0.16294 | 0.30415 | 0.34542 | 0.33348 | 0.34542 | 0.38887 | 0.43341
Capacity |  |  | MW |  | 2.6261 | 4.3493 | 8.8036 | 15.8824 | 25.0183 | 32.2154 | 45.7826 | 62.709 | 83.4024
Annual max load hours |  |  | h |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
Anual heat transfer |  |  | MWh/a |  | 5252.1035 | 8698.6813 | 17607.2836 | 31764.8063 | 50036.5134 | 64430.7664 | 91565.2337 | 125418.0756 | 166804.7582
Annual heat losses/km |  |  | %/km |  | 2.52% | 1.718% | 0.9169% | 0.9484% | 0.6856% | 0.5149% | 0.3758% | 0.3091% | 0.2592%
Cost per meter |  |  | EUR/m |  | 769.0879 | 888.6484 | 1110.4714 | 1448.9718 | 1743.379 | 2029.9851 | 2207.3756 | 2207.3756 | 2497.4462
Cost per MWh/a per km |  |  | EUR/MWh/a/km |  | 146.4343 | 102.159 | 63.0689 | 45.6156 | 34.8421 | 31.5065 | 24.1071 | 17.6001 | 14.9723
|  |  | Unit |  | DN600 | DN700 | DN800 | DN900 | DN1000
Inner diameter |  |  | mm |  | 595.8 | 693.6 | 795.2 | 894.4 | 994 |  | DN15 | 16418.0062
Velocity at 10 mm/m |  |  | m/s |  | 2.9 | 3.18 | 3.46 | 3.5 | 3.5 |  | DN20 | 7548.0914
Water flow |  |  | m3/h |  | 2911.0367 | 4326.0743 | 6186.9632 | 7917.3586 | 9778.8887 |  | DN25 | 4291.8709
Maximal supply temperature |  |  | oC |  | 90 | 90 | 90 | 90 | 90 |  | DN32 | 2309.7781
Return temperature |  |  | oC |  | 50 | 50 | 50 | 50 | 50 |  | DN40 | 1621.8206
Heat loss capacity |  |  | W/m |  | 44.268 | 49.6 | 62 | 68.2 | 74.4 |  | DN50 | 932.173
Heat loss energy per year |  |  | MWh/m/a |  | 0.38779 | 0.4345 | 0.54312 | 0.59743 | 0.65174 |  | DN65 | 514.973
Capacity |  |  | MW |  | 135.0721 | 200.7298 | 287.0751 | 367.3654 | 453.7404 |  | DN80 | 377.7646
Annual max load hours |  |  | h |  | 2000 | 2000 | 2000 | 2000 | 2000 |  | DN100 | 217.2502
Anual heat transfer |  |  | MWh/a |  | 270144.2089 | 401459.6996 | 574150.1835 | 734730.8776 | 907480.8716 |  | DN125 | 146.4343
Annual heat losses/km |  |  | %/km |  | 0.1433% | 0.1081% | 0.09451% | 0.08125% | 0.07177% |  | DN150 | 102.159
Cost per meter |  |  | EUR/m |  | 2629.3011 | 2761.1954 | 2893.0898 | 3024.9842 | 3156.8786 |  | DN200 | 63.0689
Cost per MWh/a per km |  |  | EUR/MWh/a/km |  | 9.733 | 6.8779 | 5.0389 | 4.1171 | 3.4787 |  | DN250 | 45.6156
[11 empty] | DN300 | 34.8421
[11 empty] | DN350 | 31.5065
[11 empty] | DN400 | 24.1071
[11 empty] | DN450 | 17.6001
[11 empty] | DN500 | 14.9723
[11 empty] | DN600 | 9.733
[11 empty] | DN700 | 6.8779
[11 empty] | DN800 | 5.0389
[11 empty] | DN900 | 4.1171
[11 empty] | DN1000 | 3.4787
Table 9-2: District heating pipe technical parameters [14]
DN | Dy | t | Di | Vel.10 0/00 | Velocity | Flow | Flow | Power | Loss | Loss | Heat | Heat loss
mm | mm | mm | mm | m/s | m/s | l/s | m3/h | MW | W/m/oC | W/m | MWh/år | MWh/år/m
Dn | Dy | t | Di |  | Velocity | Flow1 | Flow2 | Power | Loss1 | Loss2 | Heat
DN15 | 21.3 | 2 | 17.3 | 0.29 | 0.29 | 0.068177 | 0.24544 | 0.011388 | 0.07 | 8.68 | 22.7765 | 0.076037
DN20 | 26.9 | 2 | 22.9 | 0.36 | 0.36 | 0.14829 | 0.53385 | 0.024771 | 0.08 | 9.92 | 49.5416 | 0.086899
DN25 | 33.7 | 2.3 | 29.1 | 0.42 | 0.42 | 0.27937 | 1.0057 | 0.046666 | 0.08 | 9.92 | 93.3323 | 0.086899
DN32 | 42.4 | 2.6 | 37.2 | 0.5 | 0.5 | 0.5435 | 1.9566 | 0.090787 | 0.08 | 9.92 | 181.5735 | 0.086899
DN40 | 48.3 | 2.6 | 43.1 | 0.55 | 0.55 | 0.80253 | 2.8891 | 0.13406 | 0.1 | 12.4 | 268.1105 | 0.10862
DN50 | 60.3 | 2.9 | 54.5 | 0.64 | 0.64 | 1.4932 | 5.3755 | 0.24942 | 0.1 | 12.4 | 498.8496 | 0.10862
DN65 | 76.1 | 2.9 | 70.3 | 0.76 | 0.76 | 2.9503 | 10.6212 | 0.49282 | 0.11 | 13.64 | 985.6459 | 0.11949
DN80 | 88.9 | 3.2 | 82.5 | 0.84 | 0.84 | 4.4909 | 16.1672 | 0.75016 | 0.12 | 14.88 | 1500.3198 | 0.13035
DN100 | 114.3 | 3.6 | 107.1 | 1 | 1 | 9.01 | 32.436 | 1.505 | 0.12 | 14.88 | 3010.0632 | 0.13035
DN125 | 139.7 | 3.6 | 132.5 | 1.14 | 1.14 | 15.7211 | 56.5959 | 2.6261 | 0.125 | 15.5 | 5252.1035 | 0.13578
DN150 | 168.3 | 4 | 160.3 | 1.29 | 1.29 | 26.0377 | 93.7358 | 4.3493 | 0.14 | 17.36 | 8698.6813 | 0.15207
DN200 | 219.1 | 4.5 | 210.1 | 1.52 | 1.52 | 52.7038 | 189.7337 | 8.8036 | 0.15 | 18.6 | 17607.2836 | 0.16294
DN250 | 273 | 5 | 263 | 1.75 | 1.75 | 95.0814 | 342.2932 | 15.8824 | 0.28 | 34.72 | 31764.8063 | 0.30415
DN300 | 323.9 | 5.6 | 312.7 | 1.95 | 1.95 | 149.774 | 539.1866 | 25.0183 | 0.318 | 39.432 | 50036.5134 | 0.34542
DN350 | 355.6 | 5.6 | 344.4 | 2.07 | 2.07 | 192.8603 | 694.2971 | 32.2154 | 0.307 | 38.068 | 64430.7664 | 0.33348
DN400 | 406.4 | 6.3 | 393.8 | 2.25 | 2.25 | 274.0818 | 986.6943 | 45.7826 | 0.318 | 39.432 | 91565.2337 | 0.34542
DN450 | 457 | 6.3 | 444.4 | 2.42 | 2.42 | 375.4133 | 1351.4879 | 62.709 | 0.358 | 44.392 | 125418.0756 | 0.38887
DN500 | 508 | 6.3 | 495.4 | 2.59 | 2.59 | 499.2959 | 1797.4651 | 83.4024 | 0.399 | 49.476 | 166804.7582 | 0.43341
DN600 | 610 | 7.1 | 595.8 | 2.9 | 2.9 | 808.6213 | 2911.0367 | 135.0721 | 0.357 | 44.268 | 270144.2089 | 0.38779
DN700 | 711.2 | 8.8 | 693.6 | 3.18 | 3.18 | 1201.6873 | 4326.0743 | 200.7298 | 0.4 | 49.6 | 401459.6996 | 0.4345
DN800 | 812.8 | 8.8 | 795.2 | 3.46 | 3.46 | 1718.6009 | 6186.9632 | 287.0751 | 0.5 | 62 | 574150.1835 | 0.54312
DN900 | 914.4 | 10 | 894.4 | 3.5 | 3.5 | 2199.2663 | 7917.3586 | 367.3654 | 0.55 | 68.2 | 734730.8776 | 0.59743
DN1000 | 1016 | 11 | 994 | 3.5 | 3.5 | 2716.358 | 9778.8887 | 453.7404 | 0.6 | 74.4 | 907480.8716 | 0.65174
Design parameters
Cooling of circulated water |  |  | 40 | oC |  | Supply temp. Average |  |  | 90 | oC
Pressure gradient |  |  | 10 | 0/00 |  | Return temp. Average |  |  | 50 | oC
Max load hours |  |  | 2000 | h/a |  | Tempersture of soil |  |  | 8 | oC
Prices |  | Including all construction costs, design supervsion and unexpected costs
Land |  | Denmark
System |  | Preinsulated steel pipes with welded PEH casing including surveillance system
Local conditions |  | Wide road in suburb areas
9.2 Prices
Table 9-3: District heating pipe prices [14]
Country | Denmark | Denmark | Denmark | Denmark | Denmark | Great Britain | Great Britain | Sweden | Sweden | Kazakhstan | USA | USA
Type of road | Large roads | Residential streets | Uncoated | Renovation of concrete edges | Twin | Hard | Soft | Hard | Soft | Hard | Hard | Soft
Reference | Ramboll
DN | €/m | €/m | €/m | €/m | €/m | €/m | €/m | €/m | €/m | €/m | €/m | €/m
DN20 | 373.9446 | 336.5502 | 278.2962 | 387.0327 | 236.5518 | 893.1818 | 687.5 | 293.2446 | 205.8342 | 105.3571 | 596.8527 | 424.8884
DN25 | 400.5702 | 347.2343 | 284.2318 | 399.3194 | 241.5971 | 897.7273 | 692.0455 | 336.8475 | 262.0266 | 113.3929 | 649.8884 | 470.2902
DN32 | 419.3946 | 378.1535 | 314.5883 | 434.8765 | 267.4001 | 945.4545 | 739.7727 | 380.5527 | 318.1167 | 132.1429 | 677.6116 | 476.317
DN40 | 434.8272 | 394.1797 | 318.6585 | 453.3067 | 270.8597 | 965.9091 | 760.2273 | 467.8608 | 349.3347 | 153.5714 | 721.4062 | 496.6071
DN50 | 465.0141 | 419.7569 | 332.2256 | 482.7204 | 282.3918 | 1032.9545 | 801.1364 | 511.566 | 399.2835 | 183.9286 | 794.7321 | 477.5223
DN65 | 507.5811 | 462.3315 | 319.5064 | 531.6813 | 271.5805 | 1086.3636 | 835.2273 | 561.4125 | 449.13 | 221.4286 | 884.7321 | 538.192
DN80 | 566.7678 | 514.7809 | 360.0383 | 591.998 | 306.0325 | 1197.7273 | 937.5 | 605.1177 | 499.0788 | 270.5357 | 1025.558 | 634.2188
DN100 | 653.9367 | 596.6926 | 424.3127 | 686.1965 | 360.6658 | 1303.4091 | 1038.6364 | 723.6438 | 567.6561 | 335.7143 | 1210.1786 | 774.0402
DN125 | 769.0879 | 704.0195 | 517.926 | 809.6225 | 440.2371 | 1396.5909 | 1143.1818 | 767.349 | 623.8485 | 396.4286 | 1250.3571 | 915.2679
DN150 | 888.6484 | 727.4923 | 612.3873 | 836.6161 | 520.5292 | 1512.5 | 1217.0455 | 848.4135 | 680.0409 | 436.6071 | 1582.0312 | 1054.6875
DN175 | 999.5599 | 920.4542 | 705.6615 | 1058.5223 | 599.8123 | 1647.7273 | 1348.8636 | 910.7984 | 723.695 | 476.7857 | 1670.9263 | 1123.7946
DN200 | 1110.4714 | 1023.896 | 798.0877 | 1177.4804 | 678.3745 | 1782.9545 | 1480.6818 | 973.1832 | 767.349 | 608.9286 | 1759.8214 | 1192.9018
DN250 | 1448.9718 | 1341.5061 | 937.6598 | 1542.732 | 797.0108 | 1900 | 1585.2273 | 1072.9785 | 879.6315 | 818.75 | 2305.8482 | 1401.4286
DN300 | 1743.379 | 1618.8079 | 1311.0956 | 1861.629 | 1114.4313 | 2153.4091 | 1820.4545 | 1235.2098 | 1010.6448 | 1000 | 2782.567 | 1959.7098
DN350 | 2029.9851 | 1888.0156 | 1538.515 | 2171.218 | 1307.7377 | 2251.1364 | 1908.6538 | 1359.9795 | 1122.825 | 1133.0357 | 3245.2232 | 2305.6473
DN400 | 2207.3756 | 2057.0192 | 1682.1572 | 2365.572 | 1429.8336 | 2348.8636 | 1996.8531 | 1484.7492 | 1235.2098 | 1265.1786 | 3535.7143 | 2514.1741
DN500 | 2497.4462 |  |  |  |  | 2446.5909 | 2085.0524 | 1721.8014 | 1428.5568 | 1562.5 | 3732.7902 | 2653.9955
DN600 | 2629.3011 |  |  |  |  | 2544.3182 | 2173.2517 | 1971.3408 | 1634.4933 | 1858.9286 | 3929.8661 | 2793.817
DN700 | 2761.1954 |  |  |  |  | 2642.246 | 2261.451 | 2072.6233 | 1721.8315 | 1962.5525 | 4127.0011 | 2933.6857
DN800 | 2893.0898 |  |  |  |  | 2740.1738 | 2349.6503 | 2173.9057 | 1809.1697 | 2066.1765 | 4324.136 | 3073.5544
DN900 | 3024.9842 |  |  |  |  | 2838.1016 | 2437.8497 | 2275.1882 | 1896.5079 | 2169.8004 | 4521.271 | 3213.4231
DN1000 | 3156.8786 |  |  |  |  | 2936.0294 | 2526.049 | 2376.4706 | 1983.8461 | 2273.4244 | 4718.406 | 3353.2918
Country | Denmark | Denmark | Denmark | Denmark | Denmark | Great Britain | Great Britain | Sweden | Sweden | Kazakhstan | USA | USA
Type of road | Large roads | Residential streets | Uncoated | Renovation of concrete edges | Twin | Hard | Soft | Hard | Soft | Hard | Hard | Soft
Reference | Rambøll
DN | EUR/m | EUR/m | EUR/m | EUR/m | EUR/m | EUR/m | EUR/m | EUR/m | EUR/m | EUR/m | EUR/m | EUR/m
DN20 | 373.9446 | 336.5502 | 278.2962 | 387.0327 | 236.5518 | 893.1818 | 687.5 | 293.2446 | 205.8342 | 105.3571 | 596.8527 | 424.8884
DN25 | 400.5702 | 347.2343 | 284.2318 | 399.3194 | 241.5971 | 897.7273 | 692.0455 | 336.8475 | 262.0266 | 113.3929 | 649.8884 | 470.2902
DN32 | 419.3946 | 378.1535 | 314.5883 | 434.8765 | 267.4001 | 945.4545 | 739.7727 | 380.5527 | 318.1167 | 132.1429 | 677.6116 | 476.317
DN40 | 434.8272 | 394.1797 | 318.6585 | 453.3067 | 270.8597 | 965.9091 | 760.2273 | 467.8608 | 349.3347 | 153.5714 | 721.4062 | 496.6071
DN50 | 465.0141 | 419.7569 | 332.2256 | 482.7204 | 282.3918 | 1032.9545 | 801.1364 | 511.566 | 399.2835 | 183.9286 | 794.7321 | 477.5223
DN65 | 507.5811 | 462.3315 | 319.5064 | 531.6813 | 271.5805 | 1086.3636 | 835.2273 | 561.4125 | 449.13 | 221.4286 | 884.7321 | 538.192
DN80 | 566.7678 | 514.7809 | 360.0383 | 591.998 | 306.0325 | 1197.7273 | 937.5 | 605.1177 | 499.0788 | 270.5357 | 1025.558 | 634.2188
DN100 | 653.9367 | 596.6926 | 424.3127 | 686.1965 | 360.6658 | 1303.4091 | 1038.6364 | 723.6438 | 567.6561 | 335.7143 | 1210.1786 | 774.0402
DN125 | 769.0879 | 704.0195 | 517.926 | 809.6225 | 440.2371 | 1396.5909 | 1143.1818 | 767.349 | 623.8485 | 396.4286 | 1250.3571 | 915.2679
DN150 | 888.6484 | 727.4923 | 612.3873 | 836.6161 | 520.5292 | 1512.5 | 1217.0455 | 848.4135 | 680.0409 | 436.6071 | 1582.0312 | 1054.6875
DN175 | 999.5599 | 920.4542 | 705.6615 | 1058.5223 | 599.8123 | 1647.7273 | 1348.8636 | 910.7984 | 723.695 | 476.7857 | 1670.9263 | 1123.7946
DN200 | 1110.4714 | 1023.896 | 798.0877 | 1177.4804 | 678.3745 | 1782.9545 | 1480.6818 | 973.1832 | 767.349 | 608.9286 | 1759.8214 | 1192.9018
DN250 | 1448.9718 | 1341.5061 | 937.6598 | 1542.732 | 797.0108 | 1900 | 1585.2273 | 1072.9785 | 879.6315 | 818.75 | 2305.8482 | 1401.4286
DN300 | 1743.379 | 1618.8079 | 1311.0956 | 1861.629 | 1114.4313 | 2153.4091 | 1820.4545 | 1235.2098 | 1010.6448 | 1000 | 2782.567 | 1959.7098
DN350 | 2029.9851 | 1888.0156 | 1538.515 | 2171.218 | 1307.7377 | 2251.1364 | 1908.6538 | 1359.9795 | 1122.825 | 1133.0357 | 3245.2232 | 2305.6473
DN400 | 2207.3756 | 2057.0192 | 1682.1572 | 2365.572 | 1429.8336 | 2348.8636 | 1996.8531 | 1484.7492 | 1235.2098 | 1265.1786 | 3535.7143 | 2514.1741
DN500 | 2497.4462 |  |  |  |  | 2446.5909 | 2085.0524 | 1721.8014 | 1428.5568 | 1562.5 | 3732.7902 | 2653.9955
DN600 | 2629.3011 |  |  |  |  | 2544.3182 | 2173.2517 | 1971.3408 | 1634.4933 | 1858.9286 | 3929.8661 | 2793.817
DN700 | 2761.1954 |  |  |  |  | 2642.246 | 2261.451 | 2072.6233 | 1721.8315 | 1962.5525 | 4127.0011 | 2933.6857
DN800 | 2893.0898 |  |  |  |  | 2740.1738 | 2349.6503 | 2173.9057 | 1809.1697 | 2066.1765 | 4324.136 | 3073.5544
DN900 | 3024.9842 |  |  |  |  | 2838.1016 | 2437.8497 | 2275.1882 | 1896.5079 | 2169.8004 | 4521.271 | 3213.4231
DN1000 | 3156.8786 |  |  |  |  | 2936.0294 | 2526.049 | 2376.4706 | 1983.8461 | 2273.4244 | 4718.406 | 3353.2918
9.3 Hydraulic network analysis
Figure 9-2: Hydraulic network analysis | [6 empty] | Figure 9-3: District heating network zoning (Cambridge in Boston)
9.4 Pre-insulated pipes
Figure 9-4: Installation of pre-insulated pipes
9.5 District heating development
Figure 9-5: District heating development and concrete duct (utility tunnel)
9.6 Two-pipe active beam system
9.7 Steam pipes
Table 9-4: Steam pipes [19]
STEAM PIPING CAPACITY | [5 empty] | 1,000 LBS./HR STEAM QUANTITY
(1,000 FT²) AREA [HP] FEEDWATER PUMP HP
BURIED PIPE |  |  | INITIAL PRESSURE ΔP/100 FT • TOTAL ΔP SATURATED TEMPERATURE (°F)
STEAM/ CONDENSATE | COST | 15 0.4 · 4 250 | 30 0.6 · 8 270 | 50 0.8 · 12 300 | 100 1.2 · 20 340 | 125 1.6 · 26 350 | 150 2 · 32 370 | 250 3 · 50 400
24"/ 10" | $1,000/LF | 100 (1500) [5] | 200 (3000) [20] | 300 (4500) [40] | 600 (9000) [150] | 700 (10,000) [250] | 1000 (15,000) [400] | 1500 (22,000) [1000]
20” / 8” | $900/LF | 70 (1000) [3] | 150 (2200) [15] | 200 (3000) [30] | 400 (6000) [100] | 450 (6800) [150] | 600 (9000) [250] | 950 (14,000) [600]
18" / 8 " | $850/LF | 50 (750) [2] | 100 (1500) [10] | 150 (2200) [20] | 300 (4500) [75] | 350 (5200) [120] | 450 (6800) [200] | 700 (10,000) [500]
16" / 6" | $700/LF | 40 (600) [1] | 70 (1000) [5] | [100 (1500) [15] | 200 (3000) [50] | 250 (3800) [100] | 350 (5200) [150] | 550 (8300) [400]
14" / 6" | $660/LF | 25 (380) [1] | 50 (750) [4] | 80 (1200) [10] | 150 (2200) [40] | 170 (2500) [75] | 250 (3800) [100] | 350 (5200) [300]
12" / 4" | $550/LF | 20 (300) [1] | 40 (600) [3] | 60 (900) [10] | 120 (1800) [30] | 150 (2200) [50] | 200 (3000) [75] | 300 (4500) [200]
10" / 4" | $500/LF | 15 (220) [1] | 25 (380) [2] | 40 (600) [5] | 70 (1000) [20] | 80 (1200) [25] | 120 (1800) [50] | 200 (3000) [150]
8" / 4" | $480/LF | 7 (100) [1] | 15 (220) [1] | 20 (300) [2] | 40 (600) [10] | 50 (750) [20] | 70 (1000) [30] | 100 (1500) [75]
6" / 3" | $450/LF | 4 (60) [1] | 7 (100) [1] | 10 (150) [1] | 20 (300) [5] | 25 (380) [7] | 35 (520) [15] | 50 (750) [50]
4" / 1.5" | $400/LF | 1 (15) [1] | 2 (30) [1] | 4 (60) [1] | 6 (90) [1] | 7 (100) [2] | 10 (150) [4] | 15 (220) [10]
NOTES: Building SQFT values are based on 60 Btuh/ft2 peak average combined load (building heat and domestic hot water). For winter lows below +25°F: at 0°F multiply building SQFT by 0.8, at -20°F multiply building SQFT by 0.6. Steam lines are sized to approximately 10,000 ft/min. Condensate lines are sized to approximately yield pressure drops less than 2’/100’. Prices shown are construction costs for direct buried pipe. For total project cost add A-E fees, testing, escalations, contingencies, etc. This chart is intended to be used for obtaining an initial estimate of required pipe size and cost. Actual system design must be based on values obtained specifically for the project.
9.8 New technology 1
9.8.1 Technical and economic assumptions
9.9 New technology 2
9.9.1 Technical and economic assumptions
The district heating network is the most important component to take into account in the heat planning, as it is an expensive natural monopoly infrastructure, which enables use of many heat sources at various locations to supply heat to customers in each district. That is why one must be careful in the planning only to plan for the network in zones, which has sufficient heat density, and not least ensure that there are incentives for customers to connect the network.
The investment in the network related to the sale of heat is a simple key figure and indicator for cost effectiveness. Therefore, it is a good idea to calculate the indicator “investment in district heating grid per heat sale”, in the unit €/MWh/a for each district. In the DHAT model a marginal heat cost considering all costs over total heat production is calculated. Once the profitability of a district heating investment project is analysed based on the difference between customers alternative heat cost and the cost of generating the heat, we know the critical key figure. Thus, the energy planner can look at all marginal extensions of the network and prove that all key figures for each branch line to individual customers have key figures lower than the critical.
Due to the economies of scale for district heating networks, the key figure will illustrate that it can be a good idea to establish a 500 m branch line to a large customer, whereas a 15 m branch line to a small customer may not be cost effective. In this work, the map is essential, as it shows how the production plants can be interconnected with all the districts and customers and how the districts can be supplied one after the other and ranked. First priority should be given to districts close to the plants and districts with large heat density. Second priority should be given to districts, which can be supplied by pipes via the first priority districts. Third priority is given to districts with a longer distance from the production plants, which can be supplied from second priority districts. Finally, small branches of the grid and branch lines can be assessed by the investment key-figure. Following information is required:
- Identification of a suitable trench of the distribution network from production to all districts and customers plus large branch lines
- Estimate of pipe dimensions and length of each pipe for a distribution network and for typical branch lines in each district -
- The network will normally be analysed by a hydraulic analysis system, but for a simple case, the energy planner can make a rough estimate manually based on a design table and manual measurements of pipe length
- The planner can draw a logic sequence of the network. For example, connection to district A is necessary for supply of heat to district B. Therefore, the network in district A must be designed to also supply district B
Moreover, the planner has to look for the most cost effective and realistic design concept, within the local boundaries and constrains. These could be the following:
- The variation of the elevation: The height above sea level of production plant and customers
- The need for maximal supply temperature to the majority of customers on the coldest day (see also section 3.4)
- Analysis of alternative solutions for the few customers, who need larger supply temperature than the majority. For example, customers who need heat at a larger temperature for industrial processes
- The most likely return temperature from customers, once their customer installations are upgraded with control valves
- Length of the system and suitable places for booster pump stations
- Capacity constrains in existing district heating pipes
Development of district heating pipe constructions in vrief in 5 decades:
1970 Concrete ducts, expensive, long life-time, but some failures, first preinsulated pipes in Løgstør, but poor quality
1980 Danish standard for DH pipes in the ground, Better quality of preinsulated pipes of various principles and competition
1990 Preinsulated pipes of good quality almost 100% market share, bondes system, welded muffs, no expansion joints, surveillance system
2000 Bended pipes, twin pipes, no-dig methods etc.
2010 Preinsuated pipes all over the world for DH&C
Standards for district heating pipe systems and pipes freedom to good design based on function:
- Standards for use of preinsulated pipes
- Standards for the pipes
- Safety regulations and classification, e.g. pressure and temperature
- Standards for specific components, boilers etc.
- Environmental requirements
- Guidelines for infrastructure in the ground in roads – “the guest principle”
- Way of right, same importance as roads for public use
- Declaration in land-owners register
Typical design parameters:
- Pressure level: 6, 10, 16 or 25 bar max pres.
- Maximal temperature: <110 oC or <160 oC
- Return temperature: as low as possible
- Hydraulic design: Optimize based on life-cycle cost, use available pressure,
but max 3,5 m/s, typical 10 mm/m for new networks, as much
as possible in old networks
- Bonded without expansion joints for < 110 oC
- Twin pipes < DN200 if regular flat trench
- Long trench, ”gas pipe” technology
- No-dig method for crossings
- Small no-dig tunnels under rail roads
- Possibility to install local peak boilers
- Quality of typical customer heating systems considering direct connection
- The maximal supply temperature of base load production units
- The benefit of heat storages
Based on this information, the energy planner is guided to propose a realistic system design. In the first stage, the options are the following:
1. Steam system in case a majority of industrial customers requires process energy
2. Super-heated hot water district heating (temperatures above 110 oC and up to 165 oC) in case industrial customers need low pressure steam
3. Hot water district heating (temperatures below 110 oC) in case the majority of customers only need heating
4. Low temperature district heating (temperatures below 95 oC or even lower)
The first two options, which can supply most types of customers, have been the solution in many cities for years, but option 3 and 4 are becoming best practice due to lower costs of pipe installations, lower cost of customer installations, more cost effective for establishing thermal storages, more cost effective heat production from combined heat and power, heat pumps, geothermal energy, solar heating and flue gas condensation, lower heat losses in the district heating grid and improved reliability.
In the conceptual design of a low temperature district heating network, the maximal operation temperature must be lower than 95 oC to allow pressure less heat storage tanks or lower than 85 oC to allow heat storage pits and certain renewable heat production sources. Furthermore, the pressure level must be 6 bar for direct connection or 10 bar, 16 bar or 25 bar for indirect connection at customer installations. Figure 3-1 below shows a print from a GIS-based hydraulic analysis, which has been used to calculate the accurate length of pipes and to design the necessary dimensions considering heat load of each costumer, diversity of consumption, maximal supply temperature, estimated return temperature and available pressure difference from the production plants. In the network design it must be taken into account that the diversity factor is 1.0 at customer branch lines and that it is gradually reduced for larger dimensions for a number of customers.
To determine the dimensions of the pipes in the district heating network, one must do the following:
- Identify load cases on the heat duration curves (zonal development)
- Peak load
- Maximal use of base load
- Summer load
- Calculate trench in hydraulic model
- Transfer demand and production capacity to the grid
- Design parameters, pressure levels and zones, temperature
- Design of network for the base case, including booster pumps
- Optimization, booster pumps and considerations for future expansion
1G distrct heating systems are steam systems with steam pipes in concrete ducts. Typically, the costs for establishing and maintning such a system are much higher than later generations of district heating systems. Most American systems still operated as steam systems (1st generation)
The 4G district heating systems are operated at lower temperatures. Experiences from Denmark are in few residential areas. Typically, theses systems have much lower heat losses and thereby higher efficiencies.
Synergies between district heating and cooling systems are easier to obtain, when the temperatures are lowered because the heat pumps cannot operate at very high temperatures (maybe with low efficiency).
It is also easier to onvert to 100 % renewable energy systems, as heat pumps and electric boilers utilize electricity production from renewable energy sources like electricity from wind and solar.
Technology
Active beams are devices able to provide outdoor air, sensible heating and sensible cooling to a space. They consist of a primary air plenum, a mixing chamber, a heat exchanger and several nozzles. The primary air is discharged to the mixing chamber though nozzles. This generates a low static pressure region, which induced air from the room up through the heat exchanger, where the hot or cold water is circulating. The conditioned air is then mixed with primary air, and the mixture is supplied to the space.
Application
Active beams are commonly used in a four-pipe configuration including two supply pipes and two return pipes. Therefore, some zones can receive hot water for heating, while other zones receive chilled water for cooling. The main characteristic of the novel two-pipe active beam system is its ability to provide simultaneous heating and cooling by operating a single hydronic circuit with supply water temperatures of about 22°C all year round. A room with an indoor air temperature of 20°C would be heated, while a room at 24°C would be cooled. Beside the advantages in terms of exploitation of sustainable energy sources, operating such water temperature opens opportunities for transferring heat among different rooms when simultaneous heating and cooling occurs in the building.
Scientific studies
The operation of the novel two-pipe active beam system was studied by means of simulation-based analyses and full-scale experiments. Simulation results showed that the novel two-pipe system is able to reduce the annual primary energy use of buildings by approximately 20% in comparison to conventional four-pipe system.
Full-scale experiments were performed in a newly constructed building in Jönköping, Sweden. Physical parameters such as water flows and temperatures were monitored for a one-year period in the hydronic circuit, and measurements of room air temperature, air velocity and humidity were collected in indoor spaces to assess thermal comfort conditions. The monitoring of water flows and temperatures confirmed the ability of the system in operating with a single hydronic circuit to provide simultaneous heating and cooling while reducing annual primary energy use. Measurements and questionnaires regarding thermal comfort showed that the system provides a satisfactory thermal environment in the building.
Reports
A total of 9 scientific publications have been produced on the topic of the novel two-pipe active beam system:
Journal articles
1. A. Maccarini, G. Hultmark, N. C. Bergsøe and A. Afshari. 2018. Free cooling potential of a PCM-based heat exchanger coupled with a novel HVAC system for simultaneous heating and cooling of buildings. Sustainable Cities and Societies
2. A. Maccarini, G. Hultmark, A. Afshari, N. C. Bergsøe, and A. Vorre. 2017. Transferring heat among building zones through a room-temperature water loop – Influence of climate and occupancy. Building Simulation, volume 10, pp 697-710.
3. A. Maccarini, M. Wetter, G. Hultmark, A. Vorre, A. Afshari, and N. C. Bergsøe. 2017. Energy savings potential of a two-pipe system for simultaneous heating and cooling of office buildings. Energy and Buildings, volume 134, pp 234-247.
4. A. Maccarini, G. Hultmark, A. Vorre, A. Afshari, and N. C. Bergsøe. 2015. Modeling of active beam units with Modelica. Building Simulation, volume 8, pp 543–550.
Articles in conference proceedings
5. A. Maccarini, G. Hultmark, N. C. Bergsøe and A. Afshari. 2018. Operation of a novel two-pipe system in an office building: a thermal comfort study. Accepted for oral presentation at the 15th International Conference on Indoor Air Quality and Climate (IndoorAir 2018). Philadelphia, USA, July 22-27.
6. A. Maccarini, G. Hultmark, A. Afshari, and N. C. Bergsøe. 2017. Analysis of control strategies for a novel HVAC system equipped with a room-temperature water loop. Proceedings of the 15th IBPSA Conference. San Francisco, USA, August 7-9.
7. A. Maccarini, A. Afshari, G. Hultmark, N. C. Bergsøe, and A. Vorre. 2016. Development of a new controller for simultaneous heating and cooling of office buildings. Proceedings of the 9th IAQVEC Conference. Seoul, South Korea, October 24-26.
8. A. Maccarini, A. Afshari, G. Hultmark, N. C. Bergsøe, and A. Vorre. 2016. Modeling of a novel low-exergy system for office buildings with Modelica. Proceedings of the 12th REHVA World Congress (CLIMA 2016). Aalborg, Denmark, May 23–26.
9. A. Maccarini, A. Afshari, N. C. Bergsøe, G. Hultmark, M. Jacobsson, and A. Vorre. 2014. Innovative two-pipe active chilled beam system for simultaneous heating and cooling of office buildings. Proceedings of the 13th International Conference on Indoor Air Quality and Climate (IndoorAir 2014). Hong Kong, July 7–12.

## 10. District cooling network
Back to user guide
10. District cooling network
List of contents
10. District cooling network
10.1 Capacities and losses
10.2 PEX pipes
10.3 New technology 1
10.4 New technology 2
Assumptions applied (selected in 3.1 LCOE results)
Discount rate |  |  |  |  | 5% | %
Calculation period |  |  |  |  | 1
Start year of calculation |  |  |  |  | 2022
Electricity price development |  |  |  |  | Green
Expected solar thermal production |  |  |  |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  |  |  |  | Sustainable development scenario
Country |  |  |  |  | EU
Currency abbreviation |  |  |  |  | EUR
Currency factor |  |  |  |  | 1
Equipment |  |  |  |  | 1
Installation |  |  |  |  | 1
10.1 Capacities and losses
Table 10-1: Pre-insulated pipes [14]
|  |  | Unit |  | DN15 | DN20 | DN25 | DN32 | DN40 | DN50 | DN65 | DN80 | DN100
Inner diameter |  |  | mm |  | 17.3 | 22.9 | 29.1 | 37.2 | 43.1 | 54.5 | 70.3 | 82.5 | 107.1
Velosity at 10 mm/m |  |  | m/s |  | 0.29 | 0.36 | 0.42 | 0.5 | 0.55 | 0.64 | 0.76 | 0.84 | 1
Water flow |  |  | m3/h |  | 0.24544 | 0.53385 | 1.0057 | 1.9566 | 2.8891 | 5.3755 | 10.6212 | 16.1672 | 32.436
Maximal supply temperature |  |  | oC |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Return temperature |  |  | oC |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Heat loss capacity |  |  | W/m |  | 0.35 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.55 | 0.6 | 0.6
Heat loss energy per year |  |  | MWh/m/a |  | 0.003066 | 0.003504 | 0.003504 | 0.003504 | 0.00438 | 0.00438 | 0.004818 | 0.005256 | 0.005256
Capacity |  |  | MW |  | 0.0025624 | 0.0055734 | 0.0105 | 0.020427 | 0.030162 | 0.056121 | 0.11089 | 0.16879 | 0.33863
Annual max load hours |  |  | h |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
Anual heat transfer |  |  | MWh/a |  | 5.1247 | 11.1469 | 20.9998 | 40.854 | 60.3249 | 112.2412 | 221.7703 | 337.572 | 677.2642
Annual heat losses/km |  |  | %/km |  | 37.43% | 23.92% | 14.3% | 7.899% | 6.769% | 3.756% | 2.126% | 1.533% | 0.7701%
Cost per meter |  |  | EUR/m |  | 373.9446 | 373.9446 | 400.5702 | 419.3946 | 434.8272 | 465.0141 | 507.5811 | 566.7678 | 653.9367
Cost per MWh/a per km |  |  | EUR/MWh/a/km |  | 72968.9163 | 33547.0731 | 19074.9818 | 10265.6804 | 7208.0916 | 4142.9909 | 2288.7691 | 1678.9539 | 965.5563
|  |  | Unit |  | DN125 | DN150 | DN200 | DN250 | DN300 | DN350 | DN400 | DN450 | DN500
Inner diameter |  |  | mm |  | 132.5 | 160.3 | 210.1 | 263 | 312.7 | 344.4 | 393.8 | 444.4 | 495.4
Velosity at 10 mm/m |  |  | m/s |  | 1.14 | 1.29 | 1.52 | 1.75 | 1.95 | 2.07 | 2.25 | 2.42 | 2.59
Water flow |  |  | m3/h |  | 56.5959 | 93.7358 | 189.7337 | 342.2932 | 539.1866 | 694.2971 | 986.6943 | 1351.4879 | 1797.4651
Maximal supply temperature |  |  | oC |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Return temperature |  |  | oC |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Heat loss capacity |  |  | W/m |  | 0.625 | 0.7 | 0.75 | 1.4 | 1.59 | 1.535 | 1.59 | 1.79 | 1.995
Heat loss energy per year |  |  | MWh/m/a |  | 0.005475 | 0.006132 | 0.00657 | 0.012264 | 0.013928 | 0.013447 | 0.013928 | 0.01568 | 0.017476
Capacity |  |  | MW |  | 0.59086 | 0.9786 | 1.9808 | 3.5735 | 5.6291 | 7.2485 | 10.3011 | 14.1095 | 18.7655
Annual max load hours |  |  | h |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
Anual heat transfer |  |  | MWh/a |  | 1181.7233 | 1957.2033 | 3961.6388 | 7147.0814 | 11258.2155 | 14496.9224 | 20602.1776 | 28219.067 | 37531.0706
Annual heat losses/km |  |  | %/km |  | 0.4612% | 0.3123% | 0.1656% | 0.1713% | 0.1236% | 0.09267% | 0.06756% | 0.05554% | 0.04654%
Cost per meter |  |  | EUR/m |  | 769.0879 | 888.6484 | 1110.4714 | 1448.9718 | 1743.379 | 2029.9851 | 2207.3756 | 2207.3756 | 2497.4462
Cost per MWh/a per km |  |  | EUR/MWh/a/km |  | 650.819 | 454.0399 | 280.3061 | 202.7362 | 154.8539 | 140.0287 | 107.1428 | 78.2228 | 66.5434
|  |  | Unit |  | DN600 | DN700 | DN800 | DN900 | DN1000
Inner diameter |  |  | mm |  | 595.8 | 693.6 | 795.2 | 894.4 | 994
Velosity at 10 mm/m |  |  | m/s |  | 2.9 | 3.18 | 3.46 | 3.5 | 3.5
Water flow |  |  | m3/h |  | 2911.0367 | 4326.0743 | 6186.9632 | 7917.3586 | 9778.8887
Maximal supply temperature |  |  | oC |  | 15 | 15 | 15 | 15 | 15
Return temperature |  |  | oC |  | 6 | 6 | 6 | 6 | 6
Heat loss capacity |  |  | W/m |  | 1.785 | 2 | 2.5 | 2.75 | 3
Heat loss energy per year |  |  | MWh/m/a |  | 0.015637 | 0.01752 | 0.0219 | 0.02409 | 0.02628
Capacity |  |  | MW |  | 30.3912 | 45.1642 | 64.5919 | 82.6572 | 102.0916
Annual max load hours |  |  | h |  | 2000 | 2000 | 2000 | 2000 | 2000
Anual heat transfer |  |  | MWh/a |  | 60782.447 | 90328.4324 | 129183.7913 | 165314.4475 | 204183.1961
Annual heat losses/km |  |  | %/km |  | 0.02572% | 0.01939% | 0.01695% | 0.01457% | 0.01287%
Cost per meter |  |  | EUR/m |  | 769.0879 | 888.6484 | 1110.4714 | 1448.9718 | 1743.379
Cost per MWh/a per km |  |  | EUR/MWh/a/km |  | 12.6531 | 9.838 | 8.5961 | 8.7649 | 8.5383
Table 10-2: District heating pipe technical parameters [14]
DN | Dy | t | Di | Vel.10 0/00 | Velocity | Flow | Flow | Power | Loss | Loss | Heat | Heat loss
mm | mm | mm | mm | m/s | m/s | l/s | m3/h | MW | W/m/oC | W/m | MWh/år | MWh/år/m
Dn | Dy | t | Di |  | Velocity | Flow1 | Flow2 | Power | Loss1 | Loss2 | Heat
DN15 | 21.3 | 2 | 17.3 | 0.29 | 0.29 | 0.068177 | 0.24544 | 0.0025624 | 0.07 | 0.35 | 5.1247 | 0.003066
DN20 | 26.9 | 2 | 22.9 | 0.36 | 0.36 | 0.14829 | 0.53385 | 0.0055734 | 0.08 | 0.4 | 11.1469 | 0.003504
DN25 | 33.7 | 2.3 | 29.1 | 0.42 | 0.42 | 0.27937 | 1.0057 | 0.0105 | 0.08 | 0.4 | 20.9998 | 0.003504
DN32 | 42.4 | 2.6 | 37.2 | 0.5 | 0.5 | 0.5435 | 1.9566 | 0.020427 | 0.08 | 0.4 | 40.854 | 0.003504
DN40 | 48.3 | 2.6 | 43.1 | 0.55 | 0.55 | 0.80253 | 2.8891 | 0.030162 | 0.1 | 0.5 | 60.3249 | 0.00438
DN50 | 60.3 | 2.9 | 54.5 | 0.64 | 0.64 | 1.4932 | 5.3755 | 0.056121 | 0.1 | 0.5 | 112.2412 | 0.00438
DN65 | 76.1 | 2.9 | 70.3 | 0.76 | 0.76 | 2.9503 | 10.6212 | 0.11089 | 0.11 | 0.55 | 221.7703 | 0.004818
DN80 | 88.9 | 3.2 | 82.5 | 0.84 | 0.84 | 4.4909 | 16.1672 | 0.16879 | 0.12 | 0.6 | 337.572 | 0.005256
DN100 | 114.3 | 3.6 | 107.1 | 1 | 1 | 9.01 | 32.436 | 0.33863 | 0.12 | 0.6 | 677.2642 | 0.005256
DN125 | 139.7 | 3.6 | 132.5 | 1.14 | 1.14 | 15.7211 | 56.5959 | 0.59086 | 0.125 | 0.625 | 1181.7233 | 0.005475
DN150 | 168.3 | 4 | 160.3 | 1.29 | 1.29 | 26.0377 | 93.7358 | 0.9786 | 0.14 | 0.7 | 1957.2033 | 0.006132
DN200 | 219.1 | 4.5 | 210.1 | 1.52 | 1.52 | 52.7038 | 189.7337 | 1.9808 | 0.15 | 0.75 | 3961.6388 | 0.00657
DN250 | 273 | 5 | 263 | 1.75 | 1.75 | 95.0814 | 342.2932 | 3.5735 | 0.28 | 1.4 | 7147.0814 | 0.012264
DN300 | 323.9 | 5.6 | 312.7 | 1.95 | 1.95 | 149.774 | 539.1866 | 5.6291 | 0.318 | 1.59 | 11258.2155 | 0.013928
DN350 | 355.6 | 5.6 | 344.4 | 2.07 | 2.07 | 192.8603 | 694.2971 | 7.2485 | 0.307 | 1.535 | 14496.9224 | 0.013447
DN400 | 406.4 | 6.3 | 393.8 | 2.25 | 2.25 | 274.0818 | 986.6943 | 10.3011 | 0.318 | 1.59 | 20602.1776 | 0.013928
DN450 | 457 | 6.3 | 444.4 | 2.42 | 2.42 | 375.4133 | 1351.4879 | 14.1095 | 0.358 | 1.79 | 28219.067 | 0.01568
DN500 | 508 | 6.3 | 495.4 | 2.59 | 2.59 | 499.2959 | 1797.4651 | 18.7655 | 0.399 | 1.995 | 37531.0706 | 0.017476
DN600 | 610 | 7.1 | 595.8 | 2.9 | 2.9 | 808.6213 | 2911.0367 | 30.3912 | 0.357 | 1.785 | 60782.447 | 0.015637
DN700 | 711.2 | 8.8 | 693.6 | 3.18 | 3.18 | 1201.6873 | 4326.0743 | 45.1642 | 0.4 | 2 | 90328.4324 | 0.01752
DN800 | 812.8 | 8.8 | 795.2 | 3.46 | 3.46 | 1718.6009 | 6186.9632 | 64.5919 | 0.5 | 2.5 | 129183.7913 | 0.0219
DN900 | 914.4 | 10 | 894.4 | 3.5 | 3.5 | 2199.2663 | 7917.3586 | 82.6572 | 0.55 | 2.75 | 165314.4475 | 0.02409
DN1000 | 1016 | 11 | 994 | 3.5 | 3.5 | 2716.358 | 9778.8887 | 102.0916 | 0.6 | 3 | 204183.1961 | 0.02628
Design parameters
Cooling of circulated water |  |  | 9 | oC |  | Return temp. Average |  |  | 15 | oC
Pressure gradient |  |  | 10 | 0/00 |  | Supply temp. Average |  |  | 6 | oC
Max load hours |  |  | 2000 | h/a |  | Tempersture of soil |  |  | 8 | oC
Prices |  | Including all construction costs, design supervsion and unexpected costs
Land |  | Denmark
System |  | Preinsulated steel pipes with welded PEH casing including surveillance system
Local conditions |  | Wide road in suburb areas
Table 10-3: Chilled water piping capacity [19]
CHILLED WATER PIPING CAPACITY PIPE SIZE VS. TONS - BLDG. SQ. FT PER TONS CAPACITY WATER SIDE TEMPERATURE DIFFERENTIAL (1,000 FT²) AREA
DIRECT BURIED PIPE |  | WATER SIDE TEMPERATURE RISE, ΔT GPM/TON
PIPE DIAMETER (IN) | GPM VEL FT/100 FT HP COST | 10° F 2.4 | 12° F 2.06 | 14° F 1.7 | 16° F 1.5 | 18° F 1.33 | 20° F 1.20 | 24° F 1.0
48” | 60,000 GPM 10.6 FPS 0.8’/100’ 400 HP $2,500/LF | 25,000 (7,500) | 30,000 (9,000) | 35,000 (10,500) | 40,000 (12,000) | 45,000 (13,500) | 50,000 (15,000) | 60,000 (18,000)
42” | 40,000 GPM 9.2 FPS 0.8’/100’ 200 HP $2,200/LF | 16,000 (4,800) | 20,000 (6,000) | 24,000 (7,200) | 27,000 (8,000) | 30,000 (9,000) | 34,000 (10,000) | 40,000 (12,000)
36” | 30,000 GPM 9.4 FPS 1.0’/100’ 200 HP $2,000/LF | 12,500 (3,800) | 15,000 (4,500) | 17,500 (5,300) | 20,000 (6,000) | 22,500 (6,800) | 25,000 (7,500) | 30,000 (9,000)
30” | 20,000 GPM 9.1 FPS 1.1’/100’ 150 HP $1,500/LF | 8,000 (2,400) | 10,000 (3,000) | 12,000 (3,600) | 13,000 (4,000) | 15,000 (4,500) | 17,000 (5,000) | 20,000 (6,000)
24” | 12,000 GPM 8.5 FPS 1.3’/100’ 120 HP $1,300/LF | 5,000 (1,500) | 6,000 (1,800) | 7,000 (2,100) | 8,000 (2,400) | 9,000 (2,700) | 10,000 (3,000) | 12,000 (3,600)
18” | 7,000 GPM 9.5 FPS 2.0’/100’ 100 HP $1,000/LF | 3,000 (900) | 3,500 (1,050) | 4,000 (1,200) | 4,600 (1,400) | 5,200 (1,600) | 6,000 (1,800) | 7,000 (2,100)
16” | 5,000 GPM 9.0 FPS 2.8’/100’ 100 HP $800/LF | 2,000 (600) | 2,500 (750) | 3,000 (900) | 3,500 (1,050) | 3,800 (1,100) | 4,000 (1,200) | 5,000 (1,500)
14” | 4,000 GPM 9.5 FPS 3.0’/100’ 100 HP $700/LF | 1,700 (500) | 2,000 (600) | 2,400 (720) | 2,700 (800) | 3,000 (900) | 3,400 (1,000) | 4,000 (1,200)
12” | 3,000 GPM 8.7 FPS 3.8’/100’ 75 HP $650/LF | 1,250 (380) | 1,500 (450) | 1,800 (540) | 2,000 (600) | 2,300 (680) | 2,500 (750) | 3,000 (900)
10” | 2,000 GPM 8.0 FPS 3.1’/100’ 40 HP $500/LF | 800 (240) | 1,000 (300) | 1,200 (360) | 1,300 (400) | 1,500 (450) | 1,700 (500) | 2,000 (600)
8” | 1,200 GPM 7.7 FPS 4.0.’/100’ 35 HP $400/LF | 500 (150) | 600 (180) | 700 (200) | 800 (240) | 900 (270) | 1,000 (300) | 1,200 (360)
6” | 600 GPM 6.7 FPS 4.0’/100’ 20 HP $300/LF | 250 (75) | 300 (90) | 350 (100) | 400 (120) | 450 (140) | 500 (150) | 600 (180)
4” | 200 GPM 5.0 FPS 4.0’/100’ 5 HP $200/LF | 80 (24) | 100 (30) | 120 (36) | 130 (40) | 150 (45) | 170 (50) | 200 (60)
NOTES GPM’s were selected to maintain water velocities (V) below 10 fps, and pressure drop (f) below 1’/100’ for large size pipes. The GPM values for smaller size pipes were selected to maintain water velocities below 7 fps and pressure drop below 4’/100’. The velocities and friction drop values are according to Cameron. (C=100). HP values to pump the water through 1000’ supply and 1000’ return calculated using: HP = GPM x TDH TDH = 2000 x f 3940 x .75 100 1000’s of gross sq ft of building are figured at 300 GSF/ton, i.e. (10,500) indicates that approximately 10,500,000 GSF can be air-conditioned with 35,000 tons. For heavy research areas use 220 GSF/ton. This chart is intended to be used for obtaining an initial estimate of required pipe size and cost. Actual system design must be based on values obtained specifically for the project. Total installed cost per linear ft of buried supply & return piping (2 pipes). Price includes trenching, insulation, fittings, back fill & moderate amounts of surfacing repairs. For total project cost add A-E fees, testing, escalations, contingencies, etc.
Table 10-4: Chilled water central plant cost
CHILLED WATER CENTRAL PLANT COST
1 | Water chillers (with starters) |  |  |  |  | Average
| a. | Centrifugal |  | 300 to 600 tons | $320/ton
|  |  |  | 600 to 1,400 tons |  | $290/ton
|  |  |  | 1,500 to 3,000 tons | $280/ton
| b. | Absorption | (1 stage): | 90 to 1,600 tons | $400/ton
|  |  | (2 stage): | 350 to 1,000 tons | $800/ton
| c. | Screw |  | 70 to 130 tons | $500/ton
|  |  |  | 150 to 450 tons | $400/ton
| d. | Screw | (air cooled) | 70 to 400 tons | $550/ton
| e. | Setting, Rigging, Installation |  | $50 to $150 tons |  | $130/ton
| f. | Add 4160 Volt Motor |  |  | $15/ton
| g. | Add .035” Tubes |  |  | $10/ton
| h. | Add Gas Engine Driver |  |  | $300/ton
2 | Pumps $50 - $120/ton |  |  |  |  | $80/ton
3 | Cooling tower
| a. | Normal |  | $50 to $140/ton
| b. | Permanent |  | $100 to $240/ton |  | $200/ton
4 |  | PIPING |  | $120 to $250/ton |  | $200/ton
5 |  | CONTROLS |  | $40 to $100/ton |  | $80/ton
6 |  | ELECTRICAL |  | $80 to $300/ton |  | $180/ton
7 |  | BUILDING |  | @ 1.5 sf/ton at $160/sf |  | $240/ton
TOTAL | [5 empty] | $1400/ton
TOTAL WITHOUT BUILDING AND WITH PERMANENT COOLING TOWER | [5 empty] | $1160/ton
TOTAL WITHOUT BUILDING AND WITH NORMAL COOLING TOWER | [5 empty] | $1100/ton
NOTE: |  | Drop-in Chiller with minimum pipe and conventional tower and simple electrical |  |  |  | $810/ton
|  | CHILLED WATER DISTRIBUTION, LARGE CAMPUS |  |  |  | $500/ton
$200 to $1000/ton
|  | PLATE/FRAME HEAT EXCHANGER |  |  |  | $80/ton
Unit only $40 to $120/ton
|  | Complete Installation with piping and Simple Auto Control |  |  |  | $140/ton
$100 to $160/ton
10.2 PEX pipes
Figure 10-2: Cost comparison between Thermaflex Twin and Steel Twin
Table 10-5: Alupex pipes [14]
|  |  | €/m | EUR/m
Alupex16 Twin |  |  | 145 | 145
Alupex20 Twin |  |  | 175 | 175
Alupex26 Twin |  |  | 190 | 190
Table 10-6: Thermaflex pipes [14]
|  |  | €/m | EUR/m
Thermaflex 16 Twin |  |  | 110 | 110
Thermaflex 20 Twin |  |  | 130 | 130
Thermaflex 25 Twin |  |  | 153.226 | 153.226
Thermaflex 32 Twin |  |  | 231.4769 | 231.4769
Thermaflex 40 Twin |  |  | 255.2625 | 255.2625
Thermaflex 50 Twin |  |  | 319.5614 | 319.5614
Thermaflex 63 Twin |  |  | 293.3345 | 293.3345
Thermaflex 75 |  |  | 367.1439 | 367.1439
Thermaflex 90 |  |  | 418.1649 | 418.1649
Thermaflex 110 |  |  | 567.6277 | 567.6277 |  | Figure 10-3: PEX pipes for low temperature district heating and district cooling
10.3 New technology 1
10.3.1 Technical- and economic assumptions
10.4 New technology 2
10.4.1 Technical- and economic assumptions
The District Cooling (DC) network is a vital part of the energy infrastrucure for developing low carbon resilient solutions in all campusses and cities warm and mild climate, as it is the key to utilize and store cost effective and efficient low carbon sources for cooling. Main focus will be on traditional cold water pipe systems, e.g. 6 dgr.C supply and 15 dgr.C return, which could be established either as a DH water system in preinsulated pipes or as a fresh water system in PEH pipes, which can distribute water including ozygen. These pipes can also be used to distibute cold deep-lake water directly without heat exchanger. The secrets of district cooling:
- The design capacity of buildings can be adjusted (avoid overcapacity in buildings)
- Reduction in maximum capacity due to diversity, factor 0,8
- Tank thermal energy storage for cold water will reduce peak by factor 0,7
- Reduction in CapEx due to economies of scale for chillers, factor 0,5-0,9
- Optimize electricity consumption with storage tank – operation during off-peak hours in which most efficient plants are supplying electricity to the electrical grid
- Optimal location of cooling plant as part of the urban planning
- Use surplus heat from cooling for district heating
- Use of ATES aquifer thermal energy storage for heat and cold
- Combined use of heat pumps for cooling and heating (co-gen)
- Use of absorption chillers to use surplus heat if any
- Use of absorption chillers reduce electric capacity demand
- Offer total solution for thermal comfort to the building owner
- Save expensive space at buildings, in basement and on roof-tops
- Use ventilation coils and floor tubes for heating or cooling
- Synergies between district heating and district cooling
PEX pipes can be used for low temperature district heating and district cooling. The investment costs are typically lower at small dimensions than similar sized steel pipes. On the other hand is the heat loss slightly higher for plastic pipes than steel pipes. Thus, only at low temperatures are plastic pipes preferable. We have listed pros and cons for plastic pipes, mostly related to low temperature district heating, but it can also be related to district cooling.
The advantage of lower temperatures are:
- Cheaper plastic pipes can be used
- Heat loss is lower when the temperature is lower
The downside is, however:
- The pipe dimensions will increase due to lower DeltaT, thus increasing heat loss.
- The heat loss for plastic pipes of the same dimension is greater than that of steel pipes

## 11. Natural gas network
Back to user guide
11. Natural gas network
List of contents
11. Natural gas network
11.1 Natural gas transmission
11.2 Natural gas distribution
11.3 Biogas networks
11.4 Hydrogen networks
11.5 New technology 1
11.6 New technology 2
Assumptions applied (selected in 3.1 LCOE results)
Discount rate |  |  |  |  | 5% | %
Calculation period |  |  |  |  | 1
Start year of calculation |  |  |  |  | 2022
Electricity price development |  |  |  |  | Green
Expected solar thermal production |  |  |  |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  |  |  |  | Sustainable development scenario
Country |  |  |  |  | EU
Currency abbreviation |  |  |  |  | EUR
Currency factor |  |  |  |  | 1
Equipment |  |  |  |  | 1
Installation |  |  |  |  | 1
11.1 Natural gas transmission
11.1.1 Technical- and economic assumptions
Table 11-1: Technical- and economic assumptions for natural gas distribution lines [1]
Technology |  |  |  |  | Energy Transport, Natural Gas Main distribution line
2020
Energy/technical data
Energy losses, lines 1-20 MW (%) |  |  |  |  | 0.1
Energy losses, lines 20-100 MW (%) |  |  |  |  | 0.1
Energy losses, lines above 100 MW (%) |  |  |  |  | 0.1
Energy losses, stations [Type 1] (%) |  |  |  |  | -
Energy losses, stations [Type 2] (%) |  |  |  |  | 0.1
Auxiliary electricity consumption (% energy transmitted) |  |  |  |  | 0.005
Technical life time (years) |  |  |  |  | 50
Typical load profile (-) |  |  |  |  | 0.2
Construction time (years) |  |  |  |  | 1
Financial data
Investment costs
Investment costs; single line, 0 - 50 MW (EUR/MW/m) |  |  |  |  | 10.8
Investment costs; single line, 50-100 MW (EUR/MW/m) |  |  |  |  | 4.2
Investment costs; single line, 100 - 250 MW (EUR/MW/m) |  |  |  |  | 2.24
Investment costs; single line, 250-500 MW (EUR/MW/m) |  |  |  |  | 1.17
Investment costs; single line, 500-1000 MW (EUR/MW/m) |  |  |  |  | 0.68
Investment costs; single line, above 1000 MW (EUR/MW/m) |  |  |  |  | -
Reinforcement costs (EUR/MW) |  |  |  |  | -
Investment costs; [type 1] station (EUR/MW) |  |  |  |  | -
Investment costs; [type 2] station (EUR/MW) |  |  |  |  | 27000
Investments, percentage installation |  |  |  |  | 75
Investments, percentage materials |  |  |  |  | 25
Fixed O&M (EUR/MW/km/year) |  |  |  |  | 0.12099
Variable O&M (EUR/MWh/km) |  |  |  |  | 1.1255e-05
Financial data (EUR) |  |  | Unit
Investment costs |  |  | EUR/MW/m
Investment costs; single line, 0 - 50 MW |  |  | EUR/MW/m |  | 10.8
Investment costs; single line, 50-100 MW |  |  | EUR/MW/m |  | 4.2
Investment costs; single line, 100 - 250 MW |  |  | EUR/MW/m |  | 2.24
Investment costs; single line, 250-500 MW |  |  | EUR/MW/m |  | 1.17
Investment costs; single line, 500-1000 MW |  |  | EUR/MW/m |  | 0.68
Investment costs; single line, above 1000 MW |  |  | EUR/MW/m |  | #VALUE!
Reinforcement costs |  |  | EUR/MW |  | #VALUE!
Investment costs; [type 1] station |  |  | EUR/MW |  | #VALUE!
Investment costs; [type 2] station |  |  | EUR/MW |  | 27000
Investments, percentage installation |  |  | EUR/MW |  | 20250
Investments, percentage materials |  |  | EUR/MW |  | 6750
Fixed O&M |  |  | EUR/MW/km/year |  | 0.12099
Variable O&M |  |  | EUR/MWh/km |  | 1.1255e-05
11.2 Natural gas distribution
11.2.1 Technical- and economic assumptions
Table 11-2: Technical- and economic assumptions for natural gas distribution lines in rural areas [1]
Technology |  |  |  |  | Energy Transport Natural Gas Distribution, New distribution in existing rual areas |  | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy Transport Natural Gas Distribution, New distribution in existing city areas |  | Energy Transport Natural Gas Distribution, New developed residential areas
[5 empty] | 2020 |  | 2020 | 2020 |  | 2020
Energy/technical data
Energy losses, lines (%) |  |  |  |  | 0.26307 |  | 0.26307 | - |  | 0.26307
Energy losses, stations (%) |  |  |  |  | - |  | - | - |  | -
Auxiliary electricity consumption (% of energy delivered) |  |  |  |  | 0 |  | 0 | 0 |  | 0
Technical life time (years) |  |  |  |  | 50 |  | 50 | 50 |  | 50
Typical load profile (-) | [6 empty] | - |  |  | -
- Residential |  |  |  |  | 0.2 |  | 0 | 0.2 |  | 0.2
- Commercial |  |  |  |  | N/A |  | N/A | N/A |  | N/A
Construction time (years) |  |  |  |  | 0.4 |  | 0.4 | 0.4 |  | 0.4
Financial data
Distribution network costs (EUR/MWh/year), Rural |  |  |  |  | 140 |  | 150 | 10 |  | 270
Investment costs; service line, 0 - 20 kW (EUR/unit) |  |  |  |  | 1600 |  | 1600 | - |  | 1600
Investment costs; service line, 20 - 50 kW (EUR/unit) |  |  |  |  | - |  | - | - |  | -
Investment costs; service line, 50-100 kW (EUR/unit) |  |  |  |  | - |  | - | - |  | -
Investment costs; service line, above 100 kW (EUR/unit) |  |  |  |  | - |  | - | 15000 |  | -
Investment costs; single line, 0-50 kW (EUR/m) |  |  |  |  | 50 |  | 53.3333 | 64 |  | 46.6667
Investment costs; single line, 50-250 kW (EUR/m) |  |  |  |  | 50 |  | 53.3333 | 64 |  | 46.6667
Investment costs; single line, 100-250 kW (EUR/m) |  |  |  |  | 50 |  | 53.3333 | 64 |  | 46.6667
Investment costs; single line, 250 kW - 1 MW (EUR/m) |  |  |  |  | 50 |  | 53.3333 | 64 |  | 46.6667
Investment costs; single line, 1 MW - 5 MW (EUR/m) |  |  |  |  | 53.3333 |  | 60 | 72 |  | 50
Investment costs; single line, 5 MW - 25 MW (EUR/m) |  |  |  |  | 68.3333 |  | 86.6667 | 104 |  | 63.3333
Investment costs; single line, 25 MW - 100 MW (EUR/m) |  |  |  |  | - |  | - | - |  | -
Reinforcement costs (EUR/MW) |  |  |  |  | - |  | - | - |  | -
Type 1 station (EUR/MW) |  |  |  |  | - |  | - | - |  | -
Type 2 station (EUR/MW) |  |  |  |  | - |  | - | - |  | -
Investments, percentage installation |  |  |  |  | 0.8 |  | 0.8 | 0.8 |  | 0.8
Investments, percentage materials |  |  |  |  | 0.2 |  | 0.2 | 0.2 |  | 0.2
Fixed O&M (EUR/MW/year) |  |  |  |  | 750 |  | 310 | 20 |  | 920
Variable O&M (EUR/MWh) |  |  |  |  | 0 |  | 0 | 0 |  | 0
Financial data (EUR) |  |  | Unit
Distribution network costs |  |  | EUR/MWh |  | 140 |  | 150 | 10 |  | 270
Investment costs; service line, 0 - 20 kW |  |  | EUR/unit |  | 1600 |  | 1600 | --- |  | 1600
Investment costs; service line, 20 - 50 kW |  |  | EUR/unit |  | --- |  | --- | --- |  | ---
Investment costs; service line, 50-100 kW |  |  | EUR/unit |  | --- |  | --- | --- |  | ---
Investment costs; service line, above 100 kW |  |  | EUR/unit |  | --- |  | --- | 15000 |  | ---
Investment costs; single line, 0-50 kW |  |  | EUR/m |  | 50 |  | 53.3333 | 64 |  | 46.6667
Investment costs; single line, 50-250 kW |  |  | EUR/m |  | 50 |  | 53.3333 | 64 |  | 46.6667
Investment costs; single line, 100-250 kW |  |  | EUR/m |  | 50 |  | 53.3333 | 64 |  | 46.6667
Investment costs; single line, 250 kW - 1 MW |  |  | EUR/m |  | 50 |  | 53.3333 | 64 |  | 46.6667
Investment costs; single line, 1 MW - 5 MW |  |  | EUR/m |  | 53.3333 |  | 60 | 72 |  | 50
Investment costs; single line, 5 MW - 25 MW |  |  | EUR/m |  | 68.3333 |  | 86.6667 | 104 |  | 63.3333
Investment costs; single line, 25 MW - 100 MW |  |  | EUR/m |  | --- |  | --- | --- |  | ---
Reinforcement costs |  |  | EUR/MW |  | --- |  | --- | --- |  | ---
Type 1 station |  |  | EUR/MW |  | --- |  | --- | --- |  | ---
Type 2 station |  |  | EUR/MW |  | --- |  | --- | --- |  | ---
Investments, percentage installation |  |  | EUR/MW |  | 0.8 |  | 0.8 | 0.8 |  | 0.8
Investments, percentage materials |  |  | EUR/MW |  | 0.2 |  | 0.2 | 0.2 |  | 0.2
Fixed O&M |  |  | EUR/MW/year |  | 750 |  | 310 | 20 |  | 920
Variable O&M |  |  | EUR/MWh |  | 0 |  | 0 | 0 |  | 0
Table 11-3: Natural gas piping capacity [19]
NATURAL GAS PIPING CAPACITY |  |  |  |  | 1,000 CU. FT./HR CU. FT GAS
(1,000 FT²) AREA
BURIED PIPE |  | INLET PRESSURE ΔP/100 FT
DIAMETER (IN) | COST ($/LF) | 5 PSIG INLET WITH 1 PSIG DROP | 10 PSIG INLET WITH 1½ PSIG DROP | 30 PSIG INLET WITH 5 PSIG DROP | 60 PSIG INLET WITH 10 PSIG DROP
6 | $80/LF | 100 (1,000) | 140 (1,500) | 350 (3,700) | 650 (7,000)
4 | $50/LF | 35 (380) | 50 (520) | 120 (1,300) | 220 (2,300)
3 | $40/LF | 15 (160) | 25 (260) | 60 (640) | 100 (1,000)
2½ | $36/LF | 10 (100) | 13 (150) | 35 (380) | 35 (700)
2 | $32/LF | 6 (60) | 8 (85) | 20 (200) | 40 (400)
1½ | $30/LF | 3 (30) | 4 (40) | 10 (100) | 20 (200)
1 | $28/LF | 1 (10) | 1 (10) | 4 (40) | 7 (75)
NOTES: • Building SQFT values are based on 75 Btuh/ft2 peak average combined load (building heat and domestic hot water), and 80% combustion efficien- cy. For winter lows below +15°F: at 0°F multiply building SQFT by 0.8, at -20°F multiply building SQFT by 0.6. • Numbers shown are calculated for a nominal 400 ft run of pipe. • Prices shown are construction costs for direct buried pipe, including trench excavation, back fill, and pavement repair. For total project cost add A-E fees, testing, contingencies, etc. • The energy delivered to the system may be estimated at 1040 Btu/CF. Therefore, a capacity of 20,000 CF corresponds to (20,000 CF)*(1040 Btu/ CF), or 20,800,000 Btu. • The cost to provide a boiler or other heating equipment to a stand-alone (no steam) building is approximately $2 - $4 per square foot. • This chart is intended to be used for obtaining an initial estimate of required pipe size and cost. Actual system design must be based on values obtained specifically for the project.
11.3 Biogas networks
11.4 Hydrogen networks
Figure 11-5: Power-to-gas facility in Hobro
11.5 New technology 1
11.5.1 Technical- and economic assumptions
11.6 New technology 2
11.6.1 Technical- and economic assumptions
The role of the gas networks in the low carbon districts will be to distribute and store natural gas for back-up capacity for heat and power and to distribute renewable gas, e.g. biogas or gas generated from low cost electricity. The energy consumption related to operation of a gas network is generally low. The network is supplied with natural gas at a sufficiently high pressure, so no further compression is required in the main distribution lines or in the distribution system. Therefore, the electric power consumption related to operation of the main distribution lines and the distribution system is as low as 0.005 % of the transported energy. Reduction of the pressure in the system necessitates preheating, as the gas is cooled by the expansion. The heat is provided by burning an amount of gas corresponding to around 0.1 % of expanded gas. However, as there are different pressure levels in different parts of a system, preheating is not always required.
The gas system has a number of advantages. It can be supplied with gases from various sources, including green gases, such as upgraded biogas and gases from power-to-gas processes, as long as the gas meets the natural gas specifications. It also provides a large storage capacity. The Danish system contains 2-3 months of gas consumption. These properties may allow integration of large amounts of renewable energy in the energy system. Furthermore, the gas system can provide very high power capacity compared to most other energy carriers, which is required by some parts of the industry. The energy loss is very low compared to other energy distribution and transport systems. The main disadvantage is that today the cost of producing green gases of natural gas quality from e.g. renewable power production is relatively high. Therefore, the only green gas in the Danish gas system is upgraded biogas.
Natural gas networks have a minimal environmental impact during the construction phase. The environmental impacts during operation mainly consist of CO2 emissions due to preheating at MR stations and minor losses of mainly methane during distribution of the gas. There are no general data available on methane loss from the Danish gas system. If data from a European survey are applicable for the Danish system, the losses will correspond to 0.1 % of the amount of gas transported in gas networks. Yet, European gas networks are generally older than the Danish system.
Natural gas transmission systems are used to transport gas between countries and regions. The European natural gas transmissions network is shown.
While natural gas production has increased in the North Sea, most of the natural gas being used in Europe is imported via pipelines from Russia, Central Asia, the Middle East and even Africa. Additionally, there are 16 LNG regasification facilities located in Western Europe and more than 50 that are under consideration or construction. Imported natural gas is transported throughout the continent by a vast pipeline network.
A natural gas market/system typically consist of:
A wholesale market consisting of the transmission of gas from producers to the distribution network
A gas transmission system operated and owned by a TSO. The TSO is responsible for volume balancing in the natural gas system and for the management of gas supply in case of emergencies.
A gas distribution system where distribution companies are responsible for balancing and operating distribution systems in each geographical distribution area.
A storage system typically owned and operated by the TSO. The storage are collected in a company operated on commercial terms. The company sell products that allow the storage customer to store, inject and extract gas. The storage are in competition with other gas storage and providers of other flexibility services.
On the figure the three distribution companies in Denmark, which own and operate the distribution networks, are shown.
On the other hand, there are 16 gas suppliers. Natural gas customers can freely choose between these for the supply of natural gas
The retail market consists of distributing gas from the transmission network to consumers and retailing of gas to the final consumer.
The natural gas system must be a central energy carrier in the future renewable energy system, where hydrogen and biogas must also be integrated.
Biogas is produced by anaerobic digestion of biodegradable material. It consists mainly of 50-80 % methane and 20-50 % CO2. In addition, biogas contains low concentrations of undesirable substances, e.g. impurities, such as H2S, siloxanes, ammonia, oxygen and volatile organic carbons (VOC). In order to be injected into the natural gas network or in order to be used in gas vehicles, the upgraded biogas quality must meet the same requirements as natural gas. In Denmark, these requirements are described in the Gas Regulations, section C12. The methane limit is not directly specified in C12, but can be deduced from the lower wobbe limit, which is 50.8 MJ/Nm3 . This equals a minimum methane content of 97.3 % assuming the rest is CO2. H2S is limited to 5 mg/Nm3 . To avoid the risk of condensation, the water dew point up to 70 bar must be below minus 8 °C. A large number of technologies are available for upgrading, but four technologies stand out as the clearly most common technologies:
- Water scrubber
- Chemical scrubber (amine scrubber)
- Membrane scrubber
- PSA (Pressure Swing Absorption) scrubber.
Possible injection points are the following:
- Nearby 4 bar distribution network
- Nearby 19-40 bar distribution network
- Gas compression is needed before injection
- Nearby 80 bar gas transmission network. Gas compression is needed before injection.
The selection of injection point(s) depends on the following:
- Biogas plant capacity
- Local 4 bar gas distribution network base-load consumption
- Distance to nearby 4 bar gas distribution network
- Distance to nearby 19-40 bar gas distribution network
- Local 4 bar gas distribution network base-load consumption
- Distance to nearby 80 bar gas transmission network
- Cost of compression.
If the local gas consumption shows large variations during the day, a local intermediate storage facility can be used to increase the local consumption of biogas/upgraded biogas. Selection of entry point(s) will be based on an economic optimization.
It has become ever clearer that the resource of natural gas is an energy source that will be less important in the future due to limitations in natural reserves. In order to prepare for the future, the gas industry is looking at alternative gaseous fuels, one such fuel gas is hydrogen. Large reserves of natural gas are still discovered, which can contribute to about 50 % of the world energy mix for a longer time, but hydrogen gas is expected to become more and more available from converted wind energy via electrolysis. This gas can be fed to the natural gas network, and the whole gas network, including underground storage facilities, acts as a big buffer (Power to gas). Alternatively, existing gas networks are gradually converted to pure hydrogen transport systems. During preparation for a future use of hydrogen, it became evident that very little information exists regarding the compatibility between long-term exposure and transportation of hydrogen in polyethylene gas distribution pipelines. A program was, therefore, set to study the transportation in a small-scale pilot grid at the field test facilities of Danish Gas Technology Centre situated at the Scion-DTU research centre in Hoersholm, Denmark.
The results showed that 4 years (PE80) and 10 years (PE100) of continuous hydrogen exposure and subsequent laboratory tests based on international standards indicate no influence on PE80 or PE100 natural gas pipes’ durability.
Hydrogen is, like electricity, an energy carrier, which is only as clean as the energy source from which it is produced. Electrolysis can be used to enhance the value and thereby possibly the capacity of surplus energy produced from fluctuating renewable energy sources such as wind. In the operation of the electrolyser there are no environmental concerns.
The figures show the new power-to-gas facility in Hobro in Denmark.
https://www.dgc.dk/sites/default/files/filer/publikationer/C1703_IGRC2017_iskov.pdf

## 12. Electric network
Back to user guide
12. Electric network
List of contents
12. Electric network
12.1 Electric transmission network
12.2 Electric distribution network
12.3 Microgrid
12.4 New technology 1
12.5 New technology 2
Assumptions applied (selected in 3.1 LCOE results)
Discount rate |  |  |  |  | 5% | %
Calculation period |  |  |  |  | 1
Start year of calculation |  |  |  |  | 2022
Electricity price development |  |  |  |  | Green
Expected solar thermal production |  |  |  |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  |  |  |  | Sustainable development scenario
Country |  |  |  |  | EU
Currency abbreviation |  |  |  |  | EUR
Currency factor |  |  |  |  | 1
Equipment |  |  |  |  | 1
Installation |  |  |  |  | 1
12.1 Electric transmission network
12.1.1 Technical- and economic assumptions
Table 12-1: Technical- and economic assumptions for electric main distribution cables [1]
Energy Transport Electricity Main distribution, electricity cables
2020
Energy/technical data
Energy losses, lines 1-20 MW (%) |  |  |  |  | 0.3
Energy losses, lines 20-100 MW (%) |  |  |  |  | 0.3
Energy losses, lines above 100 MW (%) |  |  |  |  | 0.3
Energy losses, stations [Type 1] (%) |  |  |  |  | 0.2
Energy losses, stations [Type 2] (%) |  |  |  |  | N/A
Auxiliary electricity consumption (% energy transmitted) |  |  |  |  | N/A
Technical life time (years) |  |  |  |  | 40
Typical load profile (-) |  |  |  |  | 0.45
Construction time (years) |  |  |  |  | 1.5
Financial data
Investment costs; single line, 0 - 50 MW (EUR/MW/m) |  |  |  |  | 6
Investment costs; single line, 50-100 MW (EUR/MW/m) |  |  |  |  | 3.9
Investment costs; single line, 100 - 250 MW (EUR/MW/m) |  |  |  |  | 3.1
Investment costs; single line, 250-500 MW (EUR/MW/m) |  |  |  |  | N/A
Investment costs; single line, 500-1000 MW (EUR/MW/m) |  |  |  |  | N/A
Investment costs; single line, above 1000 MW (EUR/MW/m) |  |  |  |  | N/A
Reinforcement costs (EUR/MW) |  |  |  |  | 15800
Investment costs; [type 1] station (EUR/MW) |  |  |  |  | 76000
Investment costs; [type 2] station (EUR/MW) |  |  |  |  | 4476
Investments, percentage installation |  |  |  |  | 0.42
Investments, percentage materials |  |  |  |  | 0.58
Fixed O&M (EUR/MW/km/year) |  |  |  |  | 21.7906
Variable O&M (EUR/MWh/km) |  |  |  |  | N/A
Financial data (EUR) |  |  | Unit
Investment costs; single line, 0 - 50 MW (EUR/MW/m) |  |  | EUR/MW/m |  | 6
Investment costs; single line, 50-100 MW |  |  | EUR/MW/m |  | 3.9
Investment costs; single line, 100 - 250 MW |  |  | EUR/MW/m |  | 3.1
Investment costs; single line, 250-500 MW |  |  | EUR/MW/m |  | ---
Investment costs; single line, 500-1000 MW |  |  | EUR/MW/m |  | ---
Investment costs; single line, above 1000 MW |  |  | EUR/MW/m |  | ---
Reinforcement costs |  |  | EUR/MW |  | 15800
Investment costs; [type 1] station |  |  | EUR/MW |  | 76000
Investment costs; [type 2] station |  |  | EUR/MW |  | 4476
Investments, percentage installation |  |  | EUR/MW |  | 0.42
Investments, percentage materials |  |  | EUR/MW |  | 0.58
Fixed O&M |  |  | EUR/MW/km/year |  | 21.7906
Variable O&M |  |  | EUR/MWh/km |  | ---
12.2 Electric distribution network
12.2.1 Technical- and economic assumptions
Table 12-2: Technical- and economic assumptions for electric distribution in rural areas [1]
Technology |  |  |  |  | Energy Transport Electricity Distribution, Rural |  | Energy Transport Electricity Distribution, Suburban |  | Energy Transport Electricity Distribution, City |  | Energy Transport Electricity Distribution, New developed areas
[5 empty] | 2020 |  | 2020 |  | 2020 |  | 2020
Energy/technical data
Energy losses, lines (%) |  |  |  |  | 5.25 |  | 3 |  | 2.25 |  | 3
Energy losses, stations (%) |  |  |  |  | 1.125 |  | 1.125 |  | 1.125 |  | 1.125
Auxiliary electricity consumption (% of energy delivered) |  |  |  |  | N/A |  | N/A |  | N/A |  | N/A
Technical life time (years) |  |  |  |  | 40 |  | 40 |  | 40 |  | 40
Typical load profile (-) |  |  |  |  | 0.44 |  | 0.48 |  | 0.5 |  | 0.48
- Residential |  |  |  |  | 0.44 |  | 0.48 |  | 0.5 |  | 0.48
- Commercial |  |  |  |  | 0.44 |  | 0.48 |  | 0.5 |  | 0.48
Construction time (years) |  |  |  |  | 1 |  | 1 |  | 1 |  | 1
Financial data
Distribution network costs (EUR/MWh/year) Rural |  |  |  |  | 173 |  | 385 |  | 365 |  | 173
Investment costs; service line, 0 - 20 kW (EUR/unit) |  |  |  |  | 524 |  | 1436 |  | 2149 |  | 524
Investment costs; service line, 20 - 50 kW (EUR/unit) |  |  |  |  | 1412 |  | 4031 |  | 5618 |  | 1412
Investment costs; service line, 50-100 kW (EUR/unit) |  |  |  |  | 1583 |  | 4243 |  | 5774 |  | 1583
Investment costs; service line, above 100 kW (EUR/unit) |  |  |  |  | 3745 |  | 9066 |  | 12131 |  | 3745
Investment costs; single line, 0-50 kW (EUR/m) |  |  |  |  | N/A |  | N/A |  | N/A |  | N/A
Investment costs; single line, 50-250 kW (EUR/m) |  |  |  |  | N/A |  | N/A |  | N/A |  | N/A
Investment costs; single line, 100-250 kW (EUR/m) |  |  |  |  | 36 |  | N/A |  | N/A |  | 36
Investment costs; single line, 250 kW - 1 MW (EUR/m) |  |  |  |  | 36 |  | 75 |  | 115 |  | 36
Investment costs; single line, 1 MW - 5 MW (EUR/m) |  |  |  |  | 41 |  | 80 |  | 120 |  | 41
Investment costs; single line, 5 MW - 25 MW (EUR/m) |  |  |  |  | 88 |  | 128 |  | 169 |  | 88
Investment costs; single line, 25 MW - 100 MW (EUR/m) |  |  |  |  | N/A |  | N/A |  | N/A |  | N/A
Reinforcement costs (EUR/MW) (Station) |  |  |  |  | 11500 |  | 11500 |  | 11500 |  | 11500
Investment costs; [type 1] station (EUR/MW) |  |  |  |  | 67500 |  | 38000 |  | 38000 |  | 38000
Investment costs; [type 2] station (EUR/MW) |  |  |  |  | N/A |  | N/A |  | N/A |  | N/A
Investments, percentage installation (cables) |  |  |  |  | 0.62 |  | 0.8 |  | 0.86 |  | 0.8
Investments, percentage materials (cables) |  |  |  |  | 0.38 |  | 0.2 |  | 0.14 |  | 0.2
Investments, percentage installation (stations) |  |  |  |  | 0.22 |  | 0.14 |  | 0.05 |  | 0.14
Investments, percentage materials (stations) |  |  |  |  | 0.78 |  | 0.86 |  | 0.95 |  | 0.86
Fixed O&M (EUR/MW/year) |  |  |  |  | 1605.02 |  | 2643.8 |  | 0 |  | 1339.2617
Variable O&M (EUR/MWh) |  |  |  |  | N/A |  | N/A |  | N/A |  | N/A
Financial data (EUR) |  |  | Unit
Distribution network costs |  |  | EUR/MWh |  | 173 |  | 385 |  | 365 |  | 173
Investment costs; service line, 0 - 20 kW |  |  | EUR/unit |  | 524 |  | 1436 |  | 2149 |  | 524
Investment costs; service line, 20 - 50 kW |  |  | EUR/unit |  | 1412 |  | 4031 |  | 5618 |  | 1412
Investment costs; service line, 50-100 kW |  |  | EUR/unit |  | 1583 |  | 4243 |  | 5774 |  | 1583
Investment costs; service line, above 100 kW |  |  | EUR/unit |  | 3745 |  | 9066 |  | 12131 |  | 3745
Investment costs; single line, 0-50 kW |  |  | EUR/m |  | --- |  | --- |  | --- |  | ---
Investment costs; single line, 50-250 kW |  |  | EUR/m |  | --- |  | --- |  | --- |  | ---
Investment costs; single line, 100-250 kW |  |  | EUR/m |  | 36 |  | --- |  | --- |  | 36
Investment costs; single line, 250 kW - 1 MW |  |  | EUR/m |  | 36 |  | 75 |  | 115 |  | 36
Investment costs; single line, 1 MW - 5 MW |  |  | EUR/m |  | 41 |  | 80 |  | 120 |  | 41
Investment costs; single line, 5 MW - 25 MW |  |  | EUR/m |  | 88 |  | 128 |  | 169 |  | 88
Investment costs; single line, 25 MW - 100 MW |  |  | EUR/m |  | --- |  | --- |  | --- |  | ---
Reinforcement costs |  |  | EUR/MW |  | 11500 |  | 11500 |  | 11500 |  | 11500
Investment costs; [type 1] station |  |  | EUR/MW |  | 67500 |  | 38000 |  | 38000 |  | 38000
Investment costs; [type 2] station |  |  | EUR/MW |  | --- |  | --- |  | --- |  | ---
Investments, percentage installation (cables) |  |  | EUR/MW |  | 0.62 |  | 0.8 |  | 0.86 |  | 0.8
Investments, percentage materials (cables) |  |  | EUR/MW |  | 0.38 |  | 0.2 |  | 0.14 |  | 0.2
Investments, percentage installation (stations) |  |  | EUR/MW |  | 0.22 |  | 0.14 |  | 0.05 |  | 0.14
Investments, percentage materials (stations) |  |  | EUR/MW |  | 0.78 |  | 0.86 |  | 0.95 |  | 0.86
Fixed O&M |  |  | EUR/MW/km/year |  | 1605.02 |  | 2643.8 |  | 0 |  | 1339.2617
Variable O&M |  |  | EUR/MWh/km |  | --- |  | --- |  | --- |  | ---
Table 12-3: Underground high voltage distribution [19]
UNDERGROUND HIGH VOLTAGE DISTRIBUTION | [5 empty] | MW POWER
(1,000 FT²) AREA
[A] AMPACITY
WIRE |  |  |  |  | VOLTAGE, PHASE
WIRE SIZE (SETS) |  |  |  | COST | 5 KV RANGE | 15 KV RANGE
FOUR LOOPS 8@500 KCMIL |  |  |  | $510/LF | N/A | 32 (6,400) [1,480]
TWO LOOPS 4@500 KCMIL |  |  |  | $300/LF | N/A | 16 (3,200) [740]
ONE LOOP 2@500 KCMIL |  |  |  | $150/LF | 2.4 (490) [375] | 8 (1,600 EACH) [370 EACH]
ONE LOOP 2@350 KCMIL |  |  |  | $145/LF | 2 (410) [315] | 6.7 (1,340 EACH) [310 EACH]
ONE LOOP 2@250 KCMIL |  |  |  | $140/LF | 1.7 (340) [260] | 5.6 (1,120 EACH) [260 EACH]
RADIAL 500 KCMIL |  |  |  | $90/LF | 2.4 (480) [375] | 8 (1,600) [370]
RADIAL 350 KCMIL |  |  |  | $85/LF | 2 (400) [315] | 6.7 (1,340) [310]
RADIAL 250 |  |  |  | $80/LF | 1.7 (340) [260] | 5.6 (1,120) [260]
RADIAL 4/0 |  |  |  | $75/LF | 1.5 (300) [235] | 5.2 (1,040) [240]
RADIAL 2/0 |  |  |  | $72/LF | 1.2 (240) [185] | 4 (800) [185]
RADIAL 1/0 |  |  |  | $70/LF | 1 (200) [160] | 3.5 (700) [165]
RADIAL #1 |  |  |  | $68/LF | 0.9 (180) [140] | 3.1 (620) [145]
RADIAL #2 |  |  |  | $66/LF | 0.8 (160) [125] | 2.8 (560) [130]
NOTES: • Cables installed in UG ductbank, concrete encased ducts, 3 each. • Manhole every 500 feet. • Cost includes cable, duct, and trench excavation, backfill, and surface repair. • Cost does not include high voltage switch at each point of use ($40,000 - $50,000 each), manhole or pull box, splicing and termination. • Cable is single conductor, copper shielded, 100% insulation level high voltage cable. • Each duct contains 3 H.V. cables and a ground conductor sized per NEC. • Prices shown are the construction costs for direct buried wire, including trench excavation, backfill, and moderate pavement repair. For total project cost add A-E fees, testing, contingencies, etc. • This chart is intended to be used for obtaining an initial estimate of required wire size and cost. Actual system design must be based on values obtained specifically for the project. For radial systems, building area power usage is estimated at 5 W/ft2. For loop systems, building area power usage is estimated at 3 W/ft2 (central plant loads not included).
12.3 Microgrid
Figure 12-1: Microgrid with centralized emergency generators and a building level back-up | [6 empty] | Figure 12-2: Microgrid with centralized emergency generators and a centralized storage
Figure 12-3: Microgrid with centralized emergency generators and CHP plant | [6 empty] | Figure 12-4: Microgrid with centralized emergency generators, RE sources and a
centralized storage
Figure 12-5: Microgrid with centralized emergency generators | [6 empty] | Figure 12-6: Microgrid with decentralized emergency generators and CHP
Figure 12-7: Microgrid with decentralized emergency generators
Archtiecture Name | Description |  | Micro-grid? | Must Contain | May Contain |  | Capabi-lities | Applications |  | Advantages |  | Disadvantages
Base Case | Dedicated building-level backup generators serve critical loads when utility power is unavailable. |  | DOE - No IEEE-Yes | Building-Level Control, Building-Level Backup Generators | Various power sources such as photovoltaic, energy storage |  | Dedicated generators to critical loads | Basic critical load backup power |  | None - Base Case |  | Lack of redundancy, if backup generation source fails or there is a lack of fuel, the building will lose power.
Central Power Plant (Base Loading) | A central plant serves installation loads or supplements utility power service installation loads |  | No | Distribution-Level Control, Distribution-Level CUP | Various power sources such as photovoltaic, energy storage |  | Offset installation power consumption | Installation-scale power production |  | Provides a portion of primary power which can result in less electric cost |  | Centralized plants are costly, and must be competitive with utility provider to be sustainable; if centralized plant is lost then the associated buildings served will be lost since it is a single point of failure;
Central Backup Generators | A backup generator plant connected at the distribution level serves critical loads when utility power is not available. |  | DOE - No IEEE-Yes | Distribution-Level Control, Distribution-Level Backup Generator Plant, | distribution and building level remote controlled disconnect switch,Various power sources such as photovoltaic, energy storage |  | More efficiency backup power with more flexilibyt that dedicated building generators | More efficient and reliable critical load backup power for multiple facilities. Typically seen when multiple critical buildings are located geographically close to one another. |  | Less expensive than central plant for installation loads. May be less expensive than backup generators at individual facilities. |  | Like central plant one backup generator plant is a single point of failure; unlike central plant it only picks up power when utility power unavailable
Islandable Central Plants | A central utlity plant serves installation loads and can operate islanded from utility power |  | Yes | Control System and Network, Distribution-Level Control, Distribution-Level CUP | Distribution-Level Backup Generators,Various power sources such as photovoltaic, energy storage |  | Islandable power for large installation loads, offset installation power consumption | Installation-scale power production and support for power outage ride-through. |  | Can provide all of primary power if competitive with utility and consolidates backup power requirements at one location so may be less expensive and easier to maintain than distributed generators spread across the service area and can operate in parallel with the utility |  | Even more expensive than that ot the central plant since additional generation is needed and paralleling switchgear to operate the system in parallel with the utility. Has the same disadvantages of being a single point of failure if central plant is lost.
Distribution-Level Microgrid | Generation resources connected to the distribution system at medium voltage serve installation loads and can operate islanded from utility power |  | Yes | Control System and Network, Distribution-Level Control | Distribution-Level CUP, D-L Backup Generators, D-L Solar, D-L Energy Storage |  | Improved efficiency, runtime, flexibility, and resiliency through integration of multiple types of generation for backup power. | Integration of multiple large resources into backup power service for critical loads. Typically done when installation has multiple substations |  | Generators connected along distribution at medium voltage instead of at individual facilities is easier to operate, since they are not necessarily centralized, may avoid single point of failure issues, may be less costly than central plant installations but may not be as efficient; generation resources decoupled from individual facilities relieves the necessity to keep backup generators at individual facilities |  | Since genreation is distributed cost for control infrastructure is high as well as the complexity of the controls themselves, even though a larger variety of sizes of power sources makes the matching load to generation more optimized and efficient the larger the number of spares are needed, since electrical power can flow in bidirectional instead of unidirectional which is typically seen in distribution systems the protection scheme becomes more complex and costly.
Distributed Microgrid | Generation resrouces connected at the distribution-level and building-level serve installation loads and can operated islanded from utility power |  | Yes | Control System and Network, Distribution-Level Control | Distribution-Level CUP, D-L Backup Generators, D-L Solar, D-L Energy Storage, Building-Level Controls, B-L Generators, B-L Solar, B-L Energy Storage, B-L CHP |  | Improved efficiency, runtime, flexibility, and resiliency through integration of multiple types of generation for backup power. | Integration of multiple generation resrouces, including backup generators previously dedicated to individual buildings, into backup power service for critical loads. Typically done at factilities with dedicated building generators with grid paralleling capability |  | Adds benefit relative to distribution only generation resources of utilizing building level generators as well so may be less expensive; as with distribution resources less efficient than central plants |  | Same disadvantages as the Distribution-Level Microgrid\
Single-Building Microgrid | Generation resrouces connected to a single building serve that building's loads and can operate the single building islanded from the distribution system |  | Yes | Control System and Network, Building-Level Control | B-L Generators, B-L Solar, B-L Energy Storage, B-L CHP |  | Improved efficiency, runtime, flexibility, and resiliency through integration of multiple types of generation for backup power. | Integrating building-level generation resrouces into backup power service for the building. |  | Adds to single building tied backup generator to increase reliability and resilience through redundancy of the additional generation resources |  | More expensive than building tied backup generation; more complex controls.
Low-Voltage Microgrid | Multiple single-building microgrids use the low-voltage distrubtion system to share generation resrouces and operated islanded from utility power. |  | Yes | Control System and Network, Distribution-Level Control, Building-Level Control | B-L Generators, B-L Solar, B-L Energy Storage, B-L CHP,Various power sources such as photovoltaic, energy storage |  | Improved efficiency, runtime, flexibility, and resiliency through integration of multiple types of generation for backup power. Multiple building collaboration further improves flexilibtiy, efficiency, and resiliency. | Integrating mutliple building-level microgrids to improve redudnancy and efficiency for building backup power service. Typically done when buildings are within very close proximity of each other and very low load demand. |  | Adds benefit by utilizing building level generators and not distribution level generators so may be less expensive than either distribution level generators or a combination of both; as with distribution resources less efficient than central plants |  | Less expensive than individual facility installations but will have more complex controls since more diverse set of generators needs to be controlled. Since power is being sent along the low voltage system, larger electrical feeders are needed which increases costs. Buildings need to be closely located to one another to minimize voltage drop and cost of electrical wire.
|  |  |  | Base Case | Central Plant | Central Backup | Islandable Plants | Distribution Level Microgrid | Distributed Microgrid | Single Building Microgrid* | Low Voltage Microgrid
Control System and Network | [6 empty] | x | x | x | x | x
Distiribtuion Break/Switch Control |  |  |  |  | x | x | x | x | x |  | x
CUP |  |  |  |  | x |  | x | o | o
Distribution Backup Generators | [5 empty] | x | o | o | o
Distribution solar | [7 empty] | o | o
Distribution energy stroage | [7 empty] | o | o
Building Level Breaker/Switch Control |  |  |  | x |  |  |  |  | o | x | x
Building Backup Generators |  |  |  | x |  |  |  |  | o | o | o
Building Solar | [8 empty] | o | o | o
Building Energy storage | [8 empty] | o | o | o
Building CHP | [8 empty] | o | o | o
x - must contain
o - may contain
*Single Building Microgrid contains one or more of these resources located at a single building
Equipment |  | Rating |  | Cost (range) + (range)* |  | Cost Format |  | Reference |  | Additional Cost Items
Small Diesel Generator |  | 30 - 150 kW |  | (356 - 526) |  | $/kW |  | Ref (1) |  | Site prep, installation, testing, commissioning, controls programming
Medium Diesel Generator |  | 150 - 500 kW |  | (238 - 356) |  | $/kW |  | Ref (1) |  | Site prep, installation, testing, commissioning, controls programming
Large Diesel Generator |  | 500 kW - 1MW |  | (223-238) |  | $/kW |  | Ref (1) |  | Site prep, installation, testing, commissioning, controls programming
Extra Large Diesel Generators |  | > 1 MW |  | 550 |  | $/kW |  | Ref (4) |  | Site prep, installation, testing, commissioning, controls programming
Small NG Generator |  | 7.5 - 60 kW |  | (483 - 1586) |  | $/kW |  | Ref (1) |  | Site prep, installation, testing, commissioning, controls programming
Medium NG Generator |  | 60 - 185 kW |  | (454 - 483) |  | $/kW |  | Ref (1) |  | Site prep, installation, testing, commissioning, controls programming
Large NG Generator |  | >1 MW |  | (700 - 1000) |  | $/kW |  | Ref (4) |  | Site prep, installation, testing, commissioning, controls programming
Generator belly tank - Small Gen |  | <100 kW |  | N/A - these are included with generator package costs |  | $/gal |  | N/A |  | Including any site provisions
Generator belly tank - Medium Gen |  | 100 - 750 kW |  | N/A - these are included with generator package costs |  | $/gal |  | N/A |  | Including any site provisions
Generator belly tank - Large Gen |  | 750 kW - 2MW |  | N/A - these are included with generator package costs |  | $/gal |  | N/A |  | Including any site provisions
Generator belly tank - Extra Large Gen |  | > 2 MW |  | N/A - these are included with generator package costs |  | $/gal |  | N/A |  | Including any site provisions
Building-Mounted PV Array + Inverter |  |  |  | (1000 - 1500) |  | $/kW |  | Ref (4) |  | Including wiring, combiner boxes, mounting structure, interver, building electrical interface
Ground-Mounted PV Array + Inverter |  |  |  | (1000 - 1500) |  | $/kW |  | Ref (4) |  | Including wiring, combiner boxes, mounting structure, interver, electrical interface
Carport PV Array |  |  |  | 600-800 |  | $/kW |  | Ref (5) |  | Including wiring, combiner boxes, mounting structure, interver, electrical interface
PV inverter |  |  |  | 400-1000 |  | $/kW |  | Ref (5) |  | Equipment, installations, programming
Generic Battery Energy Storage System | [5 empty] | $/kW + $/kWh |  |  |  | inclusive of all safety systems such as fire supression that meets code and UFCs
Lithium battery energy storage systems |  |  |  | (1263 - 2162) + (829 - 1152) |  | $/kW + $/MWh |  | Ref (2 )- pg13, 26, 27 |  | inclusive of all safety systems such as fire supression that meets code and UFCs
Lead-Acid Battery energy storage systems |  |  |  | (1278 - 1763) + (108 -1225) |  | $/kW + $/MWh |  | Ref (2 )- pg13, 26, 27 |  | inclusive of all safety systems such as fire supression that meets code and UFCs
Flow Battery Energy storage system |  |  |  | (1715 - 3650) + (115 - 167) |  | $/kW + $/MWh |  | Ref (2 )- pg13, 26, 27 |  | inclusive of all safety systems such as fire supression that meets code and UFCs
Flywheel Energy Storage Systems |  |  |  | (1300-2000) + (1000-3000) |  | $/kW + $/kWh |  | Ref (5) |  | inclusive of all safety systems such as fire supression that meets code and UFCs
Capacitor Energy Storage Systems | [5 empty] | $/kW + $/kWh |  |  |  | inclusive of all safety systems such as fire supression that meets code and UFCs
CUP | [5 empty] | $/kW |  |  |  | turn-key power plant cost
Gasifier | [5 empty] | $/kW |  |  |  | turn-key power plant cost
Fuel Storage (Diesel) above ground |  |  |  | (2 - 4) |  | $/gal |  | Ref (4) |  | inclusive of civil work, equpment, installation, and commissioning
Fuel Storage (NG/propane) above ground |  |  |  | (3 - 5) |  | $/gal |  | Ref (4) |  | inclusive of civil work, equpment, installation, and commissioning
Fuel Storage (JP8) above ground |  |  |  | similar to 27 |  | $/gal |  |  |  | inclusive of civil work, equpment, installation, and commissioning
Fuel Storage (Diesel) below ground |  |  |  | likely 2x above ground costs |  | $/gal |  |  |  | inclusive of civil work, equpment, installation, and commissioning
Fuel Storage (NG) below ground |  |  |  | likely 2x above ground costs |  | $/gal |  |  |  | inclusive of civil work, equpment, installation, and commissioning
Fuel Storage (JP8) below ground |  |  |  | likely 2x above ground costs |  | $/gal |  |  |  | inclusive of civil work, equpment, installation, and commissioning
Equipment |  | Rating |  | Cost (range) + (range)* |  | Cost Format |  | Reference |  | Additional Cost Items
Medium Voltage Overhead Power Lines (~15kv) |  |  |  | 20 |  | $/ft |  | Ref (4) |  | inclusive of civil work, equpment, installation, and commissioning
Medium Voltage Underground Power Lines (~15kv) |  |  |  | 50 |  | $/ft |  | Ref (4) |  | inclusive of civil work, equpment, installation, and commissioning
MV pole-mount transformer (~15kV/208V) |  | 10 - 100 kVA |  | (55 -186) |  | $/kVA |  | Ref (1) |  | inclusive of civil work, equpment, installation, and commissioning
MV pad-mount transformer (~15kV/208V) |  | 150 -3750 kVA |  | (29 - 93) |  | $/kVA |  | Ref (1) |  | inclusive of civil work, equpment, installation, and commissioning
Substation Transformers (~69kV/~15kV) |  |  |  | (26 - 33) |  | $/kVA |  | Ref (1) |  | inclusive of civil work, equpment, installation, and commissioning
Substation Transformers (~115kV/~15kV) |  |  |  | 24 |  | $/kVA |  | Ref (1) |  | inclusive of civil work, equpment, installation, and commissioning
Substation Breaker (~15kV) |  |  |  | 76890 |  | $/ea |  | Ref (1); oil breaker |  | inclusive of civil work, equpment, installation, and commissioning
Pad-mounted Breaker (~15kV) |  |  |  | similar to 41 |  | $/ea |  |  |  | inclusive of civil work, equpment, installation, and commissioning
Pole-mounted Breaker (~15kV) |  |  |  | similar to 41 |  | $/ea |  |  |  | inclusive of civil work, equpment, installation, and commissioning
Low Voltage Breaker (208V) |  | 650 - 2500 kVA |  | (960 - 1850) |  | $/ea |  | Ref (1) |  | inclusive of civil work, equpment, installation, and commissioning
MV pole-mounted switch (~15kV) |  |  |  | similar to 46 |  | $/ea |  |  |  | inclusive of civil work, equpment, installation, and commissioning
MV pad-mount switch (~15kV) |  |  |  | 20915 |  | $/ea |  | Ref (1); manual gang operated switch |  | inclusive of civil work, equpment, installation, and commissioning
Multi-way MV pad-mount switch (~15kV) |  |  |  | similar to 46 |  | $/ea |  |  |  | inclusive of civil work, equpment, installation, and commissioning
Multi-way MV pole-mount switch (~15kV) |  |  |  | similar to 46 |  | $/ea |  |  |  | inclusive of civil work, equpment, installation, and commissioning
ATS - Small Generator |  | <100 kW |  | 5220 |  | $/ea |  | Ref (1) |  | inclusive of civil work, equpment, installation, and commissioning
ATS - Medium Generator |  | 100 - 750 kW |  | (5220 - 20475) |  | $/ea |  | Ref (1) |  | inclusive of civil work, equpment, installation, and commissioning
ATS - Large Generator |  | 750 kW - 1.5MW |  | (20475 - 35275) |  | $/ea |  | Ref (1) |  | inclusive of civil work, equpment, installation, and commissioning
ATS - Extra Large Generator |  | > 2 MW |  | >35275 |  | $/ea |  | extrapolation from Ref (1) |  | inclusive of civil work, equpment, installation, and commissioning
Motor Operator for HV Breaker (69kV) |  |  |  | N/A - these are included with breaker costs |  | $/ea |  |  |  | equipment, installation, test
Motor Operator for MV Breaker (15kV) |  |  |  | N/A - these are included with breaker costs |  | $/ea |  |  |  | equipment, installation, test
Motor Operator for LV Breaker (208kV) |  |  |  | N/A - these are included with breaker costs |  | $/ea |  |  |  | equipment, installation, test
UPS |  |  |  | 1000 - 2000 |  | $/kW |  | Ref (4) |  | equipment, installation, test
Equipment |  | Rating |  | Cost (range) + (range)* |  | Cost Format |  | Reference |  | Additional Cost Items
Microgrid Supervisory Controller |  |  |  | 700-3000** |  | $/ea |  | Ref (5) |  | Including supporting equipment, installation, programming, testing, hardening and commissioning
Microgrid HMI terminal |  |  |  | 700-3000** |  | $/ea |  | Ref (5) |  | Hardware, software, programming, hardening, test, commissioning
SCADA gateway |  |  |  | 400-2000** |  | $/ea |  | Ref (5) |  | Hardware, software, programming, hardening, test, commissioning
SCADA RTU |  |  |  | 500-2000** |  | $/ea |  | Ref (5) |  | Hardware, software, programming, hardening, test, commissioning
SCADA PLC |  |  |  | 500-2000** |  | $/ea |  | Ref (5) |  | Hardware, software, programming, hardening, test, commissioning
Generator paralleling control |  |  |  | 100000-200000 |  | $/ea |  | Ref (4) |  | Hardware, software, programming, hardening, test, commissioning
Control System to Subsystem Interface | [5 empty] | $/ea |  |  |  | Physical connection, programming, hardening, test, commissioning
New Trenched Fiber Cable Enclosure |  | 1 - 2 inches |  | (6.0 - 12.3) |  | $/ft |  | Ref (1) |  | inclusive of civil work, equpment, installation, and commissioning
New Fiber Cable in Existing Conduit |  | 48 strand |  | 6.2 |  | $/ft |  | Ref (1) |  | inclusive of civil work, equpment, installation, and commissioning
OH Pole Hung New Fiber Cable | [5 empty] | $/ft |  |  |  | inclusive of civil work, equpment, installation, and commissioning
Router |  |  |  | 1000-50000** |  | $/ea |  | Ref (5) |  | Equipment, programming, hardening, test, commissioning
Network switch |  |  |  | 500-50000** |  | $/ea |  | Ref (5) |  | Equipment, programming, hardening, test, commissioning
Network Firewall |  |  |  | 1000-100000** |  | $/ea |  | Ref (5) |  | Equipment, programming, hardening, test, commissioning
Recommission SCADA after modifcation | [5 empty] | $/ea
Equipment |  | Rating |  | Cost (range) + (range)* |  | Cost Format |  | Reference |  | Additional Cost Items
Conventional Generation (diesel, gas) |  |  |  | (833 - 1641) |  | $/kW |  | Ref (3) page 26 (utility, commerical & military microgrids)
Renewable Generation (PV, Wind) |  |  |  | (502 - 663) |  | $/kW |  | Ref (3) page 26 (utility, commerical & military microgrids)
Energy Storage |  |  |  | (248 - 351) |  | $/kW |  | Ref (3) page 26 (utility, commerical & military microgrids)
Controls |  |  |  | (48 - 162) |  | $/kW |  | Ref (3) page 26 (utility, commerical & military microgrids)
Additional Infrastructure (new switches, lines) |  |  |  | (191 - 459) |  | $/kW |  | Ref (3) page 26 (utility, commerical & military microgrids)
Soft Costs (Engineering, Construction, Commissioning, Regulatory) |  |  |  | (102 - 1655) |  | $/kW |  | Ref (3) page 26 (utility, commerical & military microgrids)
*example 1000-1500 + 300-400 for $/kW + $/KWh means range is ($1000-$1500)/kW + ($300-$400)/kWh
(1) RSMeans Electricity Costs 2019
(2) Lazard's Levelized Cost of Storage Analysis - Version 4.0
(3) Phase I Microgrid Cost Study (NREL/TP-5D00-67821; October 2018)
(4) Information from previous Sandia microgrid projects & consultation with manufacturers
(5) Information obtained from online searches
**Cost of these items largely depend on the size purchased
12.4 New technology 1
12.4.1 Technical- and economic assumptions
12.5 New technology 2
12.5.1 Technical- and economic assumptions
Electricity from power plants, wind turbines and solar cells is transported from manufacturer to consumer through the grid. The main electricity transmission network consisting of 400 kV and 150/132 kV transmission lines is owned and operated by the national TSO. The underlying distribution networks are operated and owned by local distribution companies. At European level, efforts are being made to integrate all countries in Europe into one single electricity market. This means that the market areas must be connected even stronger with electrical transmission lines. The European electricity network can be seen here:
https://www.entsoe.eu/Documents/Publications/maps/Map_Continental-Europe-2.pdf
In any electrical system, a player is required for the overall stability of the network - which means that both import and export, as well as frequency and voltage must remain within agreed limits. This player is called the system-responsible company or transmission system operator (TSO). In order to ensure that the balance between purchase and sale of electricity is constantly maintained, selected players in the electricity market have the status of "balance responsible player". All production, consumption and trade of electricity must be affiliated with a balance-responsible player. In practice, this role can be transferred to other balancing actors. For example, if the electricity vendor is not the sole responsibility of the balance, the balance is guaranteed through a purchase agreement with another balance responsible player. Liberalization of the electricity sector introduced competition between manufacturers and suppliers. These players act together in the wholesale market. Due to its status as a natural monopoly, the transmission network is not competitive.
The advantage of a liberalized electricity market is, among many, that electricity is always produced at the lowest cost, that transmission capacity between market areas is implicitly allocated and electricity flows from high-price areas to low-price areas.
The electricity systems of the future will presumably change from a central system with conventional thermal condensing- and CHP plants to a decentralized system based on wind and solar power and smaller CHP plants. To ensure a high security of supply, when domestic conventional production capacity is reduced, and to develop a common European electricity market, new power cables are built. The increased electricity consumption from heat pumps, electric boilers, data centers and electric vehicles must be covered by higher output from renewable energy production.
We believe that we will see the following trends:
- Large central power plants are decommissioned, mothballed or converted to biomass with reduced power capacity.
- Wind turbines and solar cells gradually replace the conventional power plants.
- The number of individual heat pumps and large-scale heat pumps and electric boilers increases and enables a more flexible electricity consumption.
- Electrification of the transport sector is currently stagnant, but will occur.
- New transmission lines will be built, and the existing ones expanded.
The electric distribution networks are typically owned and operated by a local distribution system operator (DSO). The DSO´s are monopolies and are subject to a non-profit regulation. Most countries also benchmark the DSO´s against each other in order to achieve reduced operating costs for the benefit of consumers.
A microgrid is a localized group of electricity sources and loads that normally operates connected to and synchronous with the traditional wide area synchronous grid (macrogrid), but can also disconnect to "island mode" — and function autonomously as physical or economic conditions dictate. In this way, a microgrid can effectively integrate various sources of disitrbuted generation (DG), especially renewable energy sources (RES) - renewable electricity, and can supply emergency power, changing between island and connected modes.
Control and protection are challenges to microgrids. A very important feature is also to provide multiple end-use needs as heating, cooling, and electricity at the same time since this allows energy carrier substitution and increased energy efficiency due to waste heat utilization for heating, domestic hot water, and cooling purposes (cross sectoral energy usage).
Onthe following figures are we presenting a list of microgrids in different configurations:
- Microgrid with centralised emergency generators and a building level back-up
- Microgrid with centralised emergency generators and a centralized storage
- Microgrid with centralised emergency generators and CHP
- Microgrid with centralised emergency generators, RE sources and a centralized storage
- Microgrid with centralised emergency generators
- Microgrid with decentralised emergency generators and CHP
- Microgrid with decentralised emergency generators
See also: https://en.wikipedia.org/wiki/Microgrid
All data below is provided by US Army Corps of Engineers.

## 13. HVAC
Back to user guide
13. HVAC
Figure 13-1 HVAC facilities
List of contents
13. HVAC
13.1 Heat exchangers (building level)
13.2 Central heating
13.3 Ventilation system
13.4 Ventilation with heat recovery
13.5 Hot tap water system
13.6 Hydronic balancing
13.7 New technology 1
13.8 New technology 2
Assumptions applied (selected in 3.1 LCOE results)
Discount rate |  |  |  | 5% | %
Calculation period |  |  |  | 1
Start year of calculation |  |  |  | 2022
Electricity price development |  |  |  | Green
Expected solar thermal production |  |  |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  |  |  | Sustainable development scenario
Country |  |  |  | EU
Currency abbreviation |  |  |  | EUR
Currency factor |  |  |  | 1
Equipment |  |  |  | 1
Installation |  |  |  | 1
13.1 Heat exchangers (building level)
Figure 13-2: District heating substations
13.1.1 Technical- and economic assumptions
Table 13-1: District heating substation price [14]
Nominal capacity | Price | Unit price
Reference
kW | EUR | EUR/kW
30 | 10298.2527 | 343.2751
47 | 13257.3925 | 282.0722
103 | 14577.957 | 141.5336
177 | 20057.7957 | 113.3209
193 | 20860.7527 | 108.0868
302 | 25085.7527 | 83.0654
607 | 36331.4516 | 59.8541
963 | 43982.9301 | 45.6728
Figure 13-3: District heating substation price
13.2 Central heating
Figure 13-4: Central heating principle and floor heating
13.2.1 Technical- and economic assumptions
Table 13-2: Hot water tank price [14] |  |  | Table 13-4: Pipes in buildings price [14]
Tank capacity | Price | Unit price | Pipe dimension | Price
Reference | Ramboll |  | Reference | Ramboll
liter | EUR | EUR/liter | DN | €/m | EUR/m
650 | 4942.6667 | 7.6041 | DN 10 | 132.1333 | 132.1333
800 | 5022.6667 | 6.2783 | DN 15 | 135.0667 | 135.0667
800 | 5022.6667 | 6.2783 | DN 20 | 138 | 138
1250 | 6314.6667 | 5.0517 | DN 25 | 140.9333 | 140.9333
2000 | 7549.3333 | 3.7747 | DN 32 | 156 | 156
2200 | 7949.3333 | 3.6133 | DN 40 | 158 | 158
2500 | 8402.6667 | 3.3611 | DN 50 | 164.8 | 164.8
|  |  | DN 65 | 158.5333 | 158.5333
Table 13-3: Radiator and floor heating price [14] |  |  | DN 80 | 178.5333 | 178.5333
| Radiator | Floor heating | DN 100 | 210.4 | 210.4
Reference | Ramboll
| €/m2 | €/m2
Value | 666.6667 | 80
Life-time | 50 | 50
| Radiator | Floor heating
Figure 13-5: Hot water tank price
Reference | Ramboll
| EUR/m2 | EUR/m2
Value | 666.6667 | 80
13.3 Ventilation system
Figure 13-6: Ventilation system
13.4 Ventilation with heat recovery
Figure 13-7: Central ventilation with heat recovery
13.5 Hot tap water system
Figure 13-8: Flat station
Figure 13-9: Domestic hot water storage tank
13.6 Hydronic balancing
13.7 New technology 1
13.7.1 Technical- and economic assumptions
13.8 New technology 2
13.8.1 Technical- and economic assumptions
The HVAC (Heating, Ventialtion, Air Conditioning) installations in the buildings are an important part of the energy system for the following reasons:
- Efficient regulation to provide good thermal comfort
- Efficient regulation to avoid waste of heat or cold
- Ability to use low temperature sources for heating, e.g. supply 70 dgr.C
and return 40 dgr.C
- Ability to use high temperature sources for cooling, e.g. supply 10 dgr.C
and return 15 dgr.C
- Ability to deliver hot tap water without any risk of legionella
- Ability to deliver resilient cooling to servers and oher vital installations
Efficient HVAC installations is a precondition for using efficient sources for heating and cooling, both at the building level and via DH and DC.
HVAC is an important part of residential structures such as single family homes, apartment buildings, hotels and senior living facilities, medium to large industrial and office buildings such as skyscrapers and hospitals, on ships and submarines, and in marine environments, where safe and healthy building conditions are regulated with respect to temperature and humidity, using fresh air from outdoors.
The district heating substation is placed at the end user with the purpose of preparing domestic hot water and delivering heat for the space heating system based on district heating. Each building with a district heating substation is supplied from a branch pipe connecting the building to the overall distribution network.
The substation is equipped with a domestic hot water heater based on either a storage tank or a heat ex-changer without storage, e.g. a plate heat exchanger. In some cases, a combination of an external heat exchanger and a storage tank is seen. The space heating is delivered by direct supply of district heating water or by a heat exchanger placed in between the district heating water (primary side) and the space heating water (secondary side). Further, the substation includes all valves, controllers, filters, pumps, etc. that are necessary for the operation .
In large buildings, the substation can be placed centrally, or small substations, the so-called flat stations, can be placed in each flat.
The figure on the next page shows the price of a district heating substation
depending on the nominal transfer capacity. Prices are based on
experience from the VEKS Køge district heating project from 2016 and includes materials and work, including the preparation of existing boiler rooms
for district heating, the district heating substation, new hot water tank,
new pumps on the building side and a new expansion valve as well as installation.
Thus, the price estimate is not for new buildings, but we still assume that one needs to prepare a technology room for installation in new buildings. We therefore use the unit prices shown for the district heating substations. Prices are for a fixed temperature set. It is therefore not reflected in the price that a larger surface in the heat exchanger is required at very low district heating temperatures (low ΔT).
Central heating is a heating system where the heat is produced a central place in the building and from there distributed to the rooms to be heated. Most buildings now have central heating, which means that heating systems are more often referred to as energy forms, eg. oil boiler or electric heating, or by means of supply, e.g district heating, or by distribution, such as air heating.
Heating by open fire has been known since prehistoric times, but the distribution of heat from a central location has been a problem. With the knowledge of steam properties and the emergence of steel and copper pipes, there was a new possibility for transport of heat. The steam pressure, even over long distances, can be used to transport the hot steam through a pipeline to radiators in each room in a building. The same type of plant with a pipe grid and radiators also proved to be useful with hot water. Yet, here this is certainly not a driving force in terms of pressure, but since hot water has a lesser density than cold water, circulation can be maintained by the hot water rising up in the system and the cooled water going downward. This form of construction has contributed to the widespread dissemination of central heating; the same applies for the introduction of circulation pumps, which has allowed the use of small pipe dimensions with a smooth pipeline to follow.
To a certain extent, central heating is also used in the form of air heating systems, where the advent of fans has made it easy to transport the hot air to the rooms. Especially in cases where a part of the year cooling is required air-conditioning systems have an advantage over installations with water.
The figure on the next page shows the price of a large hot water tank
based on our experience with WPH prices. It requires reasonable
detailed knowledge of the hot water consumption in the building to
design the container optimally. The price includes investment in tha hot water tank, insulation of the cover, pressure thermometer, air discharge, safety valve and on-site welding. We have also inserted our estimate on the cost of pipes in buildings, radiators and floor heating. the cost estimates are very uncertain and depends on will in reality vary for each building.
In many instances, ventilation for indoor air quality is simultaneously beneficial for the control of thermal comfort. At these times, it can be useful to increase the rate of ventilation beyond the minimum required for indoor air quality. Two examples include air-side economizer strategies and ventilation pre-cooling. In other instances, ventilation for indoor air quality contributes to the need for - and energy use by - mechanical heating and cooling equipment. In hot and humid climates, dehumidification of ventilation air can be a particularly energy intensive process.
Ventilation should be considered for its relationship to "venting" for appliances and combustion equipment such as water heaters, furnaces, boilers, and wood stoves. Most importantly, the design of building ventilation must be careful to avoid the backdraft of combustion products from "naturally vented" appliances into the occupied space. This issue is of greater importance in new buildings with more air tight envelopes. To avoid the hazard, many modern combustion appliances utilize "direct venting" which draws combustion air directly from outdoors, instead of from the indoor environment.
Natural ventilation can also be achieved through the use of operable windows, this has largely been removed from most current architecture buildings due to the mechanical system continuously operating. The United States current strategy for ventilating buildings is to rely solely on mechanical ventilation. In Europe designers have experimented with design solutions that will allow for natural ventilation with minimal mechanical interference. These techniques include: building layout, facade construction, and materials used for inside finishes. European designers have also switched back to the use of operable windows to solve indoor air quality issues.
https://en.wikipedia.org/wiki/Ventilation_(architecture)
Ventilation in buildings with flats are typically build as mechanical extraction or as natural ventilation without heat recovery. Since the existing ventilation is without heat recovery, heat is lost corresponding to up to 30% of the buildings total energy consumption for space heating.
The ventilation can be provided as vertical exhaust (exhaust ducts) in kitchen and bath or fresh air supply in living rooms and rooms through leaks in the facade or fresh air valves in windows or facades. If the ventilation in the building is insufficient it often caused by:
1) Too few fresh air valves in the façade
2) An inadequate exhaustion of natural ventilation.
3) The drainage conditions have become insufficient in connection with renovation work on
the loft, kitchen and bathrooms, or as a result of reduced channel crossing or inappropriate
channel entries with many bends.
4) Improper behavior by residents. If a resident closes the air valves due to draft noise or a
wish for a lower heat bill, it has a special unfortunate consequence for the entire air balance
in the flats, because it increases the downside in the apartment in relation to the surrounding
apartments and rooms. A greatly increased negative pressure often produces noise and odor
transfer between apartments or from garbage disposal.
Thus, one of two issues is often found:
1) Lack of airshift that contributes to bad atmospheric indoor climate (air quality) and risk
for the formation of mold due to moisture content in the air is too high.
2) Adequate or excessive ventilation, like partly contributing to poor thermal indoor climate
and is extremely energy-consuming.
Therefore, always remember to use the option to upgrade the ventilation with heat recovery in the following situations:
- If mold has occurred in the apartment (may often be due to lack of ventilation)
- In connection with energy renovations, for example facade renovation and window replacement.
http://www.danskfjernvarme.dk/-/media/danskfjernvarme/kurser-moder/modematerialer/erfamoeder/2015-maj-erfa-traef-om-energibesparelser/ventilationsguide--energiloesninger.pdf
Water heating is a heat transfer process that uses an energy source to heat water above its initial temperature. Typical domestic uses of hot water include cooking, cleaning, bathing, and space heating. In industry, hot water and water heated to steam have many uses.
The required temperature of hot water is 60 °C . In section 8.2 §3 of the Building Regulations it is stated that water treatment plants must be carried out to minimize the risk of growth of legionella bacteria in the hot water. From section 43 of DS 439 it is apparent that a hot water supply system must be arranged so that the temperature can be raised to 60 °C in case of confirmed bacterial growth. There is no requirement for the plant to run constantly with this temperature, just the contrary, as it causes problems with calcification. Today it is common for hot water installations to have a flow temperature of 55 °C . In the case of townhouses and apartments with low-temperature district heating units, it will probably be safe to operate at temperatures down to 45 °C if a heat exchanger is installed for the hot water and there is no DHW circulation. In European standards (in Germany: DVGW W551), water content must be less than three liters in internal pipes and the liketo reduce the risk of legionella growth. (With the "3-liter rule", flow-through units can be used immediately for single-family houses and flats with flat stations. However, this is a task for a later design phase inside the buildings.
Hydronic balancing of the building heating installation is of major importance to achieve a well-functioning and an energy efficient operation. In general terms balancing is about ensuring that the operating conditions of each component in the installation is operating within its design operating conditions, which enables an efficient heating system operation. Hydronic heating installations can be generally grouped as: radiator or floor hearing.
Hydronic heating systems
Hydronic systems can be further classified in a vertical riser systems and horizontal systems, see Figure X1.
Vertical riser systems: In these systems there are multiple pipes running through the floors and supplying radiators and hot water taps along the way, see left side of Figure X1. Vertical riser systems are generally radiator heating systems.
Horizontal systems: In these systems there is one set of a riser for each staircase of the building, which is supplying the whole heat need of the connected flats, both heating and domestic hot water, see right side of Figure X1. The heat emitters in horizontal systems can be designed with one type or a mix of radiators and floor heating.
Heat emitters
The heating demand over the year varies significantly and the control equipment will need to be able to give consistent and accurate control to meet the consumers comfort requirements, independent on the demand. Figure X2 show a typical load duration curve for heating over period of one year. From a control point of view it is recommended to look on the installation from sink to source, as an efficient operation of the sink is the key to efficient buildings.
Radiators. Radiators should be designed to achieve as large cooling of the supply as possible, while keeping the supply temperature as low as possible. Current design temperature recommendation for an energy efficient and higher temperature difference radiator heating systems are 70/30//20°C, meaning 70°C supply and 30°C return for 20°C indoor temperature at design conditions.
- Thermostatic radiator valves (TRV) are used to adapt the heat supply (flow) to the actual demand. An efficient TRV consists of a pre-set radiator valve, which is used to limit the maximum flow through the valve, and a thermostatic head, which reacts to the indoor air temperature and adapts the flow to the desired room temperature. The radiator valves are designed for operation at maximum 60 kPa differential pressure across the valve, to avoid flow noises the pressure drop across the valve should be below 30-35 kPa. The differential pressure available is dependent on the location of the radiator in respect to the pump, the closer to the pump the higher the differential pressure. To ensure good operation of the TRV the differential pressure should be controlled and kept within the desired range. The solutions are to have pressure independent radiator valves or differential pressure controllers on each riser, which are addressed below.
Floor heating. Unlike radiators floor heating loops are designed for low supply temperatures, typically in the range of 40-45°C and return temperature of 25-30°C at design condition.
- Floor heating controls include a mixing shunt, floor heating manifold and a room temperature controller, see Figure X4. The mixing shunt adapts the supply temperature to a desired level, the floor heating manifold adapts the flow to each floor heating loop based on the inputs from the room temperature controller. As with radiator valves it is important to operate the floor heating controls within the designed differential pressure range.
Riser balancing
Riser balancing is to ensure equal operating conditions between risers in the building. This is important as there will inevitable be pressure difference from the pump to the last heat user, see Figure X5. Pressure balancing is important from two perspective: 1. To ensure good distribution of the heat supply through the building. If this is not considered there is a risk that the first risers “steal” large share of the supply due to wrong setting or malfunction of a TRV, leading to large flow passing through the radiator.
2. To ensure good operating conditions of the TRV at all demand conditions and avoidance of flow noises.
Domestic hot water systems (DHW)
Generally, the DHW system in a multi-story building will follow the concept of the heating installation.
Vertical riser systems. In a vertical riser system, DHW is prepared centrally and distributed to taps with vertical risers. To ensure high degree of safety, hygienic requirements and comfort at all tapping points thermal balancing system is needed. As with the space heating supply each domestic hot water riser needs to be balanced to ensure good distribution within the building. In addition to flow balancing the DHW distribution systems needs to be maintained at sufficiently high temperatures to prevent bacterial growth at the same time as heat losses are minimized. Utilization of thermal balancing valves will ensure balanced installation, stable DHW temperatures, energy efficient operation and if in combination with electronic controller a periodic thermal disinfection of the system. Figure X6 shows a thermal balancing DHW system.
Horizontal DHW system within each flat offers the opportunity to apply a small decentralized and instantaneous DHW preparation units at the entrance to the flat. This option is especially interesting as it avoids storing of DHW water, which generally is in a temperature range that favors bacterial growth, and large inefficient DHW circulation systems. To ensure high comfort levels it is important to ensure that the hot water is delivered quickly and at a stable temperature level to the user. This can be achieved with a sophisticated control equipment that immediately detects a hot water draw off using a proportional flow controller and thermostatic controller to achieve and maintain the desired DHW temperature. To avoid temperature fluctuations due to changes in supply conditions a differential pressure control should be integrated in the DHW controller. A schematic of an instantaneous DHW flat unit is shown in Figure X7.
Energy meters
To achieve energy efficient operation of a heating installation it is essential to include energy meters. The purpose of the energy meters is twofold, first to allocate the cost of heat generation to the actual users and secondly to maintain energy awareness of the users. The heat metering options depend on the applied system type. In a vertical riser system, the heat usage is estimated using heat cost allocators at each radiator and volumetric meters at each tap. In a horizontal system there are two variants, instantaneous DHW unit and a decentral DHW supply. If there is a DHW unit the total heat supply to the flat can be measured in one place, if there is a central DHW supply the space heating demand is measured with a heat meter and the DHW consumption is measured with a volumetric meter, both at the entrance to the flat. In addition to there should be a building level heat meter, main heat meter, to measures the total heat consumption of the building. The deviation between the individual heat meters and the main heat meter, essentially the heat loss in the building distribution system, should be distributed fairly between the consumers. Figure X8 shows typical heat meter applications.

## 14. Resiliency
Back to user guide
14. Resiliency
Figure 14-1: Grid resiliency
List of contents
14. Resiliency
14.1 Emergency generators
14.2 UPS
14.3 Emergency power system
14.4 Back-up boiler and storage
14.5 Reliability technology data
14.6 New technology 1
14.7 New technology 2
Assumptions applied (selected in 3.1 LCOE results)
Discount rate |  |  |  |  | 5% | %
Calculation period |  |  |  |  | 1
Start year of calculation |  |  |  |  | 2022
Electricity price development |  |  |  |  | Green
Expected solar thermal production |  |  |  |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  |  |  |  | Sustainable development scenario
Country |  |  |  |  | EU
Currency abbreviation |  |  |  |  | EUR
Currency factor |  |  |  |  | 1
Equipment |  |  |  |  | 1
Installation |  |  |  |  | 1
14.1 Emergency generators
Figure 14-2: Emergency generators
14.2 UPS
Figure 14-3: Batteries in Fairbanks and Mira Loma
Figure 14-4: Lithium Manganese Oxide (LMO) + Lithium Nickel Manganese Cobalt
Oxide (NMC) (Left) and Lithium Iron Phosphate (LFP) (Right)
Figure 14-5: Supercapacitor
14.3 Emergency power system
Figure 14-6: Emergency power system
14.4 Back-up boiler and storage
Figure 14-7: Viborg gas CHP with thermal storage and the thermal storage at Avedøreværket
14.5 Reliability technology data
Figure 14-8: Data structure and content in the reliability database
Table 14-1: Reliability database [20]
Category/Class | Item Number | Reliability | Inherent Availability | Operational Availability | Unit Years | Failures | Failure Rate (Failures/Year) | MTBF | MTTR | MTTM | MDT | MTBM | Hrdt/Year
Battery | Item: E2-000 | 0.99301 | 0.99999 | 0.99997 | 10543.8 | 74 | 0.00702 | 1248161 | 12.11 | 0.149 | 0.217 | 7140 | 0.2668
Boiler | Item: H8-000 | 0.87864 | 0.99936 | 0.99513 | 1113 | 144 | 0.12938 | 67708.83 | 43.29 | 3.2844 | 3.738 | 768 | 42.639
Hot Water | Item: H8-100 | 0.95901 | 0.99999 | 0.9995 | 358.4 | 15 | 0.04186 | 209292.8 | 3.08 | 1 | 1.005 | 2018 | 4.3634
Steam | Item: H8-200 | 0.84287 | 0.99906 | 0.99306 | 754.6 | 129 | 0.17094 | 51245.58 | 47.96 | 3.6062 | 4.12 | 593 | 60.817
High Pressure | Item: H8-210 | 0.92803 | 0.99962 | 0.99149 | 468.6 | 35 | 0.07469 | 117277.7 | 44.63 | 3 | 3.162 | 372 | 74.528
Low Pressure | Item: H8-220 | 0.71994 | 0.99815 | 0.99562 | 286.1 | 94 | 0.32859 | 26659.1 | 49.2 | 0 | 116.734 | 26659 | 38.357
Cable, AC Per 1000 ft. | Item: E6-000 | 0.99868 | 1 | 0.99999 | 698411 | 923 | 0.00132 | 6628468 | 7.29 | 4.281 | 4.44 | 351270 | 0.1107
Cable, AC, 0-600V | Item: E6-100 | 0.99892 | 1 | 1 | 130155 | 140 | 0.00108 | 8143981 | 9.04 | 6.3706 | 6.882 | 1559723 | 0.0387
Cable, AC, 601-15kV | Item: E6-200 | 0.99862 | 1 | 0.99999 | 568256 | 783 | 0.00138 | 6357495 | 6.98 | 4.2034 | 4.333 | 298329.1 | 0.1273
Cable, Aerial Per 1 Mile | Item:E7-000 | 0.98838 | 1 | 1 | 37478.5 | 438 | 0.01169 | 749570.9 | 2.03 | 0.3529 | 1.907 | 695576 | 0.024
Cable, Aerial, 0-15kV | Item: E7-100 | 0.95393 | 0.99999 | 0.99999 | 6593.7 | 311 | 0.04717 | 185725.9 | 1.82 | 0 | 1.817 | 185726 | 0.0857
Cable, Aerial >15kV | Item: E7-200 | 0.9959 | 1 | 1 | 30884.9 | 127 | 0.00411 | 2130325 | 2.54 | 0 | 2.081 | 1680443 | 0.0108
Cable, DC Per 100 ft. | Item: E8-000 | 0.99275 | 1 | 1 | 412.2 | 3 | 0.00728 | 1203640 | 2 | 0 | 0.109 | 65653 | 0.0146
Chiller | Item: H10-000 | 0.88852 | 0.99983 | 0.99762 | 2021.9 | 239 | 0.1182 | 74109.9 | 12.62 | 1.0881 | 1.164 | 489 | 20.843
Absorption | Item: H10-100 | 0.84199 | 0.99977 | 0.99513 | 430.3 | 74 | 0.17199 | 50932.86 | 11.74 | 1 | 0.653 | 134 | 42.639
Centrifugal | Item: H10-200 | 0.95514 | 0.99992 | 0.9976 | 544.7 | 25 | 0.04589 | 190872.1 | 14.52 | 5.2247 | 5.333 | 2227 | 20.981
Reciprocating | Item: H10-300 | 0.86456 | 0.9998 | 0.9989 | 948.2 | 138 | 0.14554 | 60190.78 | 12.05 | 1.5457 | 1.837 | 1667 | 9.6519
Rotary | Item: H10-400 | 0.98699 | 0.99996 | 0.9962 | 76.4 | 1 | 0.01309 | 669120 | 24 | 6.0723 | 6.115 | 1608 | 33.305
Screw | Item: H10-500 | 0.95629 | 0.99951 | 0.99657 | 22.4 | 1 | 0.0447 | 195984 | 96 | 1 | 1.164 | 339 | 30.081
Transformer, Dry | Item: E38-100 | 0.99995 | 1 | 0.99997 | 11025.1 | 19 | 5e-05 | 18937280 | xxx | 3.2263 | 3.693 | 131402 | 0.2462
Transformer, Liquid | Item: E38-200 | 0.9948 | 0.99995 | 0.99899 | 8819.2 | 46 | 0.00522 | 1679476 | 82.74 | 16.9047 | 17.588 | 17424 | 8.8425
UPS: Uninterruptible Power | Item: E39-000 | 0.99908 | 1 | 0.99995 | 553.1 | 4 | 0.00092 | 9499764 | xxx | 3.8 | 3.688 | 75701 | 0.4267
14.6 New technology 1
14.6.1 Technical- and economic assumptions
14.7 New technology 2
14.7.1 Technical- and economic assumptions
In this category we collect all the technologies, which are in particular important for the resilience of the energy system, that is e.g. an emergency generator, which is insalled for generating power in emergecy operation only and therefore not efficient enough for normal power genration, or an UPS battery, which is installed for short-term emergency operation before a generator is started, and not for storing energy.
Energy, in all its forms, is a vital commodity for societies and economies to function properly. Disruptions in energy systems have the potential to cause severe impacts, thereby limiting economic and societal development. As such, modern energy systems need to be able to withstand shocks from a wide range of sources, including natural disasters, geopolitical conflicts, and new and emerging threats related to the ongoing digitalization of energy systems.
The energy sector faces multiple threats from climate change, in particular from extreme weather events and increasing stress on water resources. Greater resilience to climate change impacts will be essential to the technical viability of the energy sector and its ability to cost-effectively meet the rising energy demands driven by global economic and population growth.
Energy systems around the world are becoming more interconnected and intelligent. This expansion brings many opportunities, but also new challenges as suppliers and governments seek to ensure the security of these systems. To date, cyber-related disruptions to the energy sector have been relatively minor; however, cyber-attacks are becoming more common, and the issue will only become more important as greater volumes of data are exchanged or stored on servers and with the increasingly rapid development of connected devices.
An emergency generator is a back-up electrical system that operates automatically. Within seconds of a utility outage an automatic transfer switch senses the power loss, commands the generator to start and then transfers the electrical load to the generator. The standby generator begins supplying power to the circuits. After utility power returns, the automatic transfer switch transfers the electrical load back to the utility and signals the standby generator to shut off. It then returns to standby mode where it awaits the next outage. To ensure a proper response to an outage, a standby generator runs weekly self-tests. Most units run on diesel, natural gas, or liquid propane gas.
Automatic standby generator systems may be required by building codes for critical safety systems such as elevators in high-rise buildings, fire protection systems, standby lighting, or medical and life support equipment. Residential standby generators are increasingly common, providing backup electrical power to HVAC systems, security systems, and household appliances such as refrigerators, stoves, and water heaters.
https://en.wikipedia.org/wiki/Standby_generator
An uninterruptible power supply or uninterruptible power source (UPS) is an electrical apparatus that provides emergency power to a load when the input power source or mains power fails. A UPS differs from an auxiliary or emergency power system or standby generator in that it will provide near-instantaneous protection from input power interruptions, by supplying energy stored in batteries, supercapacitors, or flywheels. The on-battery run-time of most uninterruptible power sources is relatively short (only a few minutes) but sufficient to start a standby power source or properly shut down the protected equipment. It is a type of continual power system.
A UPS is typically used to protect hardware such as computers, datacenters, telecommunication equipment or other electrical equipment where an unexpected power disruption could cause injuries, fatalities, serious business disruption or data loss. UPS units range in size from units designed to protect a single computer without a video monitor (around 200 volt-ampere rating) to large units powering entire data centers or buildings. The world's largest UPS, the 46-megawatt Battery Electric Storage System (BESS), in Fairbanks, Alaska, powers the entire city and nearby rural communities during outages.
https://en.wikipedia.org/wiki/Uninterruptible_power_supply
An emergency power system is an independent source of electrical power that supports important electrical systems on loss of normal power supply. A standby power system may include a standby generator, batteries and other apparatus. Emergency power systems are installed to protect life and property from the consequences of loss of primary electric power supply. It is a type of continual power system.
They find uses in a wide variety of settings from homes to hospitals, scientific laboratories, data centers, telecommunication equipment and ships. Emergency power systems can rely on generators, deep-cycle batteries, flywheel energy storage or fuel cells.
Emergency power systems were used as early as World War II on naval ships. In combat, a ship may lose the function of its boilers, which power the steam turbines for the ship's generator. In such a case, one or more diesel engines are used to drive back-up generators. Early transfer switches relied on manual operation; two switches would be placed horizontally, in line and the "on" position facing each other. a rod is placed in between. In order to operate the switch one source must be turned off, the rod moved to the other side and the other source turned on.
https://en.wikipedia.org/wiki/Emergency_power_system
The security of supply or need for resilience must be taken into account in district heating systems. The district heating company should have defined criteria for the security of supply in a generalized form. This criterion is more political than technical. The question is how much to pay for the security of heat supply, taking into account that almost all heat consumers can accept a disruption of heat supply in around 24 hours, in case of a very infrequent break-down? Reasonable criteria for production capacity can be the following:
- All disruption of heat supply must be re-established within 24 hours to normal consumers
- Vital consumers (hospitals, industries who need 100% reliable heat in the process) must have warm back-up in terms of a warm spare boiler or a heat storage tank
- In case it is not possible to re-establish the heat supply within 24 hours, in case of break-down on a pipe crossing a railroad, at least 60% of the maximal heat demand, roughly the demand on an average winter day, must be available to the district in which the heat is disrupted
- For districts smaller than 5 GWh, the grid is prepared for a mobile peak boiler plant (around 1 MW) to deliver spare capacity
- For districts larger than 5 GWh there must be an alternative heat supply source to deliver at least 60% of the maximal capacity located in the district in case the largest production plant is out of operation.
The chosen reserve margin affects the amount of spare peak capacity installed in the system. In case, the system has one large production unit as base load, the last criteria could be critical for defining the total need for production capacity. The criteria for capacity in case of break-down of a section of the network will define the districts in which there shall be established spare capacity. This part of the spare capacity must be located at decentralized locations. The criteria for supply to vital consumers will define that a certain spare capacity must be established at these vital consumers. To summarize, we could have the following capacities in a district of mainly 10,000 one family houses or apartments, as we consider horizontal distribution:
Total capacity of all customer installations without hot water tanks 300 MW
Total capacity for the main distribution lines 60 MW
Total annual heat sale 100,000 MWh
Total annual heat production (9% heat losses of production) 110,000 MWh
Total peak load capacity demand to the network (3,000 hours) 37 MW
Total need for cost effective base load production to meet demand 22 MW
Total additional peak load capacity to supplement base load 37 - 22 MW
Total peak and spare capacity, in case of break-down on largest unit 0.6 x 37 = 22 MW
In case base load plant is the largest unit, we need additional 22 - 15 = 7 MW
Thus, the total installed capacity has to be 22 MW base-load plus 15 MW peak-load and 7 MW spare capacity – a total of 44 MW.
In case a large part of the heat demand is separated from the base load plant by a critical pipe section, for example an underground crossing of a railroad, which cannot be repaired within 24 hours, a sufficient part of the spare capacity must be located on the isolated side of the section and meet the above criteria.
In the estimate of the capacity demand for additional production capacity to the new district, it must be taken into account that different types of consumers have different load profiles. The load fluctuation during the year of each individual customer is not of interest for analysing the integrated solution. Typically, customers have a variety of load profiles and it is only of importance for the analysis to know the total load profile for supply of energy to the network to supply all customers with heating, hot tap water and thermal losses in the network. Normally, it will be possible to collect data from existing district energy systems in the region as regards daily load fluctuations and annual load fluctuations per hour.
In case all customers use the same control unit settings for heat consumption and down-regulates heat consumption during night, including a quick start from zero to maximum at 6 am., the task is not trying to meet this demand, but to advice the customers to use their heating system efficient. The benefits of night down-regulation is often overestimated compared to the lack of thermal comfort and less efficient use of the heating system indicated by a larger return temperature. If measurements indicate that night down-regulation and fast upregulation in the morning causes problems, the planning should include:
- Guidelines on how to use heating systems efficiently in order to improve comfort and to calculate the actual saved energy
- Discount for low return temperature or a penalty for large return temperature to encourage customers to use the heating system uniformly and efficient
- A requirement that the return temperature must not exceed a certain level (50 oC) and if necessary, a valve, which closes in case the return temperature is higher
- To use a capacity payment in the tariff measured (€/kW) for installed capacity. This is as an alternative to a tariff component in €/m2
- To install more heat storage capacity to level the daily load fluctuations, in case the demand peaks causes problems for optimizing the heat production
- To take into account that a heat storage tank can level the load fluctuations on the coldest day and thus contribute to the installed peak capacity
Redundancy - the duplication of critical components or functions of a system with the intention of increasing reliability of the system
N: Only the number of components needed is provided, there is no resilience and any component failure will cause downtime.
N+1: Where the number of components provided is one more than the number (N) of components needed.
2N: Comprises two complete systems, each containing N components, and are run in parallel to hot swap between each other.
2(N+1): Comprises two N+1 systems in parallel. One side can be taken down for maintenance and the other side will be protected from exposure to the risk of downtime by its own redundant module.
Reliability - the probability that a product or service will operate properly for a specified period of time under design operating conditions without failure.
MTBF –Mean Time Between Failure - average time the equipment performed its intended function between failures.
MTTR – Mean Time To Repair - average time it takes to repair the failure and get the equipment back into service.
Availability - is the long-term average fraction of time that a repairable component or system is in service and satisfactorily performing its intended function.
Availability = MTBF/(MFBF + MTTR)
8760 Hours in 1 year of operation
The header below represents the header in the database. Each column heading is explained in the text boxes.
The data originates from the report: "Survey of reliability and availability information for power distribution, power generation, and heating, ventilating and air conditioning (hvac) components for commercial, industrial, and utility installations"

## 15. Miscellaneous
Back to user guide
15. Miscellaneous
List of contents
15. Miscellaneous
15.1 Heat exchanger stations
15.2 Pressure sectioning
15.3 Pressure regulator
15.4 SCADA systems
15.5 New technology 1
15.6 New technology 2
Assumptions applied (selected in 3.1 LCOE results)
Discount rate |  | 5% | %
Calculation period |  | 1
Start year of calculation |  | 2022
Electricity price development |  | Green
Expected solar thermal production |  | 500 | kWh/m2 panel/year
Fuel and CO2 price scenario |  | Sustainable development scenario
Country |  | EU
Currency abbreviation |  | EUR
Currency factor |  | 1
Equipment |  | 1
Installation |  | 1
15.1 Heat exchanger stations
Figure 15-1: Heat exchanger station and bundle type heat exchanger
15.2 Pressure sectioning
Figure 15-2: Dantaet pressure section (leakage protection)
15.2.1 Technical- and economic assumptions
Table 15-1: Leakage protection [14]
Pipe size | Price (full leakage protection) | Price (full leakage protection)
Reference | Rambøll | Rambøll
# | EUR | EUR
DN 40 | 4063.9667 | 4063.9667
DN 50 | 4790.3667 | 4790.3667
DN 65 | 5955.7 | 5955.7
DN 80 | 6575.4333 | 6575.4333
DN 100 | 7595.5667 | 7595.5667
* All included (Dantaet prices)
15.3 Pressure regulator
Figure 15-3: One-stage and two-stage pressure regulator
15.4 SCADA systems
Figure 15-4: Control center Energinet.dk and SCADA structure
15.5 New technology 1
15.5.1 Technical- and economic assumptions
15.6 New technology 2
15.6.1 Technical- and economic assumptions
The category includes technologies, which do not fit directly into the previous categories. Therefore, for a start any interesting technology can be described here and may be later transferred to another category.
Heat exchangers have several advantages, such as sectioning pressure levels, lower the maximum temperature, secure against large amounts of water by leakage, ensure good water quality in the large systems and reduce the risk of pressure protection and more. In the district heating system in Copenhagen, the heat exchanges have typically been a natural boundary between the companies and operating organizations. These requirements have led to that in some laces in certain periods have been 3-4 heat exchangers between a final consumer and the producer.
On the figure, a heat exchanger facing a building with indirect district heating supply is shown. By direct supply there is no heat exchanger. The shunt pump tries to hold T1 while the control valve first starts when the shunt pump is at maximum and the temperature is not high enough. Temperatures are inserted for illustration, but can be adjusted to others
flow temperatures in another system.
T3: Secondary supply depends on outdoor temperature; maximum of 55 oC
T1: Primary supply will probably be T3 + 5 oC (loss over heat exchanger)
The pump regulates T1 so that the T1's setpoint is kept
For example, the control valve regulates that T1> T3 + 2 oC
Return temperatures, T4 and T2, depend on the flow temperatures and cooling in the buildings.
With direct supply one can avoid the loss in the heat exchangers. Instead, one can regulate with pressure section and a safety valves system.
In the future district heating system where low temperatures are important
certain heat exchangers can be avoided. Technically it is possible to supply 70,000 end users from a single system like in Odense, if one accept direct supply and install leakage protection, where it is necessary. In Greater Copenhagen, where the system is more technical and organizationally complex than in Odense, one could argue that there must only be
heat exchangers between transmission and distribution and between distribution and final consumption.
We have estimated the prices based on the pipe size that enters the building. All values are based on our experience.
A pressure regulator is a control valve that reduces the input pressure of a fluid to a desired value at its output. Regulators are used for gases and liquids, and can be an integral device with an output pressure setting, a restrictor and a sensor all in the one body, or consist of a separate pressure sensor, controller and flow valve.
Often, water enters water-using appliances at fluctuating pressures, especially in remote locations, and industrial settings. This pressure often needs to be kept within a range to avoid damage to appliances, or accidents involving burst pipes/conduits. A single-stage regulator is sufficient in accuracy due to the high error tolerance of most such appliances. Also used in applications where the water supply reservoir is significantly higher in elevation to the end of the line. e.g. underground mine water supply.
https://en.wikipedia.org/wiki/Pressure_regulator
Supervisory control and data acquisition (SCADA) is a control system architecture that uses computers, networked data communications and graphical user interfaces for high-level process supervisory management but uses other peripheral devices such as programmable logic controller (PLC) and discrete PID controllers to interface with the process plant or machinery. The operator interfaces that enable monitoring and the issuing of process commands, such as controller set point changes, are handled through the SCADA computer system. However, the real-time control logic or controller calculations are performed by networked modules that connect to the field sensors and actuators.
The SCADA concept was developed as a universal means of remote access to a variety of local control modules, which could be from different manufacturers allowing access through standard automation protocols. In practice, large SCADA systems have grown to become very similar to distributed control systems in function, but using multiple means of interfacing with the plant. They can control large-scale processes that can include multiple sites, and work over large distances as well as small distance. It is one of the most commonly-used types of industrial control systems, however there are concerns about SCADA systems being vulnerable to cyberwarfare/cyberterrorism attacks.
https://en.wikipedia.org/wiki/SCADA

## 16. Non energy
Back to user guide
16. Non energy
List of contents
16. Non energy
16.1 Flood control
16.2 Tunnels
16.3 New technology 1
16.4 New technology 2
16.1 Flood control
Figure 16-1: Flood control and dam in Holland
16.2 Tunnels
Figure 16-2: Utility tunnel for district heating pipes between Rigshospitalet
and Amagerværket in Copenhagen
16.3 New technology 1
16.3.1 Technical- and economic assumptions
16.4 New technology 2
16.4.1 Technical- and economic assumptions
This category includes all non-energy technologies, which are not included in the other categories, but are important for improving the resilience.
Flood control methods are used to reduce or prevent the detrimental effects of flood waters. Flood relief methods are used to reduce the effects of flood waters or high water levels.
Floods are caused by many factors or a combination of any of these generally prolonged heavy rainfall (locally concentrated or throughout a catchment area), highly accelerated snowmelt, severe winds over water, unusual high tides, tsunamis, or failure of dams, levees, retention ponds, or other structures that retained the water. Flooding can be exacerbated by increased amounts of impervious surface or by other natural hazards such as wildfires, which reduce the supply of vegetation that can absorb rainfall.
Periodic floods occur on many rivers, forming a surrounding region known as the flood plain.
During times of rain, some of the water is retained in ponds or soil, some is absorbed by grass and vegetation, some evaporates, and the rest travels over the land as surface runoff. Floods occur when ponds, lakes, riverbeds, soil, and vegetation cannot absorb all the water. Water then runs off the land in quantities that cannot be carried within stream channels or retained in natural ponds, lakes, and man-made reservoirs. About 30 percent of all precipitation becomes runoff and that amount might be increased by water from melting snow. River flooding is often caused by heavy rain, sometimes increased by melting snow. A flood that rises rapidly, with little or no warning, is called a flash flood. Flash floods usually result from intense rainfall over a relatively small area, or if the area was already saturated from previous precipitation.
https://en.wikipedia.org/wiki/Flood_control
A tunnel is an underground passageway, dug through the surrounding soil/earth/rock and enclosed except for entrance and exit, commonly at each end. A pipeline is not a tunnel, though some recent tunnels have used immersed tube construction techniques rather than traditional tunnel boring methods.
A tunnel may be for foot or vehicular road traffic, for rail traffic, or for a canal. The central portions of a rapid transit network are usually in tunnel. Some tunnels are aqueducts to supply water for consumption or for hydroelectric stations or are sewers. Utility tunnels are used for routing steam, chilled water, electrical power or telecommunication cables, as well as connecting buildings for convenient passage of people and equipment.
Secret tunnels are built for military purposes, or by civilians for smuggling of weapons, contraband, or people. Special tunnels, such as wildlife crossings, are built to allow wildlife to cross human-made barriers safely. Tunnels can be connected together in tunnel networks.
https://en.wikipedia.org/wiki/Tunnel
TEXT
TEXT

## 17. ES planning models
Back to user guide
17. Energy system planning models
List of contents
17. Energy system planning models
17.1 Energy system analysis and planning programs overview
17.2 Use of the tools
17.3 Project phases
17.4 Balmorel
17.5 EnergyPLAN
17.6 EnergyPRO
17.7 TIMES
17.8 SIFRE
17.9 Statistical analysis
17.10 Stochastic programming
17.11 Hydraulic analysis
17.12 New technology 1
17.13 New technology 2
17.1 Energy system analysis and planning programs overview
Table 18-1: Energy Systems Modelization and Simulation Tools (Overview)
Name | Users |  | Description |  | License | Limitation | Projects | Comment
Balmorel | DTU, EA Energianalyse, COWI, Energistyrelsen, Dansk Energi |  | Versatile model for analysing electricity and combined heat and power sectors in a regional or international perspective. The model covers most of the European union, with development scenarios from IEA fuel price projections. The model is a deterministic investment optimization model and will provide the same result, given the same inputs. |  | Balmorel code is open source. However, the GAMS coding language solvers are not free of charge. Depending on the number of licenses, solvers required, etc. the prices differ. App. 15.000 € for a commercial software http://balmorel.com/index.php/downloadmodel https://www.gams.com/products/buy-gams/ | The model do not evaluate investments/decommissions in a probabilistic manner. Therefore, if considering the uncertainty of all inputs, the result will certainly be wrong. The model assumes to have full foresight and that no operators act strategically. | Electric connection between DK and UK, role of demand response, district heating expansion with heat pumps and electric boilers, electricity market development, electricity price projections | Balmorel is very complex and computationally heavy reducing its applicability for communicative purposes. Usually, only representative weeks during a year are simulated for a multi-year simulation. Balmorel provides a thorough simulation of the electricity system currently only surpassed by SIFRE.
EnergyPLAN | AAU, Plan Energi, Ramboll |  | Deterministic model for optimising the operation of a given energy system. The model excludes the investment optimization. The tool is simple and fast. |  | The model is open source: http://www.energyplan.eu/ | The model do not evaluate investments. The model assumes to have full foresight and that no operators act strategically. | National energy strategies, 100% renewable energy systems, energy storage, role of demand response. The model has been used in Henrik Lund´s 100 % Renewable Energy System book and the IDA Energy Vision analysis. | EnergyPLAN is much less computationally heavy than Balmorel and better for communicative purposes. However, it focuses on the entire energy system and excludes detailed analysis of the electric system.
EnergyPRO | Ramboll, Plan Energi, DTU, Energistyrelsen, AAU |  | Modelling software package for combined techno-economic design, analysis, and optimisation of energy projects. Designed for use in district heating and cooling projects with connection to the remaining energy system. The model is deterministic. The tool is user friendly and is also used by several district heating companies. |  | A licens for the model is necessary. Price depends on modules and user. https://www.emd.dk/energypro/ | The model cannot simulate entire national energy systems. Including many units slows the program. | District heating system analysis, energy storage analysis, district cooling in cooperation with district heating. | Very useful for most projects that we have within district heating and cooling.
Name | Users |  | Description |  | License | Limitation | Projects | Comment
TIMES | DTU, Energistyrelsen, IEA |  | IEA ETSAP Energy Technology Systems Analysis Program-TIMES model developed by DTU for Denmark. Includes all sectors in the Danish energy system, finds least cost pathways to targets for renewables or emission reduction, links to Geographic Information System GIS data. The model performs a deterministic investment optimization. |  | The software is expensive: https://iea-etsap.org/index.php/etsap-tools/acquiring-etsap-tools App. 30.000 $ for a multi-user commercial software | Same as Balmorel. However, Balmorel has a more detailed electric network configuration. | Regional energy strategies, national energy strategies, excess heat in the district heating sector. | Uses time slices and is not very detailed in terms of the electricity systems. However, can be used for large system analysis.
SIFRE | Energinet.dk |  | Mixed-integer linear optimization tool simulating energy flows and energy prices in all sectors of the specified energy system in discrete time steps. The model is developed and used by Energinet.dk. |  | The mathematical formulation is open source, but the program is written in C# and runs on Energinet.dk´s servers. https://energinet.dk/Analyse-og-Forskning/Beregningsmodeller | The model is complex MILP Unit Commitment model, similar to Balmorel, providing a better ability to evaluate the system reliability provided very accurate inputs. | Danish electricity sector analysis, national energy planning strategies, role of demand response. | The mathematical optimization problem formulation is available at the webpage of Energinet.dk. It can be inserted into any coding language of preference. The focus is on the electricity system/market.
Statisitical Analysis | --- |  | Good statistical measures providing information on the energy systems based on data is often as useful as energy system analysis tools. Furthermore, statistics can be used to project the electricity price within certain boundaries (Monte Carlo, Bayesian Statistics). It provides a probabilistic measure to evaluate investments, profit optimization, etc. |  | Usually these type of analyses are written in a coding language of choice or in Excel/VBA. There are no standard programs, thus no specific licenses needed. | A statistical electricity price projection do not tell anything about the production distribution. How much wind, how much CHP power production, and so forth. We are not able to quantify how much RE that can be integrated in the systems. | Investment decisions and many scientific studies. | To perform this type of statistics requires that the user is familiar with advanced programming.
Stochastic Programming | --- |  | Electricity market clearing with stochastic programming includes a probabilistic measure of the uncertainty. The mathematical optimization problem formulation is very complex. In an overall system perspective simulating several years, the approach can be excessive. |  | Typically written in GAMS or Python. For GAMS, the license costs are shown under the Balmorel model. | This approach cannot be used for energy system planning considering long time horizons. Instead it can be seen as more of a benchmark to compare against. | Scientific studies | The mathematical optimization formulations are available to the public. However, it requires very good skills within advanced programming to implement and understand them.
17.2 Use of the tools
Table 18-2: Energy Systems Modelization and Simulation Tools (Use)
Name |  | Electricity system |  | Electricity market | District heating | District cooling | Gas | Transport
Balmorel |  | X |  | X | Aggregated level | Aggregated level | --- | Aggregated level
EnergyPLAN |  | Aggregated level |  | --- | Aggregated level | Aggregated level | Aggregated level | Aggregated level
EnergyPRO |  | Aggregated level, small islanded systems |  | --- | X | X | --- | Aggregated level, small islanded systems
TIMES |  | Aggregated level |  | Aggregated level | Aggregated level | Aggregated level | Aggregated level | Aggregated level
SIFRE |  | X |  | X | Aggregated level | Aggregated level | --- | Aggregated level
Statistical analysis |  | X |  | X | X | X | X | X
Stochastic programming |  | X |  | X | X | X | X | X
System Rørnet |  | --- |  | --- | X | X | X | ---
TERMIS |  | --- |  | --- | X | X | X | ---
* System Rørnet and Termis are hydraulic analysis tools (described separately)
17.3 Project phases
Table 18-3: Energy Systems Modelization and Simulation Tools (Project Phases)
Name |  | Planning phase |  | Detailed design phase | Operating phase | Strategic work political | Focus area
Balmorel |  | X |  | --- | --- | Yes, used widely in Denmark and starting to be implemented in Danish partner countries | Global and international energy systems
EnergyPLAN |  | X |  | --- | --- | Yes, wide spread through open source and scientific communities | National energy systems
EnergyPRO |  | X |  | --- | --- | Yes, used for projects related to detailed economic analysis for later approval in ministries/municipalities | Local community
TIMES |  | X |  | --- | --- | Yes, used by IEA and in the scientific community | Global and international energy systems
SIFRE |  | X |  | --- | X | Not really. Apart from Energinet.dk. | National energy systems
Statistical analysis |  | X |  | X | X | Yes, but only to the point where the results are still explainable to non-technical people | No constraints
Stochastic programming |  | X |  | --- | X | No, the level of detail is too high. However, the world evolves and this may be where we are heading with RE electricity markets. | Only used in test systems in scientific studies
System Rørnet |  | X |  | X | --- | --- | ---
TERMIS |  | X |  | X | X | --- | ---
* System Rørnet and Termis are hydraulic analysis tools (described separately)
17.4 Balmorel
17.5 EnergyPLAN
17.6 EnergyPRO
17.7 TIMES
17.8 SIFRE
17.9 Statistical analysis
17.10 Stochastic programming
17.11 Hydraulic analysis
17.12 New technology 1
17.12.1 Technical- and economic assumptions
17.13 New technology 2
17.13.1 Technical- and economic assumptions
This category includes a description of selected energy system planning models. The list is not exhaustive and can be increased with other programs.
We will first provide an overview and comparison between the programs, with a subsequent more detailed description per program.
EnergyPLAN has been developed and expanded on a continuous basis since 1999 at Aalborg University, Denmark.
EnergyPLAN is a user-friendly tool designed in a series of tab sheets and programmed in Delphi Pascal. Input is defined by the user in terms of technologies and cost specifications. The main purpose of the model is to assist the design of national or regional energy planning strategies on the basis of technical and economic analyses of the consequences of implementing different energy systems and investments.
The model encompasses the whole national or regional energy system including heat and electricity supplies as well as the transport and industrial sectors. All thermal, renewable, storage and conversion and transport technologies can be modelled by EnergyPLAN. The model is a deterministic input/output model. General inputs are demands, renewable energy sources, energy station capacities, costs and a number of optional different regulation strategies emphasising import/export and excess electricity production. Outputs are energy balances and resulting annual productions, fuel consumption, import/export of electricity, and total costs including income from the exchange of electricity.
Compared to other similar models, the following characteristics of EnergyPLAN can be highlighted: EnergyPLAN is a deterministic model as opposed to a stochastic model or models using Monte Carlo methods. Therefore, with the same input, it will always come to the same result. EnergyPLAN is based on analytical programming as opposed to iterations, dynamic programming or advanced mathematical tools. This makes the calculations direct and the model very fast when performing calculations. In the programming, any procedures which would increase the calculation time have been avoided, and the computation of one year requires only a few seconds on a normal computer, even in the case of complicated national energy systems.
EnergyPLAN is an hourly simulation model as opposed to a model based on aggregated annual demands and productions. Consequently, the model is able to analyse the influence of fluctuating renewable energy sources on the system as well as weekly and seasonal differences in electricity and heat demands and water inputs to large hydro power systems. EnergyPLAN is aggregated in its system description as opposed to models in which each individual station and component is described, e.g. in EnergyPLAN district-heating systems are aggregated and defined as three principle groups. EnergyPLAN optimises the operation of a given system as opposed to models which optimise investments in the system. However, by analysing different systems (investments), the model can be used for identifying feasible investments.
EnergyPLAN provides a choice between different regulation strategies for a given system as opposed to models in which a specific institutional framework is incorporated. EnergyPLAN analyses one year in steps of one hour as opposed to scenario models analysing a series of years. However, several analyses each covering one year may of course be combined into scenarios.
https://www.energyplan.eu/
Programs to be used for hydraulic analyses include Termis and the Ramboll developed program System Rornet.
The energy planning aspects of designing a district heating network are the following:
In the conceptual design of a district heating network, the maximal operation temperature must be lower than 95 oC to allow pressure less heat storage tanks or lower than 85 oC to allow heat storage pits and certain renewable heat production sources. Furthermore, the pressure level must be 6 bar for direct connection or 10 bar, 16 bar or 25 bar for indirect connection at customer installations.
Figure 18-3 shows a print from a GIS-based hydraulic analysis, which has been used to calculate the accurate length of pipes and to design the necessary dimensions considering heat load of each costumer, diversity of consumption, maximal supply temperature, estimated return temperature and available pressure difference from the production plants. In the network design it must be taken into account that the diversity factor is 1.0 at customer branch lines and that it is gradually reduced for larger dimensions for a number of customers.
For an energy planner, the following information is required:
1. Identification of a suitable trench of the distribution network from production to all districts and customers plus large branch lines
2. Estimate of pipe dimensions and length of each pipe for a distribution network and for typical branch lines in each district
3. The network will normally be analysed by a hydraulic analysis system, but for a simple case, the energy planner can make a rough estimate manually based on a design table and manual measurements of pipe length
4. The planner can draw a logic sequence of the network. For example, connection to district A is necessary for supply of heat to district B. Therefore, the network in district A must be designed to also supply district B
The BALMOREL energy model is a partial equilibrium model, which supports modelling and analysis of the energy sector with emphasis on the electricity and the combined heat and power sectors. BALMOREL is developed, maintained and distributed under open source ideals since 2000. Hence, the model as well as project generated information, including all details, can be freely downloaded. This in particular includes the model source code and a working data set. The model development is mainly project driven, with a users’ network and forum around it, supporting the open source development idea. The model is formulated in the GAMS modelling language and a GAMS license is needed to run the model; additionally it has a graphical user interface facilitating input data handling, output reporting etc. Approximately 10 versions of the BALMOREL model have been created (and the number of users is not monitored). In addition to providing 100% documentation at code level, any user can modify the model to suit specific requirements in a given application of it. Since the formulated model is solved in standard software, there is no need to write new optimization code.
Input data and calculation results are given in relation to a geographical subdivision that allows identification of countries (for description of e.g. taxes, emissions, etc.), regions (for electricity transmission) and areas (for district heating systems, local cost elements, etc.). Time aspects are treated flexibly in relation to how many years to represent, and how many subdivisions of the time within the year. Typical choices are 250 time segments per year over a 20 year time-horizon, or 8,760 time segments per year over one year, according to the purpose of the study.
BALMOREL can simulate the electricity sector and some of the heat sector (district heating), but not the transport sector (transport technologies are not represented as standard, but some projects have developed transport sector modules). Technical and economic characteristics are given for an arbitrary number of production units, e.g. capacities, fuel efficiencies, operation and maintenance costs, fuel prices.
The different types of units include electricity, heat, combined heat and power, short-term heat storages, hydro power, wind and solar. Specialties like electricity storage are provided to represent e.g. hydrogen storage or pumped hydro. Electricity transmission is described in relation to a number of nodes that are connected by transmission lines characterised by capacity, loss and cost. This flow model allows for the identification of bottlenecks in the transmission system, and thereby can show differences in electricity prices according to geography.
In relation to generation capacity, the model may invest optimally in electricity and combined heat and power technologies. The investments respect specified restrictions e.g. in relation to maximum investment addition per year, or maximum fuel available. The model also handles environmental and other taxes, subsidies and quotas. Due to the model being formulated in a modelling system additional functionalities may be (and have been) developed as needed in relation to specific project needs.
http://www.balmorel.com/
EnergyPRO is a Windows-based modeling software package for combined technoeconomic analysis and optimisation of complex energy projects with a combined supply of electricity and thermal energy from multiple different energy producing units.
EnergyPRO is a complete modelling software package for combined techno-economic analysis and optimisation of both cogeneration and trigeneration projects as well as other types of complex energy projects with a combined supply of electricity and thermal energy (steam, hot water or cooling) from multiple different energy producing units.
EnergyPRO is typically used for techno-economic analysis of energy projects such as district heating cogeneration plants with gas engines combined with boilers and thermal storage, industrial cogeneration plants supplying both electricity, steam and hot water to a site, cogeneration plants with absorption chilling (trigeneration), biogas fuelled CHP plants with a biogas store, biomass cogeneration plants.
Other types of projects, e.g. geothermal, solar collectors, photovoltaic or wind farms can also be analysed and detailed within the software.
EnergyPRO can also be used for analysing hydro pumping stations, compressed air energy storage and other electricity storage projects.
EnergyPRO allows the daily optimization of the operation to be made against fixed tariffs for electricity or against spot market prices. The optimization is taking into account the limited sizes of thermal and fuel stores.
'
EnergyPRO provides the user with a detailed financial plan in a standard format accepted by international banks and funding institutions. This includes presentation of the operating results for the project, monthly cash flows, income statements (P&L), balance sheets and key investment figures such as NPV, IRR and payback time.
The software enables the user to calculate and produce a report for the emissions (CO2, NOX, SO2, etc.) by the proposed project.
https://www.emd.dk/energypro/
The MARKAL/TIMES family are energy/economic/environmental models supporting a rich technology detail. MARKAL/TIMES were developed in a collaborative effort under the auspices of the International Energy Agency’s Energy Technology Systems Analysis Programme, which started in 1978.
MARKAL has been developed since 1980 and TIMES since 2000. New versions of TIMES are being released every few months. At the moment, MARKAL/TIMES is used in 70 countries by 250 institutions (of which 75% are active users). The source code is distributed free of charge by signing a Letter of Agreement not to provide any part of the ETSAP models generator to any third party. The code is written in GAMS, which is a commercial language and has to be purchased. 99% of the users manage the system by means of a shell, ANSWER or VEDA. The commercial software costs US$3000 – US$5,000 (€2,150 – €3,775) for an educational license and US$20,000 (€15,103) for a commercial license. The most demanding part is training and learning, which takes some months.
MARKAL/TIMES are general purpose model generators tailored by the input data to represent the evolution over a period of usually 20 to 50 or 100 years, of a specific energy-environment system at the global, multi-regional, national, state/province, or community level. Each annual load duration curve, hence each annual variable can be detailed by as many as desired time slices, which is user-defined at three levels: seasonal (or monthly), week days – weekends, and hour of the day. The entire energy system can be modelled and it is represented as a network, depicting all possible flows of energy (usually as many as reported by the detailed energy balances) from resource extraction, through energy transformation and end-use devices, to demand for useful energy services – as many as desired, in the desired units. For instance the demand for space heating can be specified by as many as desired categories such as single or multifamily, urban or rural, existing or new, etc., and in the desired units such as PJ, number of households, m2 or m3.
Each link in the network is characterized by a set of technical characteristics (e.g., capacity in place, availability factors, efficiency), environmental emission coefficients (e.g., CO2, SOx, NOx), and economic factors (e.g., capital and costs). All thermal, renewable, storage and conversion and transportation technologies can be simulated by the model. Many different energy networks or Reference Energy Systems (RES) are feasible for each time period. MARKAL/TIMES finds the “best” RES for each time period by selecting the set of options that minimizes total discounted system cost or the total discounted surplus over the entire planning horizon, within the limits of all imposed policy and physical constraints.
https://iea-etsap.org/index.php/etsap-tools/model-generators/times
Energinet.dk, the Danish TSO, has developed SIFRE - SImulation of Flexible and Renewable Energy sources. SIFRE is based on the Unit Commitment problem but includes much greater detail on fuel consumption, on multiple energy types and on connected energy systems. It allows for circles in the system, for example in the case of electrolysis where electricity is converted to gas, which can be converted back to electricity. The goal of SIFRE is to support highly flexible and integrated energy systems in great detail and in reasonable simulation time, such that the future behavior of energy system can be analyzed. The offset is the Danish heat and power system and SIFRE supports wind power and Combined Heat and Power generation in great detail. The tool is, however, not hardcoded to any energy system and can thus be applied however liked. SIFRE complements existing market simulation tools with its high level of detail, flexibility and support of integr
SIFRE is based on a MILP formulation for the Unit Commitment (UC) problem. The UC problem provides an optimal production schedule such that energy demand is met. In the literature, UC formulations consider the production of energy without taking into account details about fuel consumption. Instead, fuel consumption is represented by a (non-linear) production cost. The UC problem has been solved using Lagrangian relaxation and dynamic programming. More recently, however, MILP solvers have become so powerful that solving the UC as a MILP is an attractive alternative.
When simulating a flexible and integrated energy market, the UC formulation should not be restricted to one energy type but instead facilitate the integration of several energies. Also, it is not sufficient to only consider the production side of generators; fuel consumption must be represented in detail as fuel could be produced by another generator (heat pumps convert electricity into heat, electrolysis converts electricity into gas, etc). Fuel consumption is an important result when simulating and analyzing the behavior of energy systems.
The offset of SIFRE is the Danish heat and power systems, which are closely coupled through significant amounts of installed capacity at Combined Heat and Power production plants (CHP). The Danish system also holds a large amount of renewable energy, which brings along the need for analyzing flexibility. The proposed mathematical formulation is capable of handling renewable energy and the desired flexibility. The formulation is generic and not hardcoded to any specific energy system (not even the Danish): data and parameters for each component in the energy system are input. SIFRE aims at facilitating a very flexible and generic representation of the energy system, without restricting which energies to produce and which to consume. SIFRE is thus a generic simulation tool and is not focused on a specific energy system or geographic area. Hydro power, including pump storages, is currently not supported in SIFRE, but other than that the generic design of SIFRE facilitates modelling of power markets, district heating, gas, transportation, etc. either as several closed systems or in a single integrated energy system.
https://energinet.dk/analyse-og-forskning/beregningsmodeller
A good statistical measures providing information on the energy systems based on data is often as useful as energy system analysis tools. Furthermore, statistics can be used to project the electricity price within certain boundaries (Monte Carlo, Bayesian Statistics). It provides a probabilistic measure to evaluate investments, profit optimization, etc.
For example, one could focus on the price trends seen within a specific power market. How does the increase in renewable energy production change day-ahead electricity market prices, and how does it affect other ancillary service prices? etc. etc.
Most decision-making problems are subject to uncertainty, due to the inherent randomness of natural phenomena conditioning choices (e.g., the weather) or, more generally, to the inaccurate knowledge of input information. Decision makers are, therefore, eager for methods and tools that lead them to solutions less sensitive to environmental influences or imprecise data, while simultaneously reducing cost, increasing profit, or improving reliability.
Many decision-making processes can be posed as optimization problems, where a set of control variables (the decisions) is to be determined to optimize a certain objective, say minimize cost or maximize profit. The range of possible values the control variables can take on is typically limited by economic, technical, physical, or environmental considerations.
Stochastic programming provides some concepts and tools required to deal with the implications of having uncertain data in an optimization problem for decision making.
Stochastic programming, like Monte Carlo simulations, have long been utilized in the financial sector to evaluate uncertainties of investments. For example, have the value of a stock may evaolve in the future. For energy markets (especially the open power markets), the day-ahead allocation is typically determined in a deterministic approach. Yet, with more renewable energy entering the market, the uncertainty of what has been offered and what will be realized increases. Thus, a stochastic market is being proposed in the scientific literature.
Yet, as more insight into bid and operation of power producers is required, the free electricity market may need reconstruction. Therefore, the stochastic electricity market model may for now only be used as a benchmark model to measure the effectiveness of an existing deterministic market.
Some good books about stochastic programming/energy markets and decision making can be found here:
https://www.springer.com/us/book/9781461494102
https://www.springer.com/gp/book/9781441974204
https://www.springer.com/gb/book/9783319294995

## 18. ES operation models
Back to user guide
18. Energy system operation models
List of contents
18. Energy system operation models
18.1 Mentor Planner
18.2 Flexynets
18.3 HeatFor
18.4 New technology 1
18.5 New technology 2
18.1 Mentor Planner
Figure 19-1: The figure shows the accuracy of the load forecast ant the actual demand at week 45 in 2016 at Aalborg utility.
Figure 19-2: The figure shows the results for supply temperature optimization for minizming heat loss in the distribution grid.
The above figure shows the conceptual idea and the below figure a screenshot from the Mentor Planner.
Figure 19-3: Screenshot showing the overview of the heat demand and supply at multi heat source district heating system and how the utility is
participating in the power spot market.
18.2 Flexynets
18.3 HeatFor
18.4 New technology 1
18.4.1 Technical- and economic assumptions
18.5 New technology 2
18.5.1 Technical- and economic assumptions
This category includes the energy system operation models that we have found interesting. The list is not exhaustive and can be increased with other programs.
We provide a description per program.
The basic element of Mentor Planner is a heat consumption forecast also called a load forecast - and this enables the operating staff to evaluate the heat consumption 6 days in the future. Thus, the accumulation capacity can be used optimally in relation to the heat distribution and the electricity market.
In addition to a central role in the planning, the heat consumption forecast can also be used for other optimization functions such as temperature optimization of the flow temperature in a district heating network.
Mentor Planner is based on different modules, so that the individual customer can get a solution that exactly matches their specific needs.
The graphical user interface in Mentor Planner allows for:
- Visualization of a heat consumption forecast
- Visualization of the acu tank energy content hour by hour
- Visualization of temperature for flow and return temperature hour by hour
- Optimization of operating plans including any capacity constraints and boiler production
- Setting up the exact mathematical model for the network
- Planning and registration for the electricity market incl. regulation, day-ahead and intraday markets
- Display of spot price forecasts and realized spot price
- Visualization of an power correction
- Possibility of correction of plans at production stop
- Immediate calculation of earnings and progress of the heat storage tank
- Planning and optimization is done on the basis of access to SRO data, weather data, cost data and projection of heat consumption up to 6 days ahead.
Electricity plans and expected gas consumption are automatically sent to respectively; the production balance responsible party and the gas supplier.
The communication between the different players is standardized with the possibility of adapting Mentor Planner to specific requirements and wishes.
http://www.oe3i.dk/produkter-services/mentor-planner
FLEXYNETS is a H2020 European Project coordinated by EURAC, a research institute based in Bozen. Besides EURAC, the project sees the involvement of other five partners from different European countries: zafh.net (Germany), a research center of the “Hochschule für Technik” of Stuttgart, Solid Automation (Germany), a company specialized in control and monitoring design, PlanEnergi (Denmark), an engineering office specialized in district heating, Soltigua (Italy), a producer of concentrating solar collectors, Acciona (Spain), a large company with dedicated energy departments.
Traditionally, District Heating and Cooling (DH&C) networks distribute energy from a centralized generation plant to a number of remote customers. As such, actual DHC systems suffer from:
- Heat losses
- Some unexplored integration potential of different available energy sources (e.g. renewables and waste heat) into the network
- High network installation costs.
FLEXYNETS will develop, demonstrate and deploy a new generation of intelligent DH&C networks that reduce energy transportation losses by working at “neutral” (15-20°C) temperature levels. Reversible heat pumps will be used to exchange heat with the DHC network on the demand side, providing the necessary cooling and heating for the buildings. In this way, the same network can provide contemporary heating and cooling.
Moreover, the heat normally rejected by buildings (for example through a common split unit), will be fed into the network by the heat pumps (which are working in “cooling mode”) and recycled by other heat pumps that are producing domestic hot water.
In the same way, these networks allow to recovery and recycle waste heat available along the network path, even at very low temperatures, contrary to traditional District Heating Networks, that can harvest thermal energy only at high temperature (greater than 100°). Following this logic, it is possible to reuse also the waste heat e.g. from supermarkets’ chillers, data centers and several industrial processes. Moreover, working at low temperatures reduces the heat losses to the ground, increasing the network efficiency. This system does not substitute nor is opposed to traditional district heating networks.
In urban contexts not exploiting district heating yet, this new generation networks can represent the main heating and cooling system. In cities already making use of district heating, low temperature DH&C networks can use thermal energy from the return pipes (in addition to waste heat), which otherwise is considered as waste heat by the network utility. This allows them contemporarily to sell additional energy with the same infrastructure and makes the network more efficient, reducing the return temperature to the station.
http://www.flexynets.eu/en/
HeatFor™ is a self-learning system based on machine learning. On the basis of measurements from the district heating system, local weather stations and meteorological forecasts, the system is not only able to predict the heating demand but can also automatically and continuously improve its predictions as it is fed more data. Based on input data HeatFor™ automatically identifies and takes the systematic behavior of heat consumers into account. This means that HeatFor™ continuously adapts to the actual situation by continuously monitoring the consumption and automatically adapts to changes, such as:
- Changes in consumer behavior
- Changes in the number of consumers
- Changes in the meteorological models
- Changes in the thermal characteristics of the buildings
- Changes in the district heating network
The self-learning mechanism has the benefit, that it is not necessary to establish and maintain a complex physical description of the heating network, which is often time consuming. HeatFor™ will identify the impact of such changes by itself and quickly adapt.
Heat demand/load forecasting is complicated by the fact that the dynamics of buildings seriously affect the heat demand on an hourly basis. HeatFor™ system automatically applies an optimal smoothing effect which solves this issue, such that the physical properties of the underlying energy system are modelled correctly.
Ideally (but optionally) HeatFor™ is deployed in combination with MetFor™ (ENFOR service for locally optimized weather forecast) to obtain a more accurate local weather forecast, which will result in superior heat demand forecast accuracy.
HeatFor™ is provided as an integrated service from the ENFOR platform also which contains a data collection and validation module. The data collection and validation module collects the necessary data, ensures that the necessary data is available and contains a toolbox for automatic detection and correction of missing and/or erroneous measurements. The module then feed the validated data into the core HeatFor™™ module which then provides the forecasts.
The ENFOR platform also provides HeatFor™ with data integration modules through either FTP, SFTP or web-services such that HeatFor™ can be seamlessly integrated with the operational system (SCADA) controlling the district heating system. System integration is provided by one of the HeatFor™ system integration partners.
http://www.enfor.eu/
Case stories
Case 1:
A small utility in north of the island Fyn in Denmark. This utility has an annual consumption of 39.000 MWh of heat including the heat loss of 17%. The primary production unit is an 8 MW biomass furnace supplemented with 2 peak load gas boilers located in the city. Before they installed Mentor Planner at the utility, they supplied the network with a temperature of 74°C and had a return temperature of 39°C.
Prior to the implementation of Mentor Planner the client considered the temperatures to be good and that the potential of optimizing was limited, about 3°C in the supply temperature. The estimated impact of reducing the supply temperature by 3°C was about 7% reduction of the yearly heat loss, which would have corresponded to 460 MWh of heat per year.
Once the Mentor Planner was put in operation, it was found that the potential was considerably higher than expected. The supply temperature was reduced from 74°C to 66°C, leading to close to 12% reduction of the yearly heat loss, or 788 MWh of heat per year. The relative heat loss was reduced from 17% to 15% of the annual production. The client further achieved a reduction in the return temperature from 39°C to 35°C. In addition to optimizing the temperature profile the increased system knowledge achieved through the use of the Mentor Planner allowed the utility to address other system pain points.
The return of the investment for the client was in this case below 6 months.
Case 2:
A big utility in Aalborg, north of Jutland in Denmark. The utility had an annual consumption of 1.900 GWh of heat, including heat loss of 19%. The primary heat production is based on heat recovery from a waste incineration plant, heat recovery from a cement factory and a big coal fired combined heat and power plant. Additionally, the utility operates several peak load gas boilers around the city.
Before implementing Mentor Planner into their operation, the client had an average supply temperature of 78°C and had challenges with fluctuating supply temperature in parts of the network.
The network was divided into 12 energy zones, with a separate load forecast for each zone. Mentor Planner calculate the optimal supply temperature from several critical points in every individual energy zone, and the average supply temperature in the whole network was reduced from 78°C to an average of 69°C.
The reduction in average supply temperature gave the client a saving of 14.100 MWh of heat per year, and a more stable supply temperature where they had been experiencing supply temperature fluctuations.
All together the client reduced the relative heat loss from 19% to 17%, and the return of investment was below 6 months.

## 20. EnergyPRO (hidden)
Mild climate, wo/ grid connection | [17 empty] | Mild climate, wo/ grid connection, w/ wind production | [19 empty] | Arctic climate | [6 empty] | Tropic climate | [7 empty] | Mild climate, w/ grid connection
Heat production | [7 empty] | Cooling production |  |  |  | Electricity production | [5 empty] | Heating production | [7 empty] | Cooling production |  |  |  |  | Electricity production | [6 empty] | Electricity production |  |  | Heating production |  |  |  | Heating production |  |  |  | Cooling production |  |  |  | Heating production | [6 empty] | Cooling production
Index | Diesel boiler | Heat pump combi | Diesel engine | Heat demand | Heat rejection | Total demand | Heat rejection | Index | Chiller | Heat pump combi | Cooling demand | Index | Diesel engine | Electricity total demand | Electricity base demand | Chiller | Heat pump combi | Index | Diesel boiler | Heat pump combi | Diesel engine | Heat demand | Heat rejection | Total demand | Heat rejection | Index | Chiller | Heat pump combi | Cooling demand | Total demand | Index | Diesel engine | Wind turbine | Electricity total demand | Electricity base demand | Chiller | Heat pump combi | Index | Diesel engine | Electricity demand | Index | Diesel boiler | Diesel engine | Heat demand | Index | Heat pump combi | Natural gas boiler | Heat demand | Index | Heat pump combi | Electric chiller | Cooling demand | Index | Heat pump heat | Electric boiler | Natural gas boilers | Heat pump combi | Natural gas back pressure | Heat demand | Index | Chiller | Heat pump combi | Cooling demand
0 | 253.1535 | 20.4918 | 66.0392 | 339.6845 | 0 | 339.6845 | 339.6845 | 0 | 0 | 13.6612 | 10.929 | 0 | 52.8313 | 52.8313 | 46.0007 | 6.3798 | 13.6612 | 0 | 255.4527 | 20.4918 | 63.74 | 339.6845 | 0 | 339.6845 | 339.6845 | 0 | 0 | 13.6612 | 10.929 | 10.929 | 0 | 50.992 | 1.8393 | 52.8313 | 46.0007 | 6.3798 | 13.6612 | 0 | 5.7501 | 5.7501 | 0 | 15.9451 | 8.0501 | 23.9952 | 0 | 76.9189 | 81.8296 | 158.7484 | 0 | 51.2792 | 0 | 16.3934 | 0 | 78 | 42 | 72.273 | 26.2616 | 150 | 339.6845 | 0 | 0 | 17.5077 | 10.929
1 | 143.0576 | 28.9939 | 85.5164 | 257.5678 | 0 | 257.5678 | 257.5678 | 1 | 0 | 19.3292 | 10.929 | 1 | 68.4131 | 68.4131 | 58.7485 | 19.2583 | 10.9722 | 1 | 143.5187 | 28.9939 | 85.0552 | 257.5678 | 0 | 257.5678 | 257.5678 | 1 | 0 | 19.3292 | 10.929 | 10.929 | 1 | 68.0442 | 0.36891 | 68.4131 | 58.7485 | 19.2583 | 10.4185 | 1 | 7.3436 | 7.3436 | 1 | 16.8879 | 10.281 | 27.1689 | 1 | 25.6264 | 79.1071 | 98.9914 | 1 | 17.0843 | 0 | 24.203 | 1 | 132 | 0 | 0 | 10.929 | 120 | 257.5678 | 1 | 0 | 7.286 | 10.929
2 | 176.2619 | 8.8798 | 85.7423 | 270.884 | 0 | 270.884 | 270.884 | 2 | 0 | 5.9199 | 10.929 | 2 | 68.5939 | 68.5939 | 65.6339 | 22.9976 | 14.27 | 2 | 196.3826 | 8.8798 | 65.6217 | 270.884 | 0 | 270.884 | 270.884 | 2 | 0 | 5.9199 | 10.929 | 10.929 | 2 | 52.4973 | 16.0965 | 68.5939 | 65.6339 | 22.9976 | 14.8238 | 2 | 8.2042 | 8.2042 | 2 | 15.1833 | 11.4859 | 26.6693 | 2 | 75.1115 | 0 | 80.8536 | 2 | 50.0743 | 0 | 46.2482 | 2 | 72 | 12 | 0 | 11.9898 | 210 | 270.884 | 2 | 0 | 7.9932 | 10.929
3 | 138.4689 | 11.3067 | 85.7767 | 235.5523 | 0 | 235.5523 | 235.5523 | 3 | 0 | 7.5378 | 10.929 | 3 | 68.6214 | 68.6214 | 64.8525 | 8.9172 | 9.5077 | 3 | 140.6657 | 11.3067 | 83.58 | 235.5523 | 0 | 235.5523 | 235.5523 | 3 | 0 | 7.5378 | 10.929 | 10.929 | 3 | 66.864 | 1.7574 | 68.6214 | 64.8525 | 8.9172 | 10.4185 | 3 | 8.1066 | 8.1066 | 3 | 14.5086 | 11.3492 | 25.8578 | 3 | 76.7903 | 0 | 55.9321 | 3 | 51.1935 | 0 | 54.4847 | 3 | 102 | 42 | 0 | 22.1633 | 90 | 235.5523 | 3 | 0 | 14.7755 | 10.929
4 | 83.654 | 28.9939 | 94.4781 | 207.126 | 0 | 207.126 | 207.126 | 4 | 0 | 19.3292 | 10.929 | 4 | 75.5825 | 75.5825 | 65.9179 | 8.2112 | 18.51 | 4 | 83.9276 | 28.9939 | 94.2045 | 207.126 | 0 | 207.126 | 207.126 | 4 | 0 | 19.3292 | 10.929 | 10.929 | 4 | 75.3636 | 0.21889 | 75.5825 | 65.9179 | 8.2112 | 21.1439 | 4 | 8.2397 | 8.2397 | 4 | 15.4523 | 11.5356 | 26.9879 | 4 | 61.477 | 33.0207 | 115.3559 | 4 | 40.9847 | 0 | 65.8019 | 4 | 108 | 0 | 0 | 15.7104 | 30 | 207.126 | 4 | 0 | 10.4736 | 10.929
5 | 141.0465 | 12.9781 | 87.2486 | 241.2732 | 0 | 241.2732 | 241.2732 | 5 | 0 | 8.6521 | 10.929 | 5 | 69.7989 | 69.7989 | 65.4728 | 20.0663 | 15.1808 | 5 | 172.5686 | 12.9781 | 55.7265 | 241.2732 | 0 | 241.2732 | 241.2732 | 5 | 0 | 8.6521 | 10.929 | 10.929 | 5 | 44.5812 | 25.2177 | 69.7989 | 65.4728 | 20.0663 | 15.1808 | 5 | 8.1841 | 8.1841 | 5 | 17.8483 | 11.4577 | 29.3061 | 5 | 65.1081 | 216.9867 | 282.0948 | 5 | 43.4054 | 0 | 41.5732 | 5 | 72 | 0 | 41.1509 | 11.9898 | 90 | 241.2732 | 5 | 0 | 7.9932 | 10.929
6 | 250.3947 | 8.5745 | 73.2523 | 332.2214 | 0 | 332.2214 | 332.2214 | 6 | 0 | 5.7163 | 10.929 | 6 | 58.6018 | 58.6018 | 55.7437 | 32.4413 | 16.7937 | 6 | 266.6697 | 8.5745 | 56.9773 | 332.2214 | 0 | 332.2214 | 332.2214 | 6 | 0 | 5.7163 | 10.929 | 10.929 | 6 | 45.5819 | 13.02 | 58.6018 | 55.7437 | 32.4413 | 18.51 | 6 | 6.968 | 6.968 | 6 | 13.3489 | 9.7551 | 23.104 | 6 | 54 | 177.24 | 231.24 | 6 | 36 | 0 | 16.3934 | 6 | 72 | 0 | 33.3859 | 25.4208 | 210 | 332.2214 | 6 | 0 | 16.9472 | 10.929
7 | 249.2884 | 17.1414 | 73.2547 | 339.6845 | 0 | 339.6845 | 339.6845 | 7 | 0 | 11.4276 | 10.929 | 7 | 58.6038 | 58.6038 | 52.89 | 13.3975 | 14.8238 | 7 | 273.977 | 17.1414 | 48.5661 | 339.6845 | 0 | 339.6845 | 339.6845 | 7 | 0 | 11.4276 | 10.929 | 10.929 | 7 | 38.8529 | 19.7509 | 58.6038 | 52.89 | 13.3975 | 15.883 | 7 | 6.6112 | 6.6112 | 7 | 14.7395 | 9.2557 | 23.9952 | 7 | 9 | 149.7484 | 158.7484 | 7 | 6 | 0 | 16.3934 | 7 | 132 | 0 | 0 | 6.6831 | 230 | 339.6845 | 7 | 0 | 4.4554 | 10.929
8 | 143.6964 | 24.8306 | 89.0408 | 257.5678 | 0 | 257.5678 | 257.5678 | 8 | 0 | 16.5537 | 10.929 | 8 | 71.2326 | 71.2326 | 62.9558 | 32.2923 | 16.3383 | 8 | 148.324 | 24.8306 | 84.4131 | 257.5678 | 0 | 257.5678 | 257.5678 | 8 | 0 | 16.5537 | 10.929 | 10.929 | 8 | 67.5305 | 3.7021 | 71.2326 | 62.9558 | 32.2923 | 15.0273 | 8 | 7.8695 | 7.8695 | 8 | 16.1516 | 11.0173 | 27.1689 | 8 | 11.8918 | 87.0996 | 98.9914 | 8 | 7.9279 | 0 | 16.3934 | 8 | 114 | 0 | 0 | 16.3934 | 130 | 257.5678 | 8 | 0 | 10.929 | 10.929
9 | 163.0432 | 18.4426 | 89.3982 | 270.884 | 0 | 270.884 | 270.884 | 9 | 0 | 12.2951 | 10.929 | 9 | 71.5186 | 71.5186 | 65.371 | 14.8974 | 14.5719 | 9 | 173.7825 | 18.4426 | 78.6589 | 270.884 | 0 | 270.884 | 270.884 | 9 | 0 | 12.2951 | 10.929 | 10.929 | 9 | 62.9271 | 8.5914 | 71.5186 | 65.371 | 14.8974 | 16.8488 | 9 | 8.1714 | 8.1714 | 9 | 15.2293 | 11.4399 | 26.6693 | 9 | 48.0871 | 32.7665 | 80.8536 | 9 | 32.0581 | 0 | 16.3934 | 9 | 120 | 0 | 0 | 16.3934 | 170 | 270.884 | 9 | 0 | 10.929 | 10.929
10 | 140.2626 | 4.4761 | 85.5872 | 230.3259 | 0 | 230.3259 | 230.3259 | 10 | 0 | 2.9841 | 10.929 | 10 | 68.4697 | 68.4697 | 66.9777 | 10.0639 | 24.128 | 10 | 187.2103 | 4.4761 | 38.6395 | 230.3259 | 0 | 230.3259 | 230.3259 | 10 | 0 | 2.9841 | 10.929 | 10.929 | 10 | 30.9116 | 37.5582 | 68.4697 | 66.9777 | 10.0639 | 14.1097 | 10 | 8.3722 | 8.3722 | 10 | 14.1367 | 11.7211 | 25.8578 | 10 | 55.9321 | 0 | 55.9321 | 10 | 37.288 | 0 | 35.4337 | 10 | 114 | 6 | 7.6336 | 16.3934 | 0 | 230.3259 | 10 | 0 | 10.929 | 10.929
11 | 135.6647 | 15.0273 | 88.1261 | 238.8181 | 0 | 238.8181 | 238.8181 | 11 | 0 | 10.0182 | 10.929 | 11 | 70.5009 | 70.5009 | 65.4918 | 8.9682 | 15.883 | 11 | 186.6697 | 15.0273 | 37.121 | 238.8181 | 0 | 238.8181 | 238.8181 | 11 | 0 | 10.0182 | 10.929 | 10.929 | 11 | 29.6968 | 40.804 | 70.5009 | 65.4918 | 8.9682 | 19.4276 | 11 | 8.1865 | 8.1865 | 11 | 15.5269 | 11.4611 | 26.9879 | 11 | 60.9608 | 54.3951 | 115.3559 | 11 | 40.6405 | 0 | 42.465 | 11 | 96 | 36 | 78.6549 | 28.1633 | 0 | 238.8181 | 11 | 0 | 18.7755 | 10.929
12 | 98.8007 | 29.6769 | 88.601 | 217.0786 | 0 | 217.0786 | 217.0786 | 12 | 0 | 19.7846 | 10.929 | 12 | 70.8808 | 70.8808 | 60.9885 | 15.3654 | 15.7345 | 12 | 121.837 | 29.6769 | 65.5647 | 217.0786 | 0 | 217.0786 | 217.0786 | 12 | 0 | 19.7846 | 10.929 | 10.929 | 12 | 52.4518 | 18.429 | 70.8808 | 60.9885 | 15.3654 | 17.1439 | 12 | 7.6236 | 7.6236 | 12 | 18.6331 | 10.673 | 29.3061 | 12 | 40.056 | 242.0388 | 282.0948 | 12 | 26.704 | 0 | 34.2933 | 12 | 138 | 0 | 73.7719 | 5.3067 | 0 | 217.0786 | 12 | 0 | 3.5378 | 10.929
13 | 140.3665 | 5.1592 | 69.4486 | 214.9742 | 0 | 214.9742 | 214.9742 | 13 | 0 | 3.4394 | 10.929 | 13 | 55.5589 | 55.5589 | 53.8392 | 19.8386 | 19.4208 | 13 | 141.7957 | 5.1592 | 68.0194 | 214.9742 | 0 | 214.9742 | 214.9742 | 13 | 0 | 3.4394 | 10.929 | 10.929 | 13 | 54.4156 | 1.1433 | 55.5589 | 53.8392 | 19.8386 | 17.199 | 13 | 6.7299 | 6.7299 | 13 | 21.4436 | 9.4219 | 30.8654 | 13 | 81.6998 | 235.6232 | 317.323 | 13 | 54.4665 | 0 | 56.1007 | 13 | 114 | 0 | 83.8977 | 17.0765 | 0 | 214.9742 | 13 | 0 | 11.3843 | 10.929
14 | 160.5122 | 15.0273 | 72.0526 | 247.5921 | 0 | 247.5921 | 247.5921 | 14 | 0 | 10.0182 | 10.929 | 14 | 57.6421 | 57.6421 | 52.633 | 14.4227 | 19.526 | 14 | 160.6236 | 15.0273 | 71.9412 | 247.5921 | 0 | 247.5921 | 247.5921 | 14 | 0 | 10.0182 | 10.929 | 10.929 | 14 | 57.553 | 0.089127 | 57.6421 | 52.633 | 12.6533 | 22.2582 | 14 | 6.5791 | 6.5791 | 14 | 23.1042 | 9.2108 | 32.3149 | 14 | 100.7077 | 208.6175 | 309.3252 | 14 | 67.1385 | 0 | 37.9576 | 14 | 114 | 0 | 40.0248 | 27.4802 | 110 | 247.5921 | 14 | 0 | 18.3201 | 10.929
15 | 125.7436 | 26.9447 | 91.6897 | 244.378 | 0 | 244.378 | 244.378 | 15 | 0 | 17.9631 | 10.929 | 15 | 73.3518 | 73.3518 | 64.3702 | 22.8324 | 16.1899 | 15 | 159.4683 | 26.9447 | 57.965 | 244.378 | 0 | 244.378 | 244.378 | 15 | 0 | 17.9631 | 10.929 | 10.929 | 15 | 46.372 | 26.9798 | 73.3518 | 64.3702 | 26.5041 | 10.7254 | 15 | 8.0463 | 8.0463 | 15 | 21.8868 | 11.2648 | 33.1516 | 15 | 33.8757 | 197.8993 | 229.1215 | 15 | 22.5838 | 0 | 45.1024 | 15 | 84 | 0 | 0 | 3.9406 | 130 | 244.378 | 15 | 0 | 2.627 | 10.929
16 | 157.8265 | 17.0765 | 89.0067 | 263.9097 | 0 | 263.9097 | 263.9097 | 16 | 0 | 11.3843 | 10.929 | 16 | 71.2054 | 71.2054 | 65.5132 | 18.1329 | 8.0984 | 16 | 193.7033 | 17.0765 | 53.1298 | 263.9097 | 0 | 263.9097 | 263.9097 | 16 | 0 | 11.3843 | 10.929 | 10.929 | 16 | 42.5039 | 28.7015 | 71.2054 | 65.5132 | 14.5212 | 21.7045 | 16 | 8.1891 | 8.1891 | 16 | 17.2367 | 11.4648 | 28.7015 | 16 | 48.4392 | 73.701 | 124.7937 | 16 | 32.2928 | 0 | 51.4906 | 16 | 53.6164 | 0 | 8.6223 | 16.3934 | 200 | 263.9097 | 16 | 0 | 10.929 | 10.929
17 | 172.742 | 15.7104 | 85.9907 | 274.443 | 0 | 274.443 | 274.443 | 17 | 0 | 10.4736 | 10.929 | 17 | 68.7925 | 68.7925 | 63.5557 | 5.488 | 24.4731 | 17 | 202.7625 | 15.7104 | 55.9702 | 274.443 | 0 | 274.443 | 274.443 | 17 | 0 | 10.4736 | 10.929 | 10.929 | 17 | 44.7761 | 24.0164 | 68.7925 | 63.5557 | 6.259 | 17.6357 | 17 | 7.9445 | 7.9445 | 17 | 13.9064 | 11.1223 | 25.0287 | 17 | 107.9377 | 12.2372 | 107.3224 | 17 | 71.9585 | 0 | 58.7489 | 17 | 120 | 0 | 0 | 16.3934 | 190 | 274.443 | 17 | 0 | 10.929 | 10.929
18 | 176.5475 | 15.0273 | 84.0987 | 275.6735 | 0 | 275.6735 | 275.6735 | 18 | 0 | 10.0182 | 10.929 | 18 | 67.279 | 67.279 | 62.2698 | 12.6658 | 14.4117 | 18 | 209.6131 | 15.0273 | 51.033 | 275.6735 | 0 | 275.6735 | 275.6735 | 18 | 0 | 10.0182 | 10.929 | 10.929 | 18 | 40.8264 | 26.4526 | 67.279 | 62.2698 | 11.8347 | 16.7505 | 18 | 7.7837 | 7.7837 | 18 | 18.4973 | 10.8972 | 29.3945 | 18 | 79.3577 | 51.8865 | 125.3173 | 18 | 52.9051 | 0 | 45.0105 | 18 | 120 | 0 | 0 | 18.6831 | 140 | 275.6735 | 18 | 0 | 12.4554 | 10.929
19 | 136.6197 | 14.0389 | 79.2417 | 229.9004 | 0 | 229.9004 | 229.9004 | 19 | 0 | 9.3593 | 10.929 | 19 | 63.3934 | 63.3934 | 58.7137 | 18.0204 | 20.2882 | 19 | 169.6563 | 14.0389 | 46.2051 | 229.9004 | 0 | 229.9004 | 229.9004 | 19 | 0 | 9.3593 | 10.929 | 10.929 | 19 | 36.9641 | 26.4293 | 63.3934 | 58.7137 | 18.6391 | 21.3957 | 19 | 7.3392 | 7.3392 | 19 | 23.6415 | 10.2749 | 33.9164 | 19 | 55.5085 | 3.0072 | 77.2951 | 19 | 37.0057 | 0 | 16.3934 | 19 | 126 | 0 | 0.52459 | 16.2179 | 0 | 229.9004 | 19 | 0 | 10.8119 | 10.929
20 | 109.5257 | 20.1141 | 71.633 | 201.2728 | 0 | 201.2728 | 201.2728 | 20 | 0 | 13.4094 | 10.929 | 20 | 57.3064 | 57.3064 | 50.6017 | 8.92 | 18.9103 | 20 | 116.7961 | 20.1141 | 64.3626 | 201.2728 | 0 | 201.2728 | 201.2728 | 20 | 0 | 13.4094 | 10.929 | 10.929 | 20 | 51.4901 | 5.8163 | 57.3064 | 50.6017 | 8.3984 | 19.4276 | 20 | 6.3252 | 6.3252 | 20 | 25.838 | 8.8553 | 34.6933 | 20 | 24.5902 | 109.8675 | 134.4576 | 20 | 16.3934 | 0 | 16.3934 | 20 | 108 | 0 | 73.2236 | 20.0492 | 0 | 201.2728 | 20 | 0 | 13.3661 | 10.929
21 | 109.6045 | 11.9898 | 68.1217 | 189.716 | 0 | 189.716 | 189.716 | 21 | 0 | 7.9932 | 10.929 | 21 | 54.4974 | 54.4974 | 50.5008 | 18.5734 | 17.2058 | 21 | 141.5259 | 11.5459 | 36.6442 | 189.716 | 0 | 189.716 | 189.716 | 21 | 0 | 7.6972 | 10.929 | 10.929 | 21 | 29.3153 | 25.0341 | 54.3494 | 50.5008 | 18.9671 | 12.3934 | 21 | 6.3126 | 6.3126 | 21 | 23.2049 | 8.8376 | 32.0426 | 21 | 24.5902 | 84.7768 | 101.8835 | 21 | 16.3934 | 0 | 16.3934 | 21 | 114 | 0 | 59.3225 | 16.3934 | 0 | 189.716 | 21 | 0 | 10.929 | 10.929
22 | 115.8167 | 10.2459 | 80.2124 | 206.275 | 0 | 206.275 | 206.275 | 22 | 0 | 6.8306 | 10.929 | 22 | 64.1699 | 64.1699 | 60.7546 | 33.0089 | 16.4918 | 22 | 146.9799 | 10.6898 | 48.6053 | 206.275 | 0 | 206.275 | 206.275 | 22 | 0 | 7.1265 | 10.929 | 10.929 | 22 | 38.8843 | 25.4336 | 64.3179 | 60.7546 | 35.4482 | 21.2423 | 22 | 7.5943 | 7.5943 | 22 | 19.7447 | 10.6321 | 30.3767 | 22 | 24.1475 | 64.7654 | 87.447 | 22 | 16.0984 | 0 | 21.1981 | 22 | 102 | 0 | 77.941 | 26.334 | 0 | 206.275 | 22 | 0 | 17.556 | 10.929
23 | 104.0395 | 26.9447 | 89.458 | 220.4422 | 0 | 220.4422 | 220.4422 | 23 | 0 | 17.9631 | 10.929 | 23 | 71.5664 | 71.5664 | 62.5848 | 16.0158 | 16.842 | 23 | 108.4581 | 26.9447 | 85.0394 | 220.4422 | 0 | 220.4422 | 220.4422 | 23 | 0 | 17.9631 | 10.929 | 10.929 | 23 | 68.0315 | 3.5349 | 71.5664 | 62.5848 | 13.9191 | 13.913 | 23 | 7.8231 | 7.8231 | 23 | 20.2833 | 10.9523 | 31.2356 | 23 | 36.9549 | 38.436 | 71.4634 | 23 | 24.6366 | 0 | 45.297 | 23 | 138 | 0 | 81.7591 | 0.68306 | 0 | 220.4422 | 23 | 0 | 0.45537 | 10.929
24 | 136.6445 | 15.7104 | 85.7388 | 238.0937 | 0 | 238.0937 | 238.0937 | 24 | 0 | 10.4736 | 10.929 | 24 | 68.591 | 68.591 | 63.3542 | 32.5486 | 16.7937 | 24 | 141.6285 | 15.7104 | 80.7548 | 238.0937 | 0 | 238.0937 | 238.0937 | 24 | 0 | 10.4736 | 10.929 | 10.929 | 24 | 64.6038 | 3.9872 | 68.591 | 63.3542 | 33.9958 | 15.883 | 24 | 7.9193 | 7.9193 | 24 | 23.744 | 11.087 | 34.831 | 24 | 62.9689 | 35.9981 | 101.8596 | 24 | 41.9793 | 0 | 21.8034 | 24 | 102 | 0 | 64.3833 | 21.7104 | 50 | 238.0937 | 24 | 0 | 14.4736 | 10.929
25 | 126.7648 | 6.5253 | 82.6444 | 215.9344 | 0 | 215.9344 | 215.9344 | 25 | 0 | 4.3502 | 10.929 | 25 | 66.1155 | 66.1155 | 63.9404 | 15.8521 | 13.0023 | 25 | 127.6513 | 6.5253 | 81.7579 | 215.9344 | 0 | 215.9344 | 215.9344 | 25 | 0 | 4.3502 | 10.929 | 10.929 | 25 | 65.4063 | 0.70922 | 66.1155 | 63.9404 | 14.2771 | 15.9312 | 25 | 7.9926 | 7.9926 | 25 | 22.8879 | 11.1896 | 34.0774 | 25 | 32.9665 | 147.2182 | 189.9183 | 25 | 21.9776 | 0 | 16.3934 | 25 | 114 | 0 | 85.7712 | 16.1633 | 0 | 215.9344 | 25 | 0 | 10.7755 | 10.929
26 | 129.9719 | 28.3108 | 87.251 | 245.5337 | 0 | 245.5337 | 245.5337 | 26 | 0 | 18.8739 | 10.929 | 26 | 69.8008 | 69.8008 | 60.3639 | 9.9115 | 20.2332 | 26 | 130.5293 | 28.3108 | 86.6936 | 245.5337 | 0 | 245.5337 | 245.5337 | 26 | 0 | 18.8739 | 10.929 | 10.929 | 26 | 69.3549 | 0.44591 | 69.8008 | 60.3639 | 10.6121 | 25.2855 | 26 | 7.5455 | 7.5455 | 26 | 20.4733 | 10.5637 | 31.037 | 26 | 14.123 | 187.9517 | 201.5102 | 26 | 9.4153 | 0 | 16.3934 | 26 | 121.1552 | 0 | 25.2079 | 15.0273 | 160 | 245.5337 | 26 | 0 | 10.0182 | 10.929
27 | 173.4254 | 15.0273 | 71.2942 | 259.7469 | 0 | 259.7469 | 259.7469 | 27 | 0 | 10.0182 | 10.929 | 27 | 57.0353 | 57.0353 | 52.0262 | 19.5587 | 23.3657 | 27 | 176.638 | 15.0273 | 68.0815 | 259.7469 | 0 | 259.7469 | 259.7469 | 27 | 0 | 10.0182 | 10.929 | 10.929 | 27 | 54.4652 | 2.5701 | 57.0353 | 52.0262 | 20.2951 | 21.913 | 27 | 6.5033 | 6.5033 | 27 | 19.5349 | 9.1046 | 28.6394 | 27 | 34.8434 | 160.8769 | 195.7262 | 27 | 23.229 | 0 | 16.3934 | 27 | 126 | 0 | 0 | 13.3559 | 140 | 259.7469 | 27 | 0 | 8.9039 | 10.929
28 | 175.5672 | 5.8422 | 66.4127 | 247.8221 | 0 | 247.8221 | 247.8221 | 28 | 0 | 3.8948 | 10.929 | 28 | 53.1301 | 53.1301 | 51.1827 | 8.9534 | 19.9312 | 28 | 179.4548 | 5.8422 | 62.5251 | 247.8221 | 0 | 247.8221 | 247.8221 | 28 | 0 | 3.8948 | 10.929 | 10.929 | 28 | 50.0201 | 3.1101 | 53.1301 | 51.1827 | 8.4471 | 17.9012 | 28 | 6.3978 | 6.3978 | 28 | 17.5125 | 8.957 | 26.4695 | 28 | 0 | 170.6619 | 171.4711 | 28 | 0 | 0 | 16.3934 | 28 | 102 | 0 | 0 | 22.1633 | 40 | 247.8221 | 28 | 0 | 14.7755 | 10.929
29 | 148.366 | 17.0765 | 84.7944 | 250.237 | 0 | 250.237 | 250.237 | 29 | 0 | 11.3843 | 10.929 | 29 | 67.8356 | 67.8356 | 62.1434 | 14.8498 | 16.3383 | 29 | 151.0506 | 17.0765 | 82.1098 | 250.237 | 0 | 250.237 | 250.237 | 29 | 0 | 11.3843 | 10.929 | 10.929 | 29 | 65.6879 | 2.1477 | 67.8356 | 62.1434 | 13.4844 | 20.4918 | 29 | 7.7679 | 7.7679 | 29 | 16.9036 | 10.8751 | 27.7787 | 29 | 0 | 101.0861 | 101.0861 | 29 | 0 | 0 | 16.3934 | 29 | 120 | 0 | 12.8042 | 14.3443 | 150 | 250.237 | 29 | 0 | 9.5628 | 10.929
30 | 118.9442 | 25.5786 | 89.0747 | 233.5974 | 0 | 233.5974 | 233.5974 | 30 | 0 | 17.0524 | 10.929 | 30 | 71.2598 | 71.2598 | 62.7336 | 1.9477 | 20.4918 | 30 | 121.8765 | 25.5786 | 86.1423 | 233.5974 | 0 | 233.5974 | 233.5974 | 30 | 0 | 17.0524 | 10.929 | 10.929 | 30 | 68.9139 | 2.3459 | 71.2598 | 62.7336 | 1.9937 | 16.4299 | 30 | 7.8417 | 7.8417 | 30 | 20.609 | 10.9784 | 31.5874 | 30 | 36 | 134.638 | 170.638 | 30 | 24 | 0 | 16.3934 | 30 | 120 | 6 | 0 | 15.7104 | 60 | 233.5974 | 30 | 0 | 10.4736 | 10.929
31 | 129.0756 | 11.3067 | 84.2112 | 224.5934 | 0 | 224.5934 | 224.5934 | 31 | 0 | 7.5378 | 10.929 | 31 | 67.369 | 67.369 | 63.6001 | 7.6716 | 16.2882 | 31 | 149.5432 | 11.3067 | 63.7435 | 224.5934 | 0 | 224.5934 | 224.5934 | 31 | 0 | 7.5378 | 10.929 | 10.929 | 31 | 50.9948 | 16.3741 | 67.369 | 63.6001 | 7.3778 | 17.913 | 31 | 7.95 | 7.95 | 31 | 18.5684 | 11.13 | 29.6984 | 31 | 45 | 177.909 | 222.909 | 31 | 30 | 0 | 16.3934 | 31 | 120 | 0 | 55.3687 | 22.3934 | 0 | 224.5934 | 31 | 0 | 14.929 | 10.929
32 | 130.3642 | 12.2951 | 85.8555 | 228.5147 | 0 | 228.5147 | 228.5147 | 32 | 0 | 8.1967 | 10.929 | 32 | 68.6844 | 68.6844 | 64.586 | 8.1833 | 18.6152 | 32 | 159.2976 | 12.2951 | 56.922 | 228.5147 | 0 | 228.5147 | 228.5147 | 32 | 0 | 8.1967 | 10.929 | 10.929 | 32 | 45.5376 | 23.1468 | 68.6844 | 64.586 | 12.7982 | 17.9563 | 32 | 8.0733 | 8.0733 | 32 | 10.0706 | 11.3026 | 21.3731 | 32 | 60.7548 | 216.7817 | 277.5365 | 32 | 40.5032 | 0 | 35.8606 | 32 | 108 | 0 | 96.4429 | 11.7596 | 30 | 228.5147 | 32 | 0 | 7.8397 | 10.929
33 | 127.7775 | 24.1475 | 86.8471 | 238.7721 | 0 | 238.7721 | 238.7721 | 33 | 0 | 16.0984 | 10.929 | 33 | 69.4777 | 69.4777 | 61.4285 | 11.77 | 15.7778 | 33 | 137.0474 | 24.1475 | 77.5772 | 238.7721 | 0 | 238.7721 | 238.7721 | 33 | 0 | 16.0984 | 10.929 | 10.929 | 33 | 62.0617 | 7.4159 | 69.4777 | 61.4285 | 6.6511 | 16.0797 | 33 | 7.6786 | 7.6786 | 33 | 11.2217 | 10.75 | 21.9716 | 33 | 47.7332 | 188.3626 | 236.0958 | 33 | 31.8221 | 0 | 58.4354 | 33 | 118.2087 | 0 | 20.5024 | 15.0273 | 90 | 238.7721 | 33 | 0 | 10.0182 | 10.929
34 | 165.6038 | 18.5075 | 73.169 | 257.2803 | 0 | 257.2803 | 257.2803 | 34 | 0 | 12.3383 | 10.929 | 34 | 58.5352 | 58.5352 | 52.366 | 3.712 | 16.3315 | 34 | 169.8916 | 18.5075 | 68.8811 | 257.2803 | 0 | 257.2803 | 257.2803 | 34 | 0 | 12.3383 | 10.929 | 10.929 | 34 | 55.1049 | 3.4303 | 58.5352 | 52.366 | 8.7797 | 17.3593 | 34 | 6.5458 | 6.5458 | 34 | 12.9107 | 9.1641 | 22.0747 | 34 | 108 | 119.0916 | 226.2652 | 34 | 72 | 0 | 60.6783 | 34 | 79.1385 | 0 | 0 | 18.4426 | 210 | 257.2803 | 34 | 0 | 12.2951 | 10.929
35 | 161.0514 | 12 | 68.9578 | 242.0092 | 0 | 242.0092 | 242.0092 | 35 | 0 | 8 | 10.929 | 35 | 55.1662 | 55.1662 | 51.1662 | 10.2009 | 12.5469 | 35 | 163.811 | 12 | 66.1981 | 242.0092 | 0 | 242.0092 | 242.0092 | 35 | 0 | 8 | 10.929 | 10.929 | 35 | 52.9585 | 2.2077 | 55.1662 | 51.1662 | 6.4934 | 18.3497 | 35 | 6.3958 | 6.3958 | 35 | 13.5826 | 8.9541 | 22.5367 | 35 | 130.8132 | 86.9492 | 218.5888 | 35 | 87.2088 | 0 | 70.8227 | 35 | 126 | 0 | 0 | 10.6236 | 80 | 242.0092 | 35 | 0 | 7.0824 | 10.929
36 | 115.3425 | 20.7869 | 87.9868 | 224.1162 | 0 | 224.1162 | 224.1162 | 36 | 0 | 13.8579 | 10.929 | 36 | 70.3895 | 70.3895 | 63.4605 | 6.1686 | 17.9012 | 36 | 119.687 | 20.7869 | 83.6424 | 224.1162 | 0 | 224.1162 | 224.1162 | 36 | 0 | 13.8579 | 10.929 | 10.929 | 36 | 66.9139 | 3.4756 | 70.3895 | 63.4605 | 6.3118 | 18.75 | 36 | 7.9326 | 7.9326 | 36 | 8.2827 | 11.1056 | 19.3883 | 36 | 95.3661 | 134.6719 | 230.0379 | 36 | 63.5774 | 0 | 72.363 | 36 | 102 | 0 | 47.0666 | 27.4802 | 0 | 224.1162 | 36 | 0 | 18.3201 | 10.929
37 | 130.4339 | 9.5628 | 90.0244 | 230.0211 | 0 | 230.0211 | 230.0211 | 37 | 0 | 6.3752 | 10.929 | 37 | 72.0195 | 72.0195 | 68.8319 | 13.3083 | 21.2974 | 37 | 133.8084 | 9.5628 | 86.6499 | 230.0211 | 0 | 230.0211 | 230.0211 | 37 | 0 | 6.3752 | 10.929 | 10.929 | 37 | 69.3199 | 2.6996 | 72.0195 | 68.8319 | 17.1283 | 24.2332 | 37 | 8.604 | 8.604 | 37 | 9.6172 | 12.0456 | 21.6628 | 37 | 64.3136 | 139.4517 | 202.7004 | 37 | 42.8757 | 0 | 48.1398 | 37 | 114 | 0 | 78.8203 | 9.7104 | 40 | 230.0211 | 37 | 0 | 6.4736 | 10.929
38 | 139.1798 | 12.6728 | 91.1168 | 242.9694 | 0 | 242.9694 | 242.9694 | 38 | 0 | 8.4485 | 10.929 | 38 | 72.8934 | 72.8934 | 68.6692 | 16.8075 | 22.1963 | 38 | 150.9625 | 12.6728 | 79.3341 | 242.9694 | 0 | 242.9694 | 242.9694 | 38 | 0 | 8.4485 | 10.929 | 10.929 | 38 | 63.4673 | 9.4261 | 72.8934 | 68.6692 | 16.4997 | 12.4206 | 38 | 8.5836 | 8.5836 | 38 | 9.096 | 12.0171 | 21.1132 | 38 | 105.3094 | 18.4789 | 124.8532 | 38 | 70.2063 | 0 | 50.1773 | 38 | 111.8726 | 0 | 49.6837 | 17.0765 | 90 | 242.9694 | 38 | 0 | 11.3843 | 10.929
39 | 159.6929 | 26.9447 | 94.1186 | 280.7562 | 0 | 280.7562 | 280.7562 | 39 | 0 | 17.9631 | 10.929 | 39 | 75.2949 | 75.2949 | 66.3133 | 17.8571 | 13.9401 | 39 | 176.3591 | 26.9447 | 77.4524 | 280.7562 | 0 | 280.7562 | 280.7562 | 39 | 0 | 17.9631 | 10.929 | 10.929 | 39 | 61.9619 | 13.333 | 75.2949 | 66.3133 | 19.3206 | 18.5719 | 39 | 8.2892 | 8.2892 | 39 | 7.9806 | 11.6048 | 19.5854 | 39 | 22.3486 | 49.8051 | 72.1537 | 39 | 14.899 | 0 | 43.7999 | 39 | 23.3008 | 0 | 0 | 21.0273 | 200 | 280.7562 | 39 | 0 | 14.0182 | 10.929
40 | 176.4772 | 18.4426 | 90.7926 | 285.7124 | 0 | 285.7124 | 285.7124 | 40 | 0 | 12.2951 | 10.929 | 40 | 72.6341 | 72.6341 | 66.4865 | 13.7195 | 16.3383 | 40 | 193.507 | 18.4426 | 73.7628 | 285.7124 | 0 | 285.7124 | 285.7124 | 40 | 0 | 12.2951 | 10.929 | 10.929 | 40 | 59.0102 | 13.6238 | 72.6341 | 66.4865 | 8.933 | 18.4117 | 40 | 8.3108 | 8.3108 | 40 | 9.5991 | 11.6351 | 21.2343 | 40 | 27.2715 | 39.9431 | 67.2146 | 40 | 18.181 | 0 | 30.9965 | 40 | 72.049 | 0 | 0 | 6.6728 | 230 | 285.7124 | 40 | 0 | 4.4485 | 10.929
41 | 207.3223 | 11.3067 | 78.6804 | 297.3095 | 0 | 297.3095 | 297.3095 | 41 | 0 | 7.5378 | 10.929 | 41 | 62.9443 | 62.9443 | 59.1755 | 16.08 | 17.5009 | 41 | 223.6851 | 11.3067 | 62.3177 | 297.3095 | 0 | 297.3095 | 297.3095 | 41 | 0 | 7.5378 | 10.929 | 10.929 | 41 | 49.8542 | 13.0902 | 62.9443 | 59.1755 | 14.2812 | 19.4208 | 41 | 7.3969 | 7.3969 | 41 | 12.6573 | 10.3557 | 23.013 | 41 | 44.028 | 1.1014 | 44.8756 | 41 | 29.352 | 0 | 16.7826 | 41 | 108 | 0 | 0 | 16.3934 | 210 | 297.3095 | 41 | 0 | 10.929 | 10.929
42 | 186.6654 | 9.5628 | 74.466 | 270.6943 | 0 | 270.6943 | 270.6943 | 42 | 0 | 6.3752 | 10.929 | 42 | 59.5728 | 59.5728 | 56.3852 | 12.9608 | 20.4299 | 42 | 195.317 | 9.5628 | 65.8144 | 270.6943 | 0 | 270.6943 | 270.6943 | 42 | 0 | 6.3752 | 10.929 | 10.929 | 42 | 52.6515 | 6.9213 | 59.5728 | 56.3852 | 15.6033 | 14.5739 | 42 | 7.0481 | 7.0481 | 42 | 14.7787 | 9.8674 | 24.6461 | 42 | 41.23 | 0 | 41.4837 | 42 | 27.4867 | 0 | 16.3934 | 42 | 82.4148 | 0 | 0 | 20.7322 | 210 | 270.6943 | 42 | 0 | 13.8215 | 10.929
43 | 158.5662 | 18 | 87.2802 | 263.8464 | 0 | 263.8464 | 263.8464 | 43 | 0 | 12 | 10.929 | 43 | 69.8242 | 69.8242 | 63.8242 | 19.8358 | 13.1645 | 43 | 159.4073 | 18 | 86.4391 | 263.8464 | 0 | 263.8464 | 263.8464 | 43 | 0 | 12 | 10.929 | 10.929 | 43 | 69.1513 | 0.6729 | 69.8242 | 63.8242 | 18.5389 | 15.7778 | 43 | 7.978 | 7.978 | 43 | 17.0921 | 11.1692 | 28.2614 | 43 | 38.1496 | 61.2641 | 94.8259 | 43 | 25.433 | 0 | 16.3934 | 43 | 33.4095 | 0 | 0 | 15.7753 | 210 | 263.8464 | 43 | 0 | 10.5169 | 10.929
44 | 171.5636 | 14.1038 | 84.0897 | 269.7571 | 0 | 269.7571 | 269.7571 | 44 | 0 | 9.4026 | 10.929 | 44 | 67.2717 | 67.2717 | 62.5705 | 24.3942 | 19.8761 | 44 | 174.579 | 14.1038 | 81.0742 | 269.7571 | 0 | 269.7571 | 269.7571 | 44 | 0 | 9.4026 | 10.929 | 10.929 | 44 | 64.8594 | 2.4124 | 67.2717 | 62.5705 | 29.823 | 16.7436 | 44 | 7.8213 | 7.8213 | 44 | 15.8978 | 10.9498 | 26.8476 | 44 | 19.6688 | 66.0826 | 90.3391 | 44 | 13.1125 | 0 | 16.3934 | 44 | 44.8896 | 0 | 0 | 23.7596 | 200 | 269.7571 | 44 | 0 | 15.8397 | 10.929
45 | 171.154 | 28.9939 | 89.5606 | 289.7084 | 0 | 289.7084 | 289.7084 | 45 | 0 | 19.3292 | 10.929 | 45 | 71.6485 | 71.6485 | 61.9839 | 11.8734 | 11.3292 | 45 | 174.2298 | 28.9939 | 86.4847 | 289.7084 | 0 | 289.7084 | 289.7084 | 45 | 0 | 19.3292 | 10.929 | 10.929 | 45 | 69.1878 | 2.4607 | 71.6485 | 61.9839 | 5.9005 | 17.8028 | 45 | 7.748 | 7.748 | 45 | 16.5312 | 10.8472 | 27.3784 | 45 | 5.7137 | 98.6691 | 104.3828 | 45 | 3.8091 | 0 | 19.9496 | 45 | 19.0539 | 0 | 0 | 5.3067 | 230 | 289.7084 | 45 | 0 | 3.5378 | 10.929
46 | 169.9156 | 14.3443 | 83.0996 | 267.3595 | 0 | 267.3595 | 267.3595 | 46 | 0 | 9.5628 | 10.929 | 46 | 66.4797 | 66.4797 | 61.6983 | 4.5116 | 21.439 | 46 | 170.5278 | 14.3443 | 82.4874 | 267.3595 | 0 | 267.3595 | 267.3595 | 46 | 0 | 9.5628 | 10.929 | 10.929 | 46 | 65.9899 | 0.48976 | 66.4797 | 61.6983 | 8.5003 | 12.5469 | 46 | 7.7123 | 7.7123 | 46 | 20.157 | 10.7972 | 30.9542 | 46 | 11.8697 | 122.7217 | 132.5772 | 46 | 7.9131 | 0 | 16.6961 | 46 | 108 | 0 | 0 | 16.3934 | 160 | 267.3595 | 46 | 0 | 10.929 | 10.929
47 | 143.5648 | 18.4426 | 79.5188 | 241.5262 | 0 | 241.5262 | 241.5262 | 47 | 0 | 12.2951 | 10.929 | 47 | 63.6151 | 63.6151 | 57.4675 | 12.4403 | 14.929 | 47 | 146.747 | 18.4426 | 76.3366 | 241.5262 | 0 | 241.5262 | 241.5262 | 47 | 0 | 12.2951 | 10.929 | 10.929 | 47 | 61.0692 | 2.5458 | 63.6151 | 57.4675 | 10.1033 | 19.3224 | 47 | 7.1834 | 7.1834 | 47 | 19.8771 | 10.0568 | 29.9339 | 47 | 63 | 125.6062 | 190.6204 | 47 | 42 | 0 | 18.7714 | 47 | 114 | 0 | 0 | 20.7971 | 120 | 241.5262 | 47 | 0 | 13.8648 | 10.929
48 | 134.4263 | 13.6612 | 69.4453 | 217.5329 | 0 | 217.5329 | 217.5329 | 48 | 0 | 9.1075 | 10.929 | 48 | 55.5563 | 55.5563 | 51.0025 | 18.5052 | 14.0114 | 48 | 135.3861 | 13.6612 | 68.4855 | 217.5329 | 0 | 217.5329 | 217.5329 | 48 | 0 | 9.1075 | 10.929 | 10.929 | 48 | 54.7884 | 0.76786 | 55.5563 | 51.0025 | 24.831 | 18.3566 | 48 | 6.3753 | 6.3753 | 48 | 20.8979 | 8.9254 | 29.8233 | 48 | 24.1833 | 213.0788 | 237.2621 | 48 | 16.1222 | 0 | 43.8486 | 48 | 120 | 0 | 0 | 11.9898 | 30 | 217.5329 | 48 | 0 | 7.9932 | 10.929
49 | 122.2944 | 17.7596 | 70.5333 | 210.5873 | 0 | 210.5873 | 210.5873 | 49 | 0 | 11.8397 | 10.929 | 49 | 56.4267 | 56.4267 | 50.5068 | 19.9545 | 18.4117 | 49 | 124.0662 | 17.7596 | 68.7615 | 210.5873 | 0 | 210.5873 | 210.5873 | 49 | 0 | 11.8397 | 10.929 | 10.929 | 49 | 55.0092 | 1.4174 | 56.4267 | 50.5068 | 11.5014 | 13.9563 | 49 | 6.3134 | 6.3134 | 49 | 25.3192 | 8.8387 | 34.1579 | 49 | 82.1595 | 182.5235 | 264.683 | 49 | 54.773 | 0 | 54.5117 | 49 | 114 | 48 | 0 | 20.7971 | 0 | 210.5873 | 49 | 0 | 13.8648 | 10.929
50 | 121.1209 | 11.9898 | 85.3537 | 218.4643 | 0 | 218.4643 | 218.4643 | 50 | 0 | 7.9932 | 10.929 | 50 | 68.2829 | 68.2829 | 64.2864 | 4.3154 | 18.3566 | 50 | 121.7995 | 11.9898 | 84.6751 | 218.4643 | 0 | 218.4643 | 218.4643 | 50 | 0 | 7.9932 | 10.929 | 10.929 | 50 | 67.7401 | 0.54286 | 68.2829 | 64.2864 | 6.0957 | 11.6362 | 50 | 8.0358 | 8.0358 | 50 | 19.0521 | 11.2501 | 30.3022 | 50 | 126 | 130.5305 | 256.5305 | 50 | 84 | 0 | 59.5488 | 50 | 108 | 84 | 3.4989 | 24.0546 | 0 | 218.4643 | 50 | 0 | 16.0364 | 10.929
51 | 92.2337 | 22.8463 | 86.6528 | 201.7328 | 0 | 201.7328 | 201.7328 | 51 | 0 | 15.2309 | 10.929 | 51 | 69.3222 | 69.3222 | 61.7068 | 14.1819 | 12.8488 | 51 | 97.3211 | 22.8463 | 81.5654 | 201.7328 | 0 | 201.7328 | 201.7328 | 51 | 0 | 15.2309 | 10.929 | 10.929 | 51 | 65.2523 | 4.0699 | 69.3222 | 61.7068 | 17.6382 | 18.3566 | 51 | 7.7134 | 7.7134 | 51 | 18.3862 | 10.7987 | 29.1849 | 51 | 50.4658 | 132.2878 | 182.7536 | 51 | 33.6438 | 0 | 54.7982 | 51 | 138 | 30 | 16.4982 | 6 | 0 | 201.7328 | 51 | 0 | 4 | 10.929
52 | 98.9331 | 3.11 | 82.3659 | 184.409 | 0 | 184.409 | 184.409 | 52 | 0 | 2.0733 | 10.929 | 52 | 65.8927 | 65.8927 | 64.8561 | 13.5812 | 11.6362 | 52 | 115.8347 | 3.11 | 65.4644 | 184.409 | 0 | 184.409 | 184.409 | 52 | 0 | 2.0733 | 10.929 | 10.929 | 52 | 52.3715 | 13.5213 | 65.8927 | 64.8561 | 10.1396 | 18.0768 | 52 | 8.107 | 8.107 | 52 | 16.5041 | 11.3498 | 27.8539 | 52 | 99 | 97.5582 | 193.2388 | 52 | 66 | 0 | 50.988 | 52 | 114 | 42 | 17.7544 | 14.722 | 0 | 184.409 | 52 | 0 | 9.8147 | 10.929
53 | 91.7781 | 17.0765 | 85.6106 | 194.4652 | 0 | 194.4652 | 194.4652 | 53 | 0 | 11.3843 | 10.929 | 53 | 68.4885 | 68.4885 | 62.7963 | 11.3366 | 19.6458 | 53 | 98.0286 | 17.0765 | 79.3601 | 194.4652 | 0 | 194.4652 | 194.4652 | 53 | 0 | 11.3843 | 10.929 | 10.929 | 53 | 63.4881 | 5.0004 | 68.4885 | 62.7963 | 10.4673 | 15.2666 | 53 | 7.8495 | 7.8495 | 53 | 15.7078 | 10.9894 | 26.6971 | 53 | 81.2613 | 89.1992 | 173.7799 | 53 | 54.1742 | 0 | 51.8419 | 53 | 120 | 36 | 17.228 | 20.1141 | 0 | 194.4652 | 53 | 0 | 13.4094 | 10.929
54 | 82.1443 | 26.2616 | 83.9779 | 192.3838 | 0 | 192.3838 | 192.3838 | 54 | 0 | 17.5077 | 10.929 | 54 | 67.1823 | 67.1823 | 58.4284 | 9.9661 | 13.6984 | 54 | 84.2328 | 26.2616 | 81.8894 | 192.3838 | 0 | 192.3838 | 192.3838 | 54 | 0 | 17.5077 | 10.929 | 10.929 | 54 | 65.5116 | 1.6708 | 67.1823 | 58.4284 | 11.9145 | 16.037 | 54 | 7.3036 | 7.3036 | 54 | 19.6371 | 10.225 | 29.8621 | 54 | 86.7604 | 17.5152 | 104.2756 | 54 | 57.8403 | 0 | 51.75 | 54 | 114 | 30 | 27.68 | 17.7596 | 0 | 192.3838 | 54 | 0 | 11.8397 | 10.929
55 | 123.929 | 14.0389 | 73.2173 | 211.1852 | 0 | 211.1852 | 211.1852 | 55 | 0 | 9.3593 | 10.929 | 55 | 58.5738 | 58.5738 | 53.8942 | 15.0539 | 16.2757 | 55 | 134.7959 | 14.0389 | 62.3504 | 211.1852 | 0 | 211.1852 | 211.1852 | 55 | 0 | 9.3593 | 10.929 | 10.929 | 55 | 49.8803 | 8.6935 | 58.5738 | 53.8942 | 15.9335 | 13.2515 | 55 | 6.7368 | 6.7368 | 55 | 15.3083 | 9.4315 | 24.7397 | 55 | 80.7941 | 0 | 80.7941 | 55 | 53.8628 | 0 | 63.786 | 55 | 108 | 18 | 63.8785 | 11.3067 | 10 | 211.1852 | 55 | 0 | 7.5378 | 10.929
56 | 167.7856 | 8.8798 | 67.4596 | 244.1251 | 0 | 244.1251 | 244.1251 | 56 | 0 | 5.9199 | 10.929 | 56 | 53.9677 | 53.9677 | 51.0078 | 31.4594 | 15.0279 | 56 | 197.5225 | 8.8798 | 37.7227 | 244.1251 | 0 | 244.1251 | 244.1251 | 56 | 0 | 5.9199 | 10.929 | 10.929 | 56 | 30.1782 | 23.7895 | 53.9677 | 51.0078 | 29.9662 | 18.0615 | 56 | 6.376 | 6.376 | 56 | 14.8021 | 8.9264 | 23.7285 | 56 | 77.02 | 0 | 69.702 | 56 | 51.3466 | 3.4102 | 63.8994 | 56 | 102 | 54 | 26.6257 | 28.1633 | 40 | 244.1251 | 56 | 0 | 18.7755 | 10.929
57 | 126.8015 | 23.224 | 84.5665 | 234.5921 | 0 | 234.5921 | 234.5921 | 57 | 0 | 15.4827 | 10.929 | 57 | 67.6532 | 67.6532 | 59.9119 | 5.7268 | 13.2515 | 57 | 134.8447 | 23.224 | 76.5233 | 234.5921 | 0 | 234.5921 | 234.5921 | 57 | 0 | 15.4827 | 10.929 | 10.929 | 57 | 61.2187 | 6.4346 | 67.6532 | 59.9119 | 4.4637 | 18.2619 | 57 | 7.489 | 7.489 | 57 | 11.5232 | 10.4846 | 22.0078 | 57 | 78.2187 | 0 | 80.1634 | 57 | 52.1458 | 0 | 53.6794 | 57 | 126 | 36 | 8.8974 | 9.9406 | 50 | 234.5921 | 57 | 0 | 6.627 | 10.929
58 | 96.3143 | 10.2459 | 81.4711 | 188.0313 | 0 | 188.0313 | 188.0313 | 58 | 0 | 6.8306 | 10.929 | 58 | 65.1769 | 65.1769 | 61.7616 | 9.8025 | 14.5169 | 58 | 99.7748 | 10.2459 | 78.0106 | 188.0313 | 0 | 188.0313 | 188.0313 | 58 | 0 | 6.8306 | 10.929 | 10.929 | 58 | 62.4085 | 2.7684 | 65.1769 | 61.7616 | 9.1326 | 20.8464 | 58 | 7.7202 | 7.7202 | 58 | 18.1558 | 10.8083 | 28.9641 | 58 | 83.1806 | 0 | 88.5539 | 58 | 55.4538 | 0 | 42.7136 | 58 | 108 | 36 | 24.9583 | 16.1633 | 0 | 188.0313 | 58 | 0 | 10.7755 | 10.929
59 | 82.6679 | 16.3654 | 72.3182 | 171.3515 | 0 | 171.3515 | 171.3515 | 59 | 0 | 10.9103 | 10.929 | 59 | 57.8545 | 57.8545 | 52.3994 | 3.8859 | 18.2619 | 59 | 102.0171 | 16.3654 | 52.969 | 171.3515 | 0 | 171.3515 | 171.3515 | 59 | 0 | 10.9103 | 10.929 | 10.929 | 59 | 42.3752 | 15.4793 | 57.8545 | 52.3994 | 4.8728 | 23.1489 | 59 | 6.5499 | 6.5499 | 59 | 21.6083 | 9.1699 | 30.7781 | 59 | 58.5897 | 28.0837 | 86.6734 | 59 | 39.0598 | 0 | 49.3396 | 59 | 126 | 6 | 24.3242 | 15.0273 | 0 | 171.3515 | 59 | 0 | 10.0182 | 10.929
60 | 83.9552 | 24 | 85.9637 | 193.919 | 0 | 193.919 | 193.919 | 60 | 0 | 16 | 10.929 | 60 | 68.771 | 68.771 | 60.771 | 25.2564 | 24.8464 | 60 | 100.1607 | 24 | 69.7582 | 193.919 | 0 | 193.919 | 193.919 | 60 | 0 | 16 | 10.929 | 10.929 | 60 | 55.8066 | 12.9644 | 68.771 | 60.771 | 24.8831 | 18.2428 | 60 | 7.5964 | 7.5964 | 60 | 20.2482 | 10.6349 | 30.8831 | 60 | 92.5346 | 0 | 86.8758 | 60 | 61.6898 | 12.3245 | 63.3428 | 60 | 126 | 0 | 49.919 | 18 | 0 | 193.919 | 60 | 0 | 12 | 10.929
61 | 105.1005 | 20.7322 | 83.6104 | 209.4431 | 0 | 209.4431 | 209.4431 | 61 | 0 | 13.8215 | 10.929 | 61 | 66.8883 | 66.8883 | 59.9775 | 10.498 | 23.1489 | 61 | 110.6228 | 20.7322 | 78.088 | 209.4431 | 0 | 209.4431 | 209.4431 | 61 | 0 | 13.8215 | 10.929 | 10.929 | 61 | 62.4704 | 4.4179 | 66.8883 | 59.9775 | 11.7662 | 26.723 | 61 | 7.4972 | 7.4972 | 61 | 19.9315 | 10.4961 | 30.4275 | 61 | 60.2133 | 0 | 60.3713 | 61 | 40.1422 | 10 | 53.9118 | 61 | 114 | 6 | 68.6562 | 20.7869 | 0 | 209.4431 | 61 | 0 | 13.8579 | 10.929
62 | 126.9732 | 11.3067 | 76.8036 | 215.0835 | 0 | 215.0835 | 215.0835 | 62 | 0 | 7.5378 | 10.929 | 62 | 61.4429 | 61.4429 | 57.674 | 18.266 | 17.0331 | 62 | 128.873 | 11.3067 | 74.9038 | 215.0835 | 0 | 215.0835 | 215.0835 | 62 | 0 | 7.5378 | 10.929 | 10.929 | 62 | 59.923 | 1.5199 | 61.4429 | 57.674 | 17.8262 | 21.9743 | 62 | 7.2092 | 7.2092 | 62 | 17.922 | 10.0929 | 28.0149 | 62 | 60.565 | 0 | 60.1214 | 62 | 40.3767 | 1.0807 | 52.9498 | 62 | 126 | 6 | 74.3615 | 8.722 | 0 | 215.0835 | 62 | 0 | 5.8147 | 10.929
63 | 130.8541 | 8.1967 | 65.7292 | 204.7801 | 0 | 204.7801 | 204.7801 | 63 | 0 | 5.4645 | 10.929 | 63 | 52.5834 | 52.5834 | 49.8512 | 16.1999 | 26.25 | 63 | 133.8867 | 8.1967 | 62.6967 | 204.7801 | 0 | 204.7801 | 204.7801 | 63 | 0 | 5.4645 | 10.929 | 10.929 | 63 | 50.1574 | 2.426 | 52.5834 | 49.8512 | 15.1106 | 21.2353 | 63 | 6.2314 | 6.2314 | 63 | 22.342 | 8.724 | 31.0659 | 63 | 76.6825 | 0 | 82.627 | 63 | 51.1216 | 14.9077 | 57.4572 | 63 | 102 | 90 | 3.2915 | 26.2616 | 0 | 204.7801 | 63 | 0 | 17.5077 | 10.929
64 | 115.8863 | 17.0765 | 71.57 | 204.5329 | 0 | 204.5329 | 204.5329 | 64 | 0 | 11.3843 | 10.929 | 64 | 57.256 | 57.256 | 51.5638 | 9.6873 | 24.7157 | 64 | 122.0403 | 17.0765 | 65.4161 | 204.5329 | 0 | 204.5329 | 204.5329 | 64 | 0 | 11.3843 | 10.929 | 10.929 | 64 | 52.3329 | 4.9231 | 57.256 | 51.5638 | 10.7868 | 24.2274 | 64 | 6.4455 | 6.4455 | 64 | 19.1113 | 9.0237 | 28.135 | 64 | 116.962 | 0 | 106.7749 | 64 | 77.9747 | 0 | 55.6845 | 64 | 126 | 0 | 52.197 | 9.5628 | 0 | 204.5329 | 64 | 0 | 6.3752 | 10.929
65 | 87.0801 | 26.9447 | 89.4559 | 203.4807 | 0 | 203.4807 | 203.4807 | 65 | 0 | 17.9631 | 10.929 | 65 | 71.5647 | 71.5647 | 62.5832 | 14.9623 | 20.632 | 65 | 89.0261 | 26.9447 | 87.5099 | 203.4807 | 0 | 203.4807 | 203.4807 | 65 | 0 | 17.9631 | 10.929 | 10.929 | 65 | 70.0079 | 1.5568 | 71.5647 | 62.5832 | 13.7043 | 23.1196 | 65 | 7.8229 | 7.8229 | 65 | 21.8568 | 10.9521 | 32.8089 | 65 | 51.1601 | 0 | 61.3472 | 65 | 34.1067 | 2.7472 | 65.1749 | 65 | 120 | 0 | 67.7703 | 15.7104 | 0 | 203.4807 | 65 | 0 | 10.4736 | 10.929
66 | 150.9292 | 10.2459 | 83.0879 | 244.263 | 0 | 244.263 | 244.263 | 66 | 0 | 6.8306 | 10.929 | 66 | 66.4704 | 66.4704 | 63.0551 | 14.8498 | 24.2274 | 66 | 177.1375 | 10.2459 | 56.8796 | 244.263 | 0 | 244.263 | 244.263 | 66 | 0 | 6.8306 | 10.929 | 10.929 | 66 | 45.5037 | 20.9667 | 66.4704 | 63.0551 | 17.4578 | 22.4215 | 66 | 7.8819 | 7.8819 | 66 | 24.1688 | 11.0346 | 35.2034 | 66 | 87.3337 | 0 | 82.1152 | 66 | 58.2225 | 3.4024 | 63.5482 | 66 | 120 | 0 | 29.758 | 17.3067 | 110 | 244.263 | 66 | 0 | 11.5378 | 10.929
67 | 155.5237 | 21.8579 | 87.31 | 264.6916 | 0 | 264.6916 | 264.6916 | 67 | 0 | 14.5719 | 10.929 | 67 | 69.848 | 69.848 | 62.562 | 21.6968 | 23.1196 | 67 | 167.0606 | 21.8579 | 75.773 | 264.6916 | 0 | 264.6916 | 264.6916 | 67 | 0 | 14.5719 | 10.929 | 10.929 | 67 | 60.6184 | 9.2296 | 69.848 | 62.562 | 21.1649 | 24.6946 | 67 | 7.8203 | 7.8203 | 67 | 23.4131 | 10.9484 | 34.3615 | 67 | 74.9888 | 4.0263 | 84.2336 | 67 | 49.9925 | 0 | 54.4469 | 67 | 104.5067 | 0 | 0 | 11.0765 | 220 | 264.6916 | 67 | 0 | 7.3843 | 10.929
68 | 136.7269 | 16.3934 | 82.7999 | 235.9203 | 0 | 235.9203 | 235.9203 | 68 | 0 | 10.929 | 10.929 | 68 | 66.2399 | 66.2399 | 60.7754 | 24.0188 | 22.4215 | 68 | 154.4017 | 16.3934 | 65.1251 | 235.9203 | 0 | 235.9203 | 235.9203 | 68 | 0 | 10.929 | 10.929 | 10.929 | 68 | 52.1001 | 14.1398 | 66.2399 | 60.7754 | 22.2388 | 26.0426 | 68 | 7.5969 | 7.5969 | 68 | 22.0046 | 10.6357 | 32.6403 | 68 | 73.4205 | 0.88733 | 74.3079 | 68 | 48.947 | 0 | 47.2805 | 68 | 108 | 6.3219 | 0 | 21.4802 | 60 | 235.9203 | 68 | 0 | 14.3201 | 10.929
69 | 105.3905 | 18.4426 | 79.1244 | 202.9574 | 0 | 202.9574 | 202.9574 | 69 | 0 | 12.2951 | 10.929 | 69 | 63.2995 | 63.2995 | 57.152 | 17.6173 | 24.6946 | 69 | 129.0388 | 18.4426 | 55.476 | 202.9574 | 0 | 202.9574 | 202.9574 | 69 | 0 | 12.2951 | 10.929 | 10.929 | 69 | 44.3808 | 18.9187 | 63.2995 | 57.152 | 18.9831 | 25.5934 | 69 | 7.144 | 7.144 | 69 | 22.8302 | 10.0016 | 32.8318 | 69 | 69.6244 | 8.5871 | 78.2115 | 69 | 46.4163 | 0 | 42.7352 | 69 | 132 | 0 | 0 | 11.3067 | 0 | 202.9574 | 69 | 0 | 7.5378 | 10.929
70 | 132.8493 | 3.793 | 61.8247 | 198.467 | 0 | 198.467 | 198.467 | 70 | 0 | 2.5287 | 10.929 | 70 | 49.4597 | 49.4597 | 48.1954 | 10.5656 | 26.0426 | 70 | 136.3977 | 3.793 | 58.2762 | 198.467 | 0 | 198.467 | 198.467 | 70 | 0 | 2.5287 | 10.929 | 10.929 | 70 | 46.621 | 2.8388 | 49.4597 | 48.1954 | 9.19 | 24.8001 | 70 | 6.0244 | 6.0244 | 70 | 25.5447 | 8.4342 | 33.9789 | 70 | 63.9589 | 0 | 57.3126 | 70 | 42.6393 | 0 | 35.1743 | 70 | 114 | 0 | 59.7456 | 20.7971 | 0 | 198.467 | 70 | 0 | 13.8648 | 10.929
71 | 105.2466 | 27.6277 | 72.1013 | 204.9756 | 0 | 204.9756 | 204.9756 | 71 | 0 | 18.4185 | 10.929 | 71 | 57.681 | 57.681 | 48.4718 | 12.6253 | 25.8692 | 71 | 105.4316 | 27.6277 | 71.9162 | 204.9756 | 0 | 204.9756 | 204.9756 | 71 | 0 | 18.4185 | 10.929 | 10.929 | 71 | 57.533 | 0.14806 | 57.681 | 48.4718 | 13.9805 | 22.9273 | 71 | 6.059 | 6.059 | 71 | 23.1909 | 8.4826 | 31.6735 | 71 | 37.4031 | 16.8456 | 60.895 | 71 | 24.9354 | 0 | 34.8067 | 71 | 114 | 0 | 74.5821 | 16.3934 | 0 | 204.9756 | 71 | 0 | 10.929 | 10.929
72 | 131.5743 | 15.0273 | 79.8892 | 226.4908 | 0 | 226.4908 | 226.4908 | 72 | 0 | 10.0182 | 10.929 | 72 | 63.9114 | 63.9114 | 58.9023 | 11.2546 | 26.2387 | 72 | 134.5985 | 15.0273 | 76.865 | 226.4908 | 0 | 226.4908 | 226.4908 | 72 | 0 | 10.0182 | 10.929 | 10.929 | 72 | 61.492 | 2.4194 | 63.9114 | 58.9023 | 11.1626 | 25.0651 | 72 | 7.3628 | 7.3628 | 72 | 19.5779 | 10.3079 | 29.8858 | 72 | 67.1113 | 13.8256 | 80.937 | 72 | 44.7409 | 0 | 46.7238 | 72 | 114 | 6 | 84.5011 | 11.9898 | 10 | 226.4908 | 72 | 0 | 7.9932 | 10.929
73 | 137.9951 | 6.5253 | 76.9223 | 221.4426 | 0 | 221.4426 | 221.4426 | 73 | 0 | 4.3502 | 10.929 | 73 | 61.5378 | 61.5378 | 59.3627 | 29.1991 | 20.7575 | 73 | 144.0552 | 6.5253 | 70.8621 | 221.4426 | 0 | 221.4426 | 221.4426 | 73 | 0 | 4.3502 | 10.929 | 10.929 | 73 | 56.6897 | 4.8481 | 61.5378 | 59.3627 | 28.3758 | 23.6414 | 73 | 7.4203 | 7.4203 | 73 | 17.9007 | 10.3885 | 28.2892 | 73 | 57.6885 | 44.0816 | 96.7182 | 73 | 38.459 | 0 | 30.7425 | 73 | 114 | 30 | 46.6455 | 20.7971 | 10 | 221.4426 | 73 | 0 | 13.8648 | 10.929
74 | 70.201 | 27.6277 | 87.4944 | 185.3232 | 0 | 185.3232 | 185.3232 | 74 | 0 | 18.4185 | 10.929 | 74 | 69.9956 | 69.9956 | 60.7863 | 21.5115 | 29.0651 | 74 | 79.502 | 27.6277 | 78.1935 | 185.3232 | 0 | 185.3232 | 185.3232 | 74 | 0 | 18.4185 | 10.929 | 10.929 | 74 | 62.5548 | 7.4407 | 69.9956 | 60.7863 | 23.8127 | 29.9823 | 74 | 7.5983 | 7.5983 | 74 | 19.0311 | 10.6376 | 29.6687 | 74 | 47.1478 | 61.5847 | 106.7273 | 74 | 31.4319 | 0 | 31.3262 | 74 | 120 | 12 | 39.8252 | 22.6236 | 0 | 185.3232 | 74 | 0 | 15.0824 | 10.929
75 | 87.588 | 13.3559 | 78.6297 | 179.5736 | 0 | 179.5736 | 179.5736 | 75 | 0 | 8.9039 | 10.929 | 75 | 62.9038 | 62.9038 | 58.4518 | 19.1812 | 22.8227 | 75 | 91.656 | 13.3559 | 74.5616 | 179.5736 | 0 | 179.5736 | 179.5736 | 75 | 0 | 8.9039 | 10.929 | 10.929 | 75 | 59.6493 | 3.2545 | 62.9038 | 58.4518 | 16.2459 | 27.9276 | 75 | 7.3065 | 7.3065 | 75 | 16.4097 | 10.2291 | 26.6388 | 75 | 42.362 | 78.0343 | 123.3774 | 75 | 28.2414 | 0 | 32.7044 | 75 | 132 | 30 | 2.6884 | 5.7596 | 0 | 179.5736 | 75 | 0 | 3.8397 | 10.929
76 | 81.796 | 21.4802 | 80.4589 | 172.8637 | 0 | 172.8637 | 172.8637 | 76 | 0 | 14.3201 | 10.929 | 76 | 64.3671 | 64.3671 | 57.207 | 28.2582 | 29.2768 | 76 | 81.8158 | 21.4802 | 79.6129 | 172.8637 | 0 | 172.8637 | 172.8637 | 76 | 0 | 14.3201 | 10.929 | 10.929 | 76 | 63.6904 | 0.67675 | 64.3671 | 57.207 | 28.2582 | 24.3109 | 76 | 7.1509 | 7.1509 | 76 | 15.4734 | 10.0112 | 25.4846 | 76 | 63 | 57.1107 | 124.1867 | 76 | 42 | 0 | 37.3091 | 76 | 114 | 42 | 13.4063 | 25.9563 | 0 | 172.8637 | 76 | 0 | 17.3042 | 10.929
77 | 105.2372 | 3.11 | 64.4891 | 183.7076 | 0 | 183.7076 | 183.7076 | 77 | 0 | 2.0733 | 10.929 | 77 | 51.5913 | 51.5913 | 50.5546 | 6.9579 | 25.4518 | 77 | 108.6675 | 3.11 | 61.8848 | 183.7076 | 0 | 183.7076 | 183.7076 | 77 | 0 | 2.0733 | 10.929 | 10.929 | 77 | 49.5079 | 2.0834 | 51.5913 | 50.5546 | 6.9579 | 23.5344 | 77 | 6.3193 | 6.3193 | 77 | 18.6536 | 8.8471 | 27.5007 | 77 | 104.4749 | 14.3274 | 97.9441 | 77 | 69.6499 | 0 | 38.644 | 77 | 114 | 120 | 0 | 20.2616 | 0 | 183.7076 | 77 | 0 | 13.5077 | 10.929
78 | 115.0589 | 26.9447 | 74.3735 | 216.3772 | 0 | 216.3772 | 216.3772 | 78 | 0 | 17.9631 | 10.929 | 78 | 59.4988 | 59.4988 | 50.5173 | 28.7849 | 28.3109 | 78 | 118.2506 | 26.9447 | 71.1819 | 216.3772 | 0 | 216.3772 | 216.3772 | 78 | 0 | 17.9631 | 10.929 | 10.929 | 78 | 56.9455 | 2.5533 | 59.4988 | 50.5173 | 28.7849 | 22.7423 | 78 | 6.3147 | 6.3147 | 78 | 20.1966 | 8.8405 | 29.0371 | 78 | 65.9324 | 49.4342 | 133.1366 | 78 | 43.9549 | 0 | 68.3744 | 78 | 126 | 30 | 0 | 12.6831 | 0 | 216.3772 | 78 | 0 | 8.4554 | 10.929
79 | 143.8717 | 6.5253 | 76.3814 | 226.7783 | 0 | 226.7783 | 226.7783 | 79 | 0 | 4.3502 | 10.929 | 79 | 61.1051 | 61.1051 | 58.93 | 14.4919 | 22.1684 | 79 | 144.6912 | 6.5253 | 75.5618 | 226.7783 | 0 | 226.7783 | 226.7783 | 79 | 0 | 4.3502 | 10.929 | 10.929 | 79 | 60.4495 | 0.65562 | 61.1051 | 58.93 | 14.4919 | 26.3832 | 79 | 7.3663 | 7.3663 | 79 | 17.6777 | 10.3128 | 27.9905 | 79 | 133.4921 | 6.3207 | 131.8512 | 79 | 88.9947 | 0 | 72.925 | 79 | 120 | 42 | 0 | 24 | 10 | 226.7783 | 79 | 0 | 16 | 10.929
80 | 81.1229 | 18.8306 | 83.4551 | 183.4086 | 0 | 183.4086 | 183.4086 | 80 | 0 | 12.5537 | 10.929 | 80 | 66.7641 | 66.7641 | 60.4872 | 18.3834 | 30.0781 | 80 | 83.9048 | 18.8306 | 80.6732 | 183.4086 | 0 | 183.4086 | 183.4086 | 80 | 0 | 12.5537 | 10.929 | 10.929 | 80 | 64.5386 | 2.2255 | 66.7641 | 60.4872 | 17.3505 | 23.8075 | 80 | 7.5609 | 7.5609 | 80 | 19.5868 | 10.5853 | 30.1721 | 80 | 86.3864 | 34.7778 | 128.8164 | 80 | 57.591 | 0 | 67.2827 | 80 | 114 | 18 | 33.3581 | 3.4699 | 0 | 183.4086 | 80 | 0 | 2.3133 | 10.929
81 | 92.4846 | 15.3873 | 79.228 | 187.0999 | 0 | 187.0999 | 187.0999 | 81 | 0 | 10.2582 | 10.929 | 81 | 63.3824 | 63.3824 | 58.2533 | 11.8787 | 20.9556 | 81 | 94.0988 | 15.3873 | 77.6138 | 187.0999 | 0 | 187.0999 | 187.0999 | 81 | 0 | 10.2582 | 10.929 | 10.929 | 81 | 62.091 | 1.2914 | 63.3824 | 58.2533 | 13.0804 | 26.4833 | 81 | 7.2817 | 7.2817 | 81 | 21.4359 | 10.1943 | 31.6302 | 81 | 100.9766 | 17.0956 | 118.6764 | 81 | 67.3177 | 0 | 65.9586 | 81 | 126 | 0 | 44.7064 | 16.3934 | 0 | 187.0999 | 81 | 0 | 10.929 | 10.929
82 | 77.2869 | 26.1967 | 83.2483 | 186.7319 | 0 | 186.7319 | 186.7319 | 82 | 0 | 17.4645 | 10.929 | 82 | 66.5986 | 66.5986 | 57.8664 | 15.2896 | 28.8366 | 82 | 87.5605 | 26.1967 | 72.9746 | 186.7319 | 0 | 186.7319 | 186.7319 | 82 | 0 | 17.4645 | 10.929 | 10.929 | 82 | 58.3797 | 8.2189 | 66.5986 | 57.8664 | 14.5941 | 20.5348 | 82 | 7.2333 | 7.2333 | 82 | 17.6686 | 10.1266 | 27.7952 | 82 | 112.9433 | 0 | 115.7367 | 82 | 75.2955 | 0 | 64.9155 | 82 | 126 | 0 | 48.7421 | 11.9898 | 0 | 186.7319 | 82 | 0 | 7.9932 | 10.929
83 | 106.8866 | 13.3559 | 74.4412 | 194.6837 | 0 | 194.6837 | 194.6837 | 83 | 0 | 8.9039 | 10.929 | 83 | 59.553 | 59.553 | 55.101 | 10.3395 | 20.9445 | 83 | 127.4885 | 13.3559 | 53.8393 | 194.6837 | 0 | 194.6837 | 194.6837 | 83 | 0 | 8.9039 | 10.929 | 10.929 | 83 | 43.0715 | 16.4815 | 59.553 | 55.101 | 11.2548 | 21.4447 | 83 | 6.8876 | 6.8876 | 83 | 18.4674 | 9.6427 | 28.1101 | 83 | 61.7421 | 0 | 50.267 | 83 | 41.1614 | 9.3448 | 61.1377 | 83 | 84 | 12 | 69.6898 | 28.9939 | 0 | 194.6837 | 83 | 0 | 19.3292 | 10.929
84 | 129.3852 | 8.1967 | 62.6042 | 200.1861 | 0 | 200.1861 | 200.1861 | 84 | 0 | 5.4645 | 10.929 | 84 | 50.0834 | 50.0834 | 47.3511 | 22.1267 | 20.0423 | 84 | 152.6166 | 8.1967 | 39.3727 | 200.1861 | 0 | 200.1861 | 200.1861 | 84 | 0 | 5.4645 | 10.929 | 10.929 | 84 | 31.4982 | 18.5852 | 50.0834 | 47.3511 | 21.4619 | 28.3829 | 84 | 5.9189 | 5.9189 | 84 | 19.0562 | 8.2864 | 27.3427 | 84 | 49.6291 | 0 | 40.246 | 84 | 33.0861 | 42.1929 | 69.8553 | 84 | 126 | 0 | 57.1096 | 17.0765 | 0 | 200.1861 | 84 | 0 | 11.3843 | 10.929
85 | 104.7833 | 16.3934 | 63.8762 | 185.053 | 0 | 185.053 | 185.053 | 85 | 0 | 10.929 | 10.929 | 85 | 51.101 | 51.101 | 45.6365 | 13.5492 | 24.5658 | 85 | 114.3164 | 16.3934 | 54.3431 | 185.053 | 0 | 185.053 | 185.053 | 85 | 0 | 10.929 | 10.929 | 10.929 | 85 | 43.4745 | 7.6265 | 51.101 | 45.6365 | 12.9918 | 33.6295 | 85 | 5.7046 | 5.7046 | 85 | 18.731 | 7.9864 | 26.7174 | 85 | 42.1511 | 0 | 52.6711 | 85 | 28.1007 | 25.315 | 78.2756 | 85 | 132 | 0 | 45.5393 | 7.5137 | 0 | 185.053 | 85 | 0 | 5.0091 | 10.929
86 | 78.4303 | 26.9447 | 80.713 | 186.0879 | 0 | 186.0879 | 186.0879 | 86 | 0 | 17.9631 | 10.929 | 86 | 64.5704 | 64.5704 | 55.5888 | 19.77 | 31.458 | 86 | 106.3517 | 26.9447 | 52.7916 | 186.0879 | 0 | 186.0879 | 186.0879 | 86 | 0 | 17.9631 | 10.929 | 10.929 | 86 | 42.2333 | 22.3371 | 64.5704 | 55.5888 | 18.8802 | 30.7973 | 86 | 6.9486 | 6.9486 | 86 | 17.2648 | 9.728 | 26.9928 | 86 | 45.2487 | 0 | 55.5869 | 86 | 30.1658 | 19.1076 | 53.3444 | 86 | 126 | 0 | 47.4151 | 12.6728 | 0 | 186.0879 | 86 | 0 | 8.4485 | 10.929
87 | 86.4985 | 12.5902 | 75.937 | 175.0256 | 0 | 175.0256 | 175.0256 | 87 | 0 | 8.3934 | 10.929 | 87 | 60.7496 | 60.7496 | 56.5528 | 17.3863 | 32.3513 | 87 | 97.9297 | 12.5902 | 64.5057 | 175.0256 | 0 | 175.0256 | 175.0256 | 87 | 0 | 8.3934 | 10.929 | 10.929 | 87 | 51.6046 | 9.145 | 60.7496 | 56.5528 | 19.575 | 25.6988 | 87 | 7.0691 | 7.0691 | 87 | 17.151 | 9.8967 | 27.0477 | 87 | 57.8839 | 0 | 57.8839 | 87 | 38.5893 | 0.044195 | 26.6729 | 87 | 114 | 0 | 40.2284 | 20.7971 | 0 | 175.0256 | 87 | 0 | 13.8648 | 10.929
88 | 80.6985 | 12 | 77.8654 | 170.5638 | 0 | 170.5638 | 170.5638 | 88 | 0 | 8 | 10.929 | 88 | 62.2923 | 62.2923 | 58.2923 | 27.5474 | 34.8257 | 88 | 95.1329 | 12 | 63.4309 | 170.5638 | 0 | 170.5638 | 170.5638 | 88 | 0 | 8 | 10.929 | 10.929 | 88 | 50.7448 | 11.5475 | 62.2923 | 58.2923 | 24.9956 | 25.2365 | 88 | 7.2865 | 7.2865 | 88 | 19.1794 | 10.2012 | 29.3806 | 88 | 66.203 | 0 | 66.203 | 88 | 44.1353 | 0 | 52.0743 | 88 | 132 | 0 | 27.2571 | 11.3067 | 0 | 170.5638 | 88 | 0 | 7.5378 | 10.929
89 | 87.8195 | 17.7596 | 80.7676 | 186.3467 | 0 | 186.3467 | 186.3467 | 89 | 0 | 11.8397 | 10.929 | 89 | 64.6141 | 64.6141 | 58.6943 | 26.3763 | 20.4164 | 89 | 100.1327 | 17.7596 | 68.4544 | 186.3467 | 0 | 186.3467 | 186.3467 | 89 | 0 | 11.8397 | 10.929 | 10.929 | 89 | 54.7635 | 9.8506 | 64.6141 | 58.6943 | 27.6445 | 33.5475 | 89 | 7.3368 | 7.3368 | 89 | 19.9288 | 10.2715 | 30.2003 | 89 | 47.006 | 0 | 47.006 | 89 | 31.3373 | 26.5945 | 58.6408 | 89 | 114 | 0 | 51.5495 | 20.7971 | 0 | 186.3467 | 89 | 0 | 13.8648 | 10.929
90 | 78.7323 | 24.5902 | 77.4159 | 166.1596 | 0 | 166.1596 | 166.1596 | 90 | 0 | 16.3934 | 10.929 | 90 | 61.9327 | 61.9327 | 53.736 | 28.3093 | 26.8127 | 90 | 92.9038 | 24.5902 | 56.9647 | 166.1596 | 0 | 166.1596 | 166.1596 | 90 | 0 | 16.3934 | 10.929 | 10.929 | 90 | 45.5718 | 16.3609 | 61.9327 | 53.736 | 26.9593 | 36.9178 | 90 | 6.717 | 6.717 | 90 | 15.1813 | 9.4038 | 24.5851 | 90 | 47.6389 | 0 | 32.2958 | 90 | 31.7593 | 36.88 | 63.5427 | 90 | 108 | 0 | 38.0874 | 24.5902 | 0 | 166.1596 | 90 | 0 | 16.3934 | 10.929
91 | 32.1572 | 9.8337 | 59.953 | 116.5227 | 0 | 116.5227 | 116.5227 | 91 | 0 | 6.5558 | 14.9561 | 91 | 47.9624 | 47.9624 | 44.6845 | 18.4755 | 36.3927 | 91 | 50.2429 | 9.8337 | 48.1471 | 116.5227 | 0 | 116.5227 | 116.5227 | 91 | 0 | 6.5558 | 14.9561 | 14.9561 | 91 | 38.5176 | 9.4447 | 47.9624 | 44.6845 | 21.3239 | 15.1734 | 91 | 5.5856 | 5.5856 | 91 | 14.75 | 7.8198 | 22.5698 | 91 | 78.5228 | 0 | 83.3648 | 91 | 52.3486 | 0 | 41.0598 | 91 | 114 | 0 | 0 | 27.2155 | 0 | 116.5227 | 91 | 0 | 18.1437 | 14.9561
92 | 32.919 | 28.9939 | 67.7364 | 129.6492 | 0 | 129.6492 | 129.6492 | 92 | 0 | 19.3292 | 10.929 | 92 | 54.1891 | 54.1891 | 44.5245 | 20.9352 | 32.4658 | 92 | 60.8731 | 28.9939 | 39.7823 | 129.6492 | 0 | 129.6492 | 129.6492 | 92 | 0 | 19.3292 | 10.929 | 10.929 | 92 | 31.8258 | 22.3633 | 54.1891 | 44.5245 | 18.2556 | 27.929 | 92 | 5.5656 | 5.5656 | 92 | 14.3777 | 7.7918 | 22.1695 | 92 | 76.2362 | 55.3611 | 142.0984 | 92 | 50.8241 | 0 | 47.5237 | 92 | 108 | 0 | 0 | 4.0984 | 0 | 129.6492 | 92 | 0 | 2.7322 | 10.929
93 | 51.1281 | 17.0765 | 75.4681 | 143.6726 | 0 | 143.6726 | 143.6726 | 93 | 0 | 11.3843 | 10.929 | 93 | 60.3744 | 60.3744 | 54.6823 | 17.6071 | 27.929 | 93 | 58.9587 | 17.0765 | 67.6375 | 143.6726 | 0 | 143.6726 | 143.6726 | 93 | 0 | 11.3843 | 10.929 | 10.929 | 93 | 54.11 | 6.2645 | 60.3744 | 54.6823 | 17.6071 | 24.5303 | 93 | 6.8353 | 6.8353 | 93 | 14.6519 | 9.5694 | 24.2213 | 93 | 86.1617 | 0 | 86.1617 | 93 | 57.4411 | 0 | 57.5653 | 93 | 102 | 6 | 20.7022 | 11.8422 | 0 | 143.6726 | 93 | 0 | 7.8948 | 10.929
94 | 85.6382 | 3.11 | 70.6729 | 159.421 | 0 | 159.421 | 159.421 | 94 | 0 | 2.0733 | 10.929 | 94 | 56.5383 | 56.5383 | 55.5016 | 21.5693 | 24.5303 | 94 | 88.8894 | 3.11 | 67.4216 | 159.421 | 0 | 159.421 | 159.421 | 94 | 0 | 2.0733 | 10.929 | 10.929 | 94 | 53.9373 | 2.601 | 56.5383 | 55.5016 | 21.5693 | 12.3088 | 94 | 6.9377 | 6.9377 | 94 | 16.5487 | 9.7128 | 26.2615 | 94 | 92.5597 | 0 | 71.7015 | 94 | 61.7064 | 23.6063 | 72.2279 | 94 | 48 | 72 | 24.8514 | 33.2398 | 0 | 159.421 | 94 | 0 | 22.1598 | 10.929
95 | 55.6551 | 21.4802 | 82.8031 | 159.9384 | 0 | 159.9384 | 159.9384 | 95 | 0 | 14.3201 | 10.929 | 95 | 66.2425 | 66.2425 | 59.0825 | 5.9978 | 25.1003 | 95 | 61.0887 | 21.4802 | 77.3695 | 159.9384 | 0 | 159.9384 | 159.9384 | 95 | 0 | 14.3201 | 10.929 | 10.929 | 95 | 61.8956 | 4.3469 | 66.2425 | 59.0825 | 5.9978 | 27.7405 | 95 | 7.3853 | 7.3853 | 95 | 16.8972 | 10.3394 | 27.2366 | 95 | 40.0487 | 0 | 60.9069 | 95 | 26.6991 | 7.7094 | 67.0611 | 95 | 144 | 42 | 0 | 0 | 0 | 159.9384 | 95 | 0 | 0 | 10.929
96 | 65.2175 | 15.7104 | 80.77 | 161.6978 | 0 | 161.6978 | 161.6978 | 96 | 0 | 10.4736 | 10.929 | 96 | 64.616 | 64.616 | 59.3792 | 12.5691 | 22.2034 | 96 | 87.2457 | 15.7104 | 58.7418 | 161.6978 | 0 | 161.6978 | 161.6978 | 96 | 0 | 10.4736 | 10.929 | 10.929 | 96 | 46.9934 | 17.6225 | 64.616 | 59.3792 | 12.1111 | 18.7456 | 96 | 7.4224 | 7.4224 | 96 | 17.5641 | 10.3914 | 27.9555 | 96 | 131.275 | 0 | 110.4168 | 96 | 87.5166 | 15.5414 | 68.85 | 96 | 102 | 24 | 0 | 26.4918 | 0 | 161.6978 | 96 | 0 | 17.6612 | 10.929
97 | 65.5266 | 18.4426 | 77.7746 | 161.7438 | 0 | 161.7438 | 161.7438 | 97 | 0 | 12.2951 | 10.929 | 97 | 62.2197 | 62.2197 | 56.0721 | 13.4522 | 22.6287 | 97 | 71.6871 | 18.4426 | 71.6141 | 161.7438 | 0 | 161.7438 | 161.7438 | 97 | 0 | 12.2951 | 10.929 | 10.929 | 97 | 57.2913 | 4.9284 | 62.2197 | 56.0721 | 14.3464 | 26.1097 | 97 | 7.009 | 7.009 | 97 | 15.2168 | 9.8126 | 25.0294 | 97 | 96.1827 | 0 | 96.1827 | 97 | 64.1218 | 0 | 70.1525 | 97 | 126 | 0 | 0 | 12.1373 | 0 | 161.7438 | 97 | 0 | 8.0915 | 10.929
98 | 51.77 | 21.8579 | 68.1531 | 141.781 | 0 | 141.781 | 141.781 | 98 | 0 | 14.5719 | 10.929 | 98 | 54.5225 | 54.5225 | 47.2365 | 18.284 | 22.8119 | 98 | 58.9494 | 21.8579 | 60.9737 | 141.781 | 0 | 141.781 | 141.781 | 98 | 0 | 14.5719 | 10.929 | 10.929 | 98 | 48.779 | 5.7435 | 54.5225 | 47.2365 | 18.8399 | 20.9449 | 98 | 5.9046 | 5.9046 | 98 | 17.5542 | 8.2664 | 25.8206 | 98 | 58.6649 | 0 | 75.3314 | 98 | 39.1099 | 0 | 55.7007 | 98 | 102 | 6 | 12.7958 | 10.929 | 0 | 141.781 | 98 | 0 | 7.286 | 10.929
99 | 80.9541 | 9.5628 | 60.2796 | 150.7965 | 0 | 150.7965 | 150.7965 | 99 | 0 | 6.3752 | 10.929 | 99 | 48.2236 | 48.2236 | 45.036 | 14.007 | 26.0361 | 99 | 94.4812 | 9.5628 | 46.7524 | 150.7965 | 0 | 150.7965 | 150.7965 | 99 | 0 | 6.3752 | 10.929 | 10.929 | 99 | 37.4019 | 10.8217 | 48.2236 | 45.036 | 14.6666 | 27.3251 | 99 | 5.6295 | 5.6295 | 99 | 18.8222 | 7.8813 | 26.7035 | 99 | 37.5896 | 0 | 41.7813 | 99 | 25.0597 | 24.6278 | 64.5804 | 99 | 102 | 36 | 0 | 15.0273 | 0 | 150.7965 | 99 | 0 | 10.0182 | 10.929
100 | 54.3594 | 12.3806 | 76.5417 | 143.2817 | 0 | 143.2817 | 143.2817 | 100 | 0 | 8.2537 | 11.6449 | 100 | 61.2333 | 61.2333 | 57.1065 | 30.0071 | 26.3549 | 100 | 67.63 | 12.3806 | 63.2711 | 143.2817 | 0 | 143.2817 | 143.2817 | 100 | 0 | 8.2537 | 11.6449 | 11.6449 | 100 | 50.6169 | 10.6165 | 61.2333 | 57.1065 | 29.1787 | 23.057 | 100 | 7.1383 | 7.1383 | 100 | 17.7802 | 9.9936 | 27.7738 | 100 | 53.159 | 0 | 53.159 | 100 | 35.4394 | 36.4887 | 60.8999 | 100 | 108 | 36 | 0 | 21.4802 | 0 | 143.2817 | 100 | 0 | 14.3201 | 11.6449
101 | 39.2447 | 20.7971 | 80.2442 | 140.2861 | 0 | 140.2861 | 140.2861 | 101 | 0 | 13.8648 | 10.929 | 101 | 64.1954 | 64.1954 | 57.263 | 18.3528 | 26.2133 | 101 | 44.6604 | 20.7971 | 74.8285 | 140.2861 | 0 | 140.2861 | 140.2861 | 101 | 0 | 13.8648 | 10.929 | 10.929 | 101 | 59.8628 | 4.3326 | 64.1954 | 57.263 | 19.5596 | 31.3646 | 101 | 7.1579 | 7.1579 | 101 | 18.8633 | 10.021 | 28.8843 | 101 | 49.2197 | 0 | 49.2197 | 101 | 32.8131 | 19.2897 | 61.4998 | 101 | 126 | 0 | 0 | 12.3806 | 0 | 140.2861 | 101 | 0 | 8.2537 | 10.929
102 | 75.091 | 18.8204 | 78.6418 | 172.5532 | 0 | 172.5532 | 172.5532 | 102 | 0 | 12.5469 | 10.929 | 102 | 62.9135 | 62.9135 | 56.64 | 18.9495 | 29.3978 | 102 | 76.8381 | 18.8204 | 76.8948 | 172.5532 | 0 | 172.5532 | 172.5532 | 102 | 0 | 12.5469 | 10.929 | 10.929 | 102 | 61.5158 | 1.3976 | 62.9135 | 56.64 | 16.5 | 23.258 | 102 | 7.08 | 7.08 | 102 | 19.0626 | 9.912 | 28.9746 | 102 | 67.2096 | 0 | 46.3514 | 102 | 44.8064 | 45.0235 | 63.3482 | 102 | 102 | 30 | 0 | 26.2616 | 0 | 172.5532 | 102 | 0 | 17.5077 | 10.929
103 | 78.5773 | 22.1633 | 69.2469 | 164.2219 | 0 | 164.2219 | 164.2219 | 103 | 0 | 14.7755 | 10.929 | 103 | 55.3975 | 55.3975 | 48.0098 | 26.3456 | 19.7932 | 103 | 83.0031 | 22.1633 | 64.7667 | 164.2219 | 0 | 164.2219 | 164.2219 | 103 | 0 | 14.7755 | 10.929 | 10.929 | 103 | 51.8133 | 3.5842 | 55.3975 | 48.0098 | 28.0945 | 18.4648 | 103 | 6.0012 | 6.0012 | 103 | 21.5687 | 8.4017 | 29.9704 | 103 | 65.4571 | 0 | 78.1758 | 103 | 43.6381 | 29.7708 | 73.7574 | 103 | 114 | 0 | 20.1689 | 11.4262 | 0 | 164.2219 | 103 | 0 | 7.6175 | 10.929
104 | 84.1122 | 11.9898 | 61.9692 | 163.8367 | 0 | 163.8367 | 163.8367 | 104 | 0 | 7.9932 | 10.929 | 104 | 49.5754 | 49.5754 | 45.5788 | 12.9219 | 16.6778 | 104 | 86.8682 | 11.9898 | 59.2677 | 163.8367 | 0 | 163.8367 | 163.8367 | 104 | 0 | 7.9932 | 10.929 | 10.929 | 104 | 47.4142 | 2.1612 | 49.5754 | 45.5788 | 11.6384 | 15.1017 | 104 | 5.6973 | 5.6973 | 104 | 20.963 | 7.9763 | 28.9393 | 104 | 71.3405 | 0 | 58.6218 | 104 | 47.5603 | 51.8554 | 85.4636 | 104 | 120 | 0 | 19.8367 | 24 | 0 | 163.8367 | 104 | 0 | 16 | 10.929
105 | 88.679 | 18.5902 | 65.5936 | 169.5576 | 0 | 169.5576 | 169.5576 | 105 | 0 | 12.3934 | 10.929 | 105 | 52.4749 | 52.4749 | 46.2782 | 22.8171 | 20.1067 | 105 | 98.8971 | 18.5902 | 53.8694 | 169.5576 | 0 | 169.5576 | 169.5576 | 105 | 0 | 12.3934 | 10.929 | 10.929 | 105 | 43.0956 | 9.3794 | 52.4749 | 46.2782 | 23.5484 | 14.2616 | 105 | 5.7848 | 5.7848 | 105 | 20.6111 | 8.0987 | 28.7098 | 105 | 51.1754 | 0 | 66.7267 | 105 | 34.117 | 14.4536 | 82.1722 | 105 | 138 | 0 | 25.5576 | 6 | 0 | 169.5576 | 105 | 0 | 4 | 10.929
106 | 138.2764 | 6 | 57.8022 | 205.3838 | 0 | 205.3838 | 205.3838 | 106 | 0 | 4 | 10.929 | 106 | 46.2418 | 46.2418 | 44.2418 | 11.0656 | 17.3965 | 106 | 159.9022 | 6 | 37.6825 | 205.3838 | 0 | 205.3838 | 205.3838 | 106 | 0 | 4 | 10.929 | 10.929 | 106 | 30.146 | 16.0958 | 46.2418 | 44.2418 | 9.7309 | 8.6541 | 106 | 5.5302 | 5.5302 | 106 | 18.5903 | 7.7423 | 26.3326 | 106 | 70.1035 | 0 | 65.4056 | 106 | 46.7357 | 49.9032 | 75.8489 | 106 | 114 | 0 | 58.3987 | 24.6831 | 20 | 205.3838 | 106 | 0 | 16.4554 | 10.929
107 | 140.9078 | 18.5075 | 65.0286 | 224.4439 | 0 | 224.4439 | 224.4439 | 107 | 0 | 12.3383 | 10.929 | 107 | 52.0229 | 52.0229 | 45.8537 | 13.5611 | 24.4173 | 107 | 148.52 | 18.5075 | 57.4165 | 224.4439 | 0 | 224.4439 | 224.4439 | 107 | 0 | 12.3383 | 10.929 | 10.929 | 107 | 45.9332 | 6.0897 | 52.0229 | 45.8537 | 13.508 | 11.1446 | 107 | 5.7317 | 5.7317 | 107 | 14.855 | 8.0244 | 22.8794 | 107 | 68.6723 | 0 | 61.3353 | 107 | 45.7815 | 25.5736 | 83.091 | 107 | 120 | 0 | 20.3628 | 22.3832 | 50 | 224.4439 | 107 | 0 | 14.9221 | 10.929
108 | 99.7968 | 26.1967 | 79.9653 | 205.9588 | 0 | 205.9588 | 205.9588 | 108 | 0 | 17.4645 | 10.929 | 108 | 63.9722 | 63.9722 | 55.24 | 7.8182 | 13.1396 | 108 | 107.6012 | 26.1967 | 72.1609 | 205.9588 | 0 | 205.9588 | 205.9588 | 108 | 0 | 17.4645 | 10.929 | 10.929 | 108 | 57.7287 | 6.2435 | 63.9722 | 55.24 | 8.3111 | 25.5999 | 108 | 6.905 | 6.905 | 108 | 11.1031 | 9.667 | 20.7701 | 108 | 22.0234 | 0 | 39.3653 | 108 | 14.6823 | 48.8713 | 78.0972 | 108 | 144 | 0 | 61.9588 | 0 | 0 | 205.9588 | 108 | 0 | 0 | 10.929
109 | 133.4304 | 16.3934 | 77.5927 | 227.4165 | 0 | 227.4165 | 227.4165 | 109 | 0 | 10.929 | 10.929 | 109 | 62.0742 | 62.0742 | 56.6097 | 16.476 | 20.8921 | 109 | 141.6016 | 16.3934 | 69.4215 | 227.4165 | 0 | 227.4165 | 227.4165 | 109 | 0 | 10.929 | 10.929 | 10.929 | 109 | 55.5372 | 6.5369 | 62.0742 | 56.6097 | 16.1845 | 17.7596 | 109 | 7.0762 | 7.0762 | 109 | 14.0637 | 9.9067 | 23.9704 | 109 | 21.9178 | 0 | 21.9178 | 109 | 14.6119 | 66.335 | 83.572 | 109 | 108 | 0 | 53.0231 | 16.3934 | 50 | 227.4165 | 109 | 0 | 10.929 | 10.929
110 | 127.4202 | 12.6728 | 77.0833 | 217.1764 | 0 | 217.1764 | 217.1764 | 110 | 0 | 8.4485 | 10.929 | 110 | 61.6667 | 61.6667 | 57.4424 | 13.1427 | 19.7778 | 110 | 137.6143 | 12.6728 | 66.8892 | 217.1764 | 0 | 217.1764 | 217.1764 | 110 | 0 | 8.4485 | 10.929 | 10.929 | 110 | 53.5114 | 8.1553 | 61.6667 | 57.4424 | 15.0144 | 17.5009 | 110 | 7.1803 | 7.1803 | 110 | 16.0646 | 10.0524 | 26.117 | 110 | 31.3137 | 0 | 23.8934 | 110 | 20.8758 | 73.2177 | 91.5383 | 110 | 78 | 63.9075 | 55.2006 | 27.0273 | 0 | 217.1764 | 110 | 0 | 18.0182 | 10.929
111 | 91.6768 | 17.0765 | 78.6902 | 181.7527 | 0 | 181.7527 | 181.7527 | 111 | 0 | 11.3843 | 10.929 | 111 | 62.9522 | 62.9522 | 57.26 | 14.3852 | 14.8049 | 111 | 99.5268 | 17.0765 | 69.6664 | 181.7527 | 0 | 181.7527 | 181.7527 | 111 | 0 | 11.3843 | 10.929 | 10.929 | 111 | 55.7331 | 7.2191 | 62.9522 | 57.26 | 14.1908 | 16.7748 | 111 | 7.1575 | 7.1575 | 111 | 15.7621 | 10.0205 | 25.7826 | 111 | 39.2652 | 0 | 33.9501 | 111 | 26.1768 | 43.6722 | 52.1554 | 111 | 90 | 82.7365 | 0 | 12.5902 | 0 | 181.7527 | 111 | 0 | 8.3934 | 10.929
112 | 62.2419 | 12.6831 | 70.6061 | 151.222 | 0 | 151.222 | 151.222 | 112 | 0 | 8.4554 | 10.929 | 112 | 56.4849 | 56.4849 | 52.2572 | 14.124 | 16.2332 | 112 | 77.3089 | 12.6831 | 56.713 | 151.222 | 0 | 151.222 | 151.222 | 112 | 0 | 8.4554 | 10.929 | 10.929 | 112 | 45.3704 | 11.1145 | 56.4849 | 52.2572 | 13.9655 | 15.3775 | 112 | 6.5322 | 6.5322 | 112 | 14.5004 | 9.145 | 23.6454 | 112 | 29.0774 | 0 | 24.6075 | 112 | 19.3849 | 33.3965 | 36.5416 | 112 | 114 | 102 | 0 | 22.8463 | 0 | 151.222 | 112 | 0 | 15.2309 | 10.929
113 | 100.3836 | 11.224 | 64.4931 | 176.1008 | 0 | 176.1008 | 176.1008 | 113 | 0 | 7.4827 | 10.929 | 113 | 51.5945 | 51.5945 | 47.8532 | 12.0884 | 15.7846 | 113 | 101.0689 | 11.224 | 63.8079 | 176.1008 | 0 | 176.1008 | 176.1008 | 113 | 0 | 7.4827 | 10.929 | 10.929 | 113 | 51.0463 | 0.54822 | 51.5945 | 47.8532 | 10.452 | 18.8119 | 113 | 5.9816 | 5.9816 | 113 | 15.6706 | 8.3743 | 24.0449 | 113 | 28.8444 | 0 | 29.1182 | 113 | 19.2296 | 27.3684 | 53.393 | 113 | 102 | 18 | 0 | 17.0765 | 0 | 176.1008 | 113 | 0 | 11.3843 | 10.929
114 | 81.4111 | 16.3934 | 79.7163 | 177.5209 | 0 | 177.5209 | 177.5209 | 114 | 0 | 10.929 | 10.929 | 114 | 63.7731 | 63.7731 | 58.3086 | 18.9051 | 18.2149 | 114 | 89.6226 | 16.3934 | 71.5049 | 177.5209 | 0 | 177.5209 | 177.5209 | 114 | 0 | 10.929 | 10.929 | 10.929 | 114 | 57.2039 | 6.5692 | 63.7731 | 58.3086 | 21.2165 | 16.3934 | 114 | 7.2886 | 7.2886 | 114 | 11.967 | 10.204 | 22.171 | 114 | 26.5332 | 0 | 28.9992 | 114 | 17.6888 | 50.541 | 73.9735 | 114 | 120 | 0 | 0 | 7.5137 | 0 | 177.5209 | 114 | 0 | 5.0091 | 10.929
115 | 85.7132 | 22.1633 | 80.7413 | 188.6178 | 0 | 188.6178 | 188.6178 | 115 | 0 | 14.7755 | 10.929 | 115 | 64.593 | 64.593 | 57.2053 | 15.6025 | 15.3775 | 115 | 87.6285 | 22.1633 | 78.826 | 188.6178 | 0 | 188.6178 | 188.6178 | 115 | 0 | 14.7755 | 10.929 | 10.929 | 115 | 63.0608 | 1.5323 | 64.593 | 57.2053 | 15.4439 | 12.0915 | 115 | 7.1507 | 7.1507 | 115 | 13.3828 | 10.0109 | 23.3937 | 115 | 11.8721 | 0 | 22.132 | 115 | 7.9148 | 43.1573 | 75.022 | 115 | 126 | 0 | 37.7815 | 15.7104 | 0 | 188.6178 | 115 | 0 | 10.4736 | 10.929
116 | 102.5221 | 15.7104 | 77.8024 | 196.0349 | 0 | 196.0349 | 196.0349 | 116 | 0 | 10.4736 | 10.929 | 116 | 62.2419 | 62.2419 | 57.0051 | 25.0927 | 14.3133 | 116 | 111.8878 | 15.7104 | 68.4367 | 196.0349 | 0 | 196.0349 | 196.0349 | 116 | 0 | 10.4736 | 10.929 | 10.929 | 116 | 54.7494 | 7.4926 | 62.2419 | 57.0051 | 23.3898 | 16.7937 | 116 | 7.1256 | 7.1256 | 116 | 12.7026 | 9.9759 | 22.6785 | 116 | 81.9442 | 0 | 86.1498 | 116 | 54.6294 | 34.6521 | 82.3236 | 116 | 120 | 0 | 59.6414 | 16.3934 | 0 | 196.0349 | 116 | 0 | 10.929 | 10.929
117 | 82.3871 | 21.6175 | 80.2492 | 184.2538 | 0 | 184.2538 | 184.2538 | 117 | 0 | 14.4117 | 10.929 | 117 | 64.1993 | 64.1993 | 56.9935 | 7.8515 | 17.7045 | 117 | 84.5812 | 21.6175 | 78.0551 | 184.2538 | 0 | 184.2538 | 184.2538 | 117 | 0 | 14.4117 | 10.929 | 10.929 | 117 | 62.4441 | 1.7552 | 64.1993 | 56.9935 | 8.7106 | 17.5009 | 117 | 7.1242 | 7.1242 | 117 | 11.959 | 9.9739 | 21.9329 | 117 | 123.9901 | 0 | 120.414 | 117 | 82.6601 | 0 | 84.307 | 117 | 126 | 0 | 45.581 | 12.6728 | 0 | 184.2538 | 117 | 0 | 8.4485 | 10.929
118 | 94.3223 | 19.3661 | 76.5413 | 186.5364 | 0 | 186.5364 | 186.5364 | 118 | 0 | 12.9107 | 10.929 | 118 | 61.2331 | 61.2331 | 54.7777 | 18.6652 | 15.7345 | 118 | 98.5445 | 19.3661 | 72.1947 | 186.5364 | 0 | 186.5364 | 186.5364 | 118 | 0 | 12.9107 | 10.929 | 10.929 | 118 | 57.7557 | 3.4774 | 61.2331 | 54.7777 | 19.4169 | 19.7345 | 118 | 6.8472 | 6.8472 | 118 | 13.4762 | 9.5861 | 23.0623 | 118 | 81.4161 | 0 | 83.2577 | 118 | 54.2774 | 41.1992 | 96.1376 | 118 | 114 | 0 | 56.143 | 16.3934 | 0 | 186.5364 | 118 | 0 | 10.929 | 10.929
119 | 89.53 | 15.7104 | 64.6889 | 173.6227 | 0 | 173.6227 | 173.6227 | 119 | 0 | 10.4736 | 10.929 | 119 | 51.7511 | 51.7511 | 46.5143 | 11.1883 | 14.1598 | 119 | 103.9854 | 15.7104 | 50.3579 | 173.6227 | 0 | 173.6227 | 173.6227 | 119 | 0 | 10.4736 | 10.929 | 10.929 | 119 | 40.2863 | 11.4648 | 51.7511 | 46.5143 | 9.3065 | 6.4736 | 119 | 5.8143 | 5.8143 | 119 | 15.9241 | 8.14 | 24.0641 | 119 | 36.2027 | 0 | 37.9371 | 119 | 24.1351 | 86.3062 | 115.0914 | 119 | 120 | 6 | 30.7988 | 17.0765 | 0 | 173.6227 | 119 | 0 | 11.3843 | 10.929
120 | 119.5512 | 3.793 | 57.6495 | 180.9937 | 0 | 180.9937 | 180.9937 | 120 | 0 | 2.5287 | 10.929 | 120 | 46.1196 | 46.1196 | 44.8553 | 23.6916 | 18.4736 | 120 | 136.6736 | 3.793 | 40.5271 | 180.9937 | 0 | 180.9937 | 180.9937 | 120 | 0 | 2.5287 | 10.929 | 10.929 | 120 | 32.4217 | 13.6979 | 46.1196 | 44.8553 | 26.724 | 20.3383 | 120 | 5.6069 | 5.6069 | 120 | 14.6423 | 7.8497 | 22.4919 | 120 | 51.2538 | 0 | 35.6639 | 120 | 34.1692 | 103.5717 | 117.2748 | 120 | 72 | 114 | 1.5554 | 28.3108 | 0 | 180.9937 | 120 | 0 | 18.8739 | 10.929
121 | 81.0945 | 20.7971 | 73.9332 | 175.8248 | 0 | 175.8248 | 175.8248 | 121 | 0 | 13.8648 | 10.929 | 121 | 59.1465 | 59.1465 | 52.2142 | 27.1025 | 17.8579 | 121 | 86.2247 | 20.7971 | 68.803 | 175.8248 | 0 | 175.8248 | 175.8248 | 121 | 0 | 13.8648 | 10.929 | 10.929 | 121 | 55.0424 | 4.1042 | 59.1465 | 52.2142 | 25.2359 | 18.3684 | 121 | 6.5268 | 6.5268 | 121 | 11.8643 | 9.1375 | 21.0018 | 121 | 13.8152 | 0 | 24.6075 | 121 | 9.2102 | 75.8166 | 105.4929 | 121 | 126 | 30 | 0 | 8.1967 | 0 | 175.8248 | 121 | 0 | 5.4645 | 10.929
122 | 61.9722 | 18.4426 | 76.6717 | 157.0866 | 0 | 157.0866 | 157.0866 | 122 | 0 | 12.2951 | 10.929 | 122 | 61.3374 | 61.3374 | 55.1899 | 20.1835 | 19.1189 | 122 | 78.375 | 18.4426 | 60.269 | 157.0866 | 0 | 157.0866 | 157.0866 | 122 | 0 | 12.2951 | 10.929 | 10.929 | 122 | 48.2152 | 13.1222 | 61.3374 | 55.1899 | 21.5387 | 18.51 | 122 | 6.8987 | 6.8987 | 122 | 11.8755 | 9.6582 | 21.5337 | 122 | 17.8225 | 0 | 22.62 | 122 | 11.8816 | 91.0927 | 102.9744 | 122 | 132 | 0 | 0 | 11.3067 | 0 | 157.0866 | 122 | 0 | 7.5378 | 10.929
123 | 56.749 | 13.6612 | 74.1824 | 144.5926 | 0 | 144.5926 | 144.5926 | 123 | 0 | 9.1075 | 12.6293 | 123 | 59.3459 | 59.3459 | 54.7922 | 23.6609 | 13.7045 | 123 | 72.6334 | 13.6612 | 58.298 | 144.5926 | 0 | 144.5926 | 144.5926 | 123 | 0 | 9.1075 | 12.6293 | 12.6293 | 123 | 46.6384 | 12.7075 | 59.3459 | 54.7922 | 22.0909 | 14.3133 | 123 | 6.849 | 6.849 | 123 | 13.4003 | 9.5886 | 22.9889 | 123 | 26.3377 | 0 | 21.9178 | 123 | 17.5584 | 83.7081 | 101.2665 | 123 | 114 | 0 | 18.0437 | 19.627 | 0 | 144.5926 | 123 | 0 | 13.0847 | 12.6293
124 | 29.7661 | 45.6508 | 88.2101 | 122.8876 | 0 | 122.8876 | 122.8876 | 124 | 0 | 30.4338 | 22.3583 | 124 | 70.568 | 70.568 | 55.3511 | 9.6801 | 22.7687 | 124 | 33.9987 | 45.6508 | 72.5443 | 122.8876 | 0 | 122.8876 | 122.8876 | 124 | 0 | 30.4338 | 22.3583 | 22.3583 | 124 | 58.0354 | 12.5326 | 70.568 | 55.3511 | 9.6289 | 23.526 | 124 | 6.9189 | 6.9189 | 124 | 14.1846 | 9.6864 | 23.8711 | 124 | 27.5436 | 0 | 21.9178 | 124 | 18.3624 | 103.4404 | 103.7742 | 124 | 90 | 0 | 2.3654 | 39.4802 | 0 | 122.8876 | 124 | 0 | 26.3201 | 22.3583
125 | 0 | 31.9458 | 79.6412 | 126.8549 | 0 | 126.8549 | 126.8549 | 125 | 0 | 21.2972 | 21.2972 | 125 | 63.7129 | 63.7129 | 53.0643 | 10.2148 | 13.4576 | 125 | 13.4119 | 31.9458 | 68.2673 | 126.8549 | 0 | 126.8549 | 126.8549 | 125 | 0 | 21.2972 | 21.2972 | 21.2972 | 125 | 54.6138 | 9.0991 | 63.7129 | 53.0643 | 8.9735 | 16.0364 | 125 | 6.633 | 6.633 | 125 | 12.916 | 9.2863 | 22.2023 | 125 | 12.7854 | 0 | 21.9178 | 125 | 8.5236 | 95.6104 | 116.7073 | 125 | 102 | 0 | 0 | 25.3199 | 0 | 126.8549 | 125 | 0 | 16.8799 | 21.2972
126 | 31.3771 | 11.9815 | 59.974 | 128.804 | 0 | 128.804 | 128.804 | 126 | 0 | 7.9877 | 16.3879 | 126 | 47.9792 | 47.9792 | 43.9854 | 9.7415 | 16.1348 | 126 | 53.9188 | 11.9815 | 46.8275 | 128.804 | 0 | 128.804 | 128.804 | 126 | 0 | 7.9877 | 16.3879 | 16.3879 | 126 | 37.462 | 10.5173 | 47.9792 | 43.9854 | 10.1851 | 18.867 | 126 | 5.4982 | 5.4982 | 126 | 11.555 | 7.6974 | 19.2525 | 126 | 27.2509 | 0 | 21.9178 | 126 | 18.1673 | 98.6947 | 122.3172 | 126 | 96 | 0 | 0 | 25.265 | 0 | 128.804 | 126 | 0 | 16.8433 | 16.3879
127 | 32.5077 | 34.5419 | 67.755 | 115.5625 | 0 | 115.5625 | 115.5625 | 127 | 0 | 23.0279 | 23.4833 | 127 | 54.204 | 54.204 | 42.69 | 1.5629 | 16.24 | 127 | 36.1505 | 34.5419 | 52.872 | 115.5625 | 0 | 115.5625 | 115.5625 | 127 | 0 | 23.0279 | 23.4833 | 23.4833 | 127 | 42.2976 | 11.9063 | 54.204 | 42.69 | 0.98367 | 13.4026 | 127 | 5.3362 | 5.3362 | 127 | 10.5741 | 7.4707 | 18.0449 | 127 | 23.0959 | 0 | 21.9178 | 127 | 15.3973 | 118.2906 | 117.7774 | 127 | 84 | 0 | 0 | 34.5419 | 0 | 115.5625 | 127 | 0 | 23.0279 | 23.4833
128 | 9.5588 | 24.3637 | 78.0645 | 125.4405 | 0 | 125.4405 | 125.4405 | 128 | 0 | 16.2424 | 15.7871 | 128 | 62.4516 | 62.4516 | 54.3304 | 11.4529 | 13.6544 | 128 | 24.7592 | 24.3637 | 68.3157 | 125.4405 | 0 | 125.4405 | 125.4405 | 128 | 0 | 16.2424 | 15.7871 | 15.7871 | 128 | 54.6525 | 7.799 | 62.4516 | 54.3304 | 14.2208 | 16.7436 | 128 | 6.7913 | 6.7913 | 128 | 9.6209 | 9.5078 | 19.1287 | 128 | 18.9132 | 0 | 21.9178 | 128 | 12.6088 | 88.9447 | 117.464 | 128 | 96 | 0 | 0 | 23.6806 | 0 | 125.4405 | 128 | 0 | 15.7871 | 15.7871
129 | 41.3707 | 28.3108 | 81.4055 | 149.5948 | 0 | 149.5948 | 149.5948 | 129 | 0 | 18.8739 | 10.929 | 129 | 65.1244 | 65.1244 | 55.6874 | 9.0201 | 23.2673 | 129 | 48.0157 | 28.3108 | 80.5491 | 149.5948 | 0 | 149.5948 | 149.5948 | 129 | 0 | 18.8739 | 10.929 | 10.929 | 129 | 64.4393 | 0.68508 | 65.1244 | 55.6874 | 7.7161 | 19.883 | 129 | 6.9609 | 6.9609 | 129 | 10.6012 | 9.7453 | 20.3465 | 129 | 18.4112 | 0 | 21.9178 | 129 | 12.2741 | 94.7861 | 107.0602 | 129 | 120 | 0 | 0 | 17.0765 | 0 | 149.5948 | 129 | 0 | 11.3843 | 10.929
130 | 60.0933 | 15.0273 | 77.0081 | 159.4095 | 0 | 159.4095 | 159.4095 | 130 | 0 | 10.0182 | 10.929 | 130 | 61.6065 | 61.6065 | 56.5974 | 9.9101 | 16.6885 | 130 | 60.9186 | 15.0273 | 76.1828 | 159.4095 | 0 | 159.4095 | 159.4095 | 130 | 0 | 10.0182 | 10.929 | 10.929 | 130 | 60.9462 | 0.66025 | 61.6065 | 56.5974 | 9.3629 | 20.5282 | 130 | 7.0747 | 7.0747 | 130 | 13.1856 | 9.9045 | 23.0901 | 130 | 21.0046 | 0 | 21.9178 | 130 | 14.003 | 90.7602 | 104.7633 | 130 | 114 | 0 | 25.6356 | 16.3934 | 0 | 159.4095 | 130 | 0 | 10.929 | 10.929
131 | 103.388 | 8.1967 | 72.0654 | 183.6501 | 0 | 183.6501 | 183.6501 | 131 | 0 | 5.4645 | 10.929 | 131 | 57.6523 | 57.6523 | 54.9201 | 9.8156 | 13.3593 | 131 | 103.8927 | 8.1967 | 71.5606 | 183.6501 | 0 | 183.6501 | 183.6501 | 131 | 0 | 5.4645 | 10.929 | 10.929 | 131 | 57.2485 | 0.40379 | 57.6523 | 54.9201 | 9.0091 | 9.3593 | 131 | 6.865 | 6.865 | 131 | 13.1619 | 9.611 | 22.773 | 131 | 27.2509 | 0 | 21.9178 | 131 | 18.1673 | 96.4614 | 110.0867 | 131 | 120 | 0 | 43.536 | 20.1141 | 0 | 183.6501 | 131 | 0 | 13.4094 | 10.929
132 | 73.9128 | 25.2732 | 67.9165 | 167.1025 | 0 | 167.1025 | 167.1025 | 132 | 0 | 16.8488 | 10.929 | 132 | 54.3332 | 54.3332 | 45.9088 | 6.892 | 17.0888 | 132 | 76.6742 | 25.2732 | 65.1551 | 167.1025 | 0 | 167.1025 | 167.1025 | 132 | 0 | 16.8488 | 10.929 | 10.929 | 132 | 52.124 | 2.2092 | 54.3332 | 45.9088 | 7.4456 | 21.0888 | 132 | 5.7386 | 5.7386 | 132 | 9.9698 | 8.034 | 18.0038 | 132 | 17.498 | 0 | 21.9178 | 132 | 11.6653 | 111.3761 | 121.6363 | 132 | 126 | 0 | 29.1128 | 11.9898 | 0 | 167.1025 | 132 | 0 | 7.9932 | 10.929
133 | 74.6891 | 8.1197 | 58.1903 | 140.999 | 0 | 140.999 | 140.999 | 133 | 0 | 5.4131 | 13.358 | 133 | 46.5522 | 46.5522 | 43.8457 | 0.69054 | 14.4736 | 133 | 86.7085 | 8.1197 | 46.1709 | 140.999 | 0 | 140.999 | 140.999 | 133 | 0 | 5.4131 | 13.358 | 13.358 | 133 | 36.9367 | 9.6155 | 46.5522 | 43.8457 | 0 | 14.4736 | 133 | 5.4807 | 5.4807 | 133 | 8.1308 | 7.673 | 15.8038 | 133 | 37.2966 | 0 | 21.9178 | 133 | 24.8644 | 138.0617 | 154.1338 | 133 | 90 | 0 | 38.9192 | 28.8463 | 0 | 140.999 | 133 | 0 | 19.2309 | 13.358
134 | 34.4913 | 65.756 | 80.1209 | 112.4175 | 0 | 112.4175 | 112.4175 | 134 | 0 | 43.8373 | 36.7536 | 134 | 64.0967 | 64.0967 | 42.1781 | 0 | 22.7687 | 134 | 35.3314 | 65.756 | 78.6067 | 112.4175 | 0 | 112.4175 | 112.4175 | 134 | 0 | 43.8373 | 36.7536 | 36.7536 | 134 | 62.8854 | 1.2113 | 64.0967 | 42.1781 | 0 | 22.3133 | 134 | 5.2723 | 5.2723 | 134 | 6.659 | 7.3812 | 14.0402 | 134 | 10.0457 | 0 | 21.9178 | 134 | 6.6971 | 124.823 | 146.2594 | 134 | 54 | 0 | 6.3549 | 46.3211 | 0 | 112.4175 | 134 | 0 | 30.8807 | 36.7536
135 | 0 | 79.9262 | 100.181 | 86.0322 | 59.5473 | 86.0322 | 145.5796 | 135 | 1.8859 | 53.2841 | 61.7984 | 135 | 80.1448 | 80.1448 | 53.1255 | 0 | 14.8238 | 135 | 0 | 79.9262 | 98.0393 | 86.0322 | 56.845 | 86.0322 | 142.8773 | 135 | 1.8859 | 53.2841 | 61.7984 | 61.7984 | 135 | 78.4315 | 1.7133 | 80.1448 | 53.1255 | 0 | 14.8238 | 135 | 6.6407 | 6.6407 | 135 | 4.4344 | 9.297 | 13.7313 | 135 | 17.498 | 0 | 21.9178 | 135 | 11.6653 | 117.6616 | 129.3269 | 135 | 17.6885 | 0 | 5.4494 | 89.8687 | 0 | 86.0322 | 135 | 1.8859 | 59.9125 | 61.7984
136 | 0 | 47.3222 | 89.1602 | 102.2176 | 40.3046 | 102.2176 | 142.5221 | 136 | 0 | 31.5481 | 24.0586 | 136 | 71.3282 | 71.3282 | 55.5541 | 0 | 13.4026 | 136 | 0 | 47.3222 | 87.0728 | 102.2176 | 39.681 | 102.2176 | 141.8985 | 136 | 0 | 31.5481 | 24.0586 | 24.0586 | 136 | 69.6583 | 1.6699 | 71.3282 | 55.5541 | 0 | 12.4918 | 136 | 6.9443 | 6.9443 | 136 | 8.1927 | 9.722 | 17.9147 | 136 | 22.8311 | 0 | 21.9178 | 136 | 15.2207 | 106.8155 | 122.0362 | 136 | 36 | 0 | 0 | 36.0879 | 0 | 102.2176 | 136 | 0 | 24.0586 | 24.0586
137 | 0 | 7.4604 | 72.5301 | 110.6178 | 0 | 110.6178 | 110.6178 | 137 | 0 | 4.9736 | 12.4631 | 137 | 58.0241 | 58.0241 | 55.5373 | 0 | 19.526 | 137 | 0 | 7.4604 | 47.7953 | 110.6178 | 0 | 110.6178 | 110.6178 | 137 | 0 | 4.9736 | 12.4631 | 12.4631 | 137 | 38.2363 | 19.7878 | 58.0241 | 55.5373 | 0 | 19.9813 | 137 | 6.9422 | 6.9422 | 137 | 11.9261 | 9.719 | 21.6451 | 137 | 27.2509 | 0 | 21.9178 | 137 | 18.1673 | 91.3682 | 109.5355 | 137 | 92.9001 | 6 | 0 | 22.1633 | 0 | 110.6178 | 137 | 0 | 14.7755 | 12.4631
138 | 0 | 85.38 | 107.1372 | 75.4471 | 78.5903 | 75.4471 | 154.0374 | 138 | 10.9509 | 56.92 | 63.8311 | 138 | 85.7098 | 85.7098 | 55.0596 | 0 | 15.4759 | 138 | 0 | 85.38 | 84.4254 | 75.4471 | 29.5666 | 75.4471 | 105.0137 | 138 | 10.9509 | 56.92 | 63.8311 | 63.8311 | 138 | 67.5404 | 18.1694 | 85.7098 | 55.0596 | 0 | 15.0205 | 138 | 6.8825 | 6.8825 | 138 | 14.2232 | 9.6354 | 23.8587 | 138 | 15.6715 | 0 | 21.9178 | 138 | 10.4477 | 91.489 | 101.9367 | 138 | 12 | 0 | 0 | 45.1317 | 0 | 75.4471 | 138 | 31.4309 | 30.0878 | 63.8311
139 | 0 | 144 | 136.6535 | 45.9398 | 234.7136 | 45.9398 | 280.6535 | 139 | 46.8289 | 96 | 145.6262 | 139 | 109.3228 | 109.3228 | 51.957 | 0 | 10.0182 | 139 | 0 | 144 | 114.0887 | 45.9398 | 212.1489 | 45.9398 | 258.0887 | 139 | 46.8289 | 96 | 145.6262 | 145.6262 | 139 | 91.271 | 18.0518 | 109.3228 | 51.957 | 0 | 10.0182 | 139 | 6.4946 | 6.4946 | 139 | 14.0537 | 9.0925 | 23.1461 | 139 | 23.7443 | 0 | 21.9178 | 139 | 15.8295 | 91.3571 | 102.6987 | 139 | 0 | 0 | 0 | 90 | 0 | 45.9398 | 139 | 85.6262 | 60 | 145.6262
140 | 0 | 123.6447 | 120.8708 | 52.7014 | 191.814 | 52.7014 | 244.5155 | 140 | 58.9164 | 82.4298 | 145.5111 | 140 | 96.6966 | 96.6966 | 43.6984 | 0 | 0 | 140 | 0 | 123.6447 | 103.2756 | 52.7014 | 174.2189 | 52.7014 | 226.9203 | 140 | 58.9164 | 82.4298 | 145.5111 | 145.5111 | 140 | 82.6205 | 14.0761 | 96.6966 | 43.6984 | 0 | 0 | 140 | 5.4623 | 5.4623 | 140 | 13.5536 | 7.6472 | 21.2008 | 140 | 36.3833 | 0 | 21.9178 | 140 | 24.2555 | 100.8744 | 113.3565 | 140 | 0 | 0 | 0 | 94.2898 | 0 | 52.7014 | 140 | 82.6512 | 62.8599 | 145.5111
141 | 0 | 97.4 | 94.0395 | 75.5046 | 117.6022 | 75.5046 | 193.1068 | 141 | 0 | 64.9334 | 58.3977 | 141 | 75.2316 | 75.2316 | 42.765 | 0 | 0 | 141 | 0 | 97.3039 | 74.0172 | 75.5046 | 97.7598 | 75.5046 | 173.2644 | 141 | 0 | 64.8693 | 58.3977 | 58.3977 | 141 | 59.2138 | 15.9858 | 75.1996 | 42.765 | 0 | 0 | 141 | 5.3456 | 5.3456 | 141 | 12.8637 | 7.4839 | 20.3476 | 141 | 10.9589 | 0 | 21.9178 | 141 | 7.3059 | 88.757 | 112.3242 | 141 | 0 | 0 | 0 | 35.305 | 0 | 75.5046 | 141 | 34.8611 | 23.5366 | 58.3977
142 | 0 | 97.5881 | 109.9582 | 70.4736 | 135.4055 | 70.4736 | 205.8791 | 142 | 10.7356 | 65.0587 | 79.8628 | 142 | 87.9666 | 87.9666 | 53.2901 | 0 | 0 | 142 | 0 | 97.6842 | 65.9186 | 70.4736 | 92.3527 | 70.4736 | 162.8263 | 142 | 10.7356 | 65.1228 | 79.8628 | 79.8628 | 142 | 52.7349 | 35.2637 | 87.9986 | 53.2901 | 0 | 0 | 142 | 6.6613 | 6.6613 | 142 | 7.6966 | 9.3258 | 17.0223 | 142 | 16.5847 | 0 | 21.9178 | 142 | 11.0565 | 94.631 | 105.6874 | 142 | 0 | 0 | 0 | 53.3493 | 0 | 70.4736 | 142 | 44.2967 | 35.5662 | 79.8628
143 | 0 | 106.0218 | 113.551 | 80.5298 | 139.0429 | 80.5298 | 219.5728 | 143 | 1.4223 | 70.6812 | 64.2019 | 143 | 90.8408 | 90.8408 | 55.2157 | 0 | 0 | 143 | 0 | 106.0218 | 72.0913 | 80.5298 | 96.4164 | 80.5298 | 176.9463 | 143 | 1.4223 | 70.6812 | 64.2019 | 64.2019 | 143 | 57.673 | 33.1678 | 90.8408 | 55.2157 | 0 | 0 | 143 | 6.902 | 6.902 | 143 | 8.1684 | 9.6628 | 17.8312 | 143 | 27.2509 | 0 | 21.9178 | 143 | 18.1673 | 96.2107 | 114.378 | 143 | 0 | 0 | 0 | 68.3456 | 0 | 80.5298 | 143 | 18.6382 | 45.5637 | 64.2019
144 | 0 | 100.7044 | 112.9342 | 67.7023 | 145.9362 | 67.7023 | 213.6385 | 144 | 13.1424 | 67.1362 | 89.758 | 144 | 90.3474 | 90.3474 | 54.1508 | 0 | 0 | 144 | 0 | 100.7044 | 80.9497 | 67.7023 | 113.9517 | 67.7023 | 181.654 | 144 | 13.1424 | 67.1362 | 89.758 | 89.758 | 144 | 64.7597 | 25.5876 | 90.3474 | 54.1508 | 0 | 0 | 144 | 6.7688 | 6.7688 | 144 | 7.1908 | 9.4764 | 16.6672 | 144 | 31.9635 | 0 | 21.9178 | 144 | 21.309 | 107.8818 | 114.5887 | 144 | 0 | 0 | 0 | 108.9235 | 0 | 67.7023 | 144 | 17.1424 | 72.6157 | 89.758
145 | 0 | 88.7755 | 93.2687 | 78.7934 | 103.2509 | 78.7934 | 182.0443 | 145 | 0 | 59.1837 | 53.7186 | 145 | 74.615 | 74.615 | 45.0231 | 0 | 0 | 145 | 0 | 88.7755 | 83.371 | 78.7934 | 93.3531 | 78.7934 | 172.1466 | 145 | 0 | 59.1837 | 53.7186 | 53.7186 | 145 | 66.6968 | 7.9182 | 74.615 | 45.0231 | 0 | 0 | 145 | 5.6279 | 5.6279 | 145 | 10.0338 | 7.879 | 17.9128 | 145 | 11.8721 | 0 | 21.9178 | 145 | 7.9148 | 110.0301 | 122.1389 | 145 | 0 | 0 | 0 | 43.2053 | 0 | 78.7934 | 145 | 25.6773 | 28.8035 | 53.7186
146 | 0 | 101.7874 | 103.2599 | 66.0809 | 138.9665 | 66.0809 | 205.0474 | 146 | 12.3686 | 67.8583 | 86.7792 | 146 | 82.6079 | 82.6079 | 46.2051 | 0 | 0 | 146 | 0 | 101.7874 | 100.7347 | 66.0809 | 136.4412 | 66.0809 | 202.5222 | 146 | 12.3686 | 67.8583 | 86.7792 | 86.7792 | 146 | 80.5878 | 2.0202 | 82.6079 | 46.2051 | 0 | 0 | 146 | 5.7756 | 5.7756 | 146 | 7.9203 | 8.0859 | 16.0062 | 146 | 17.498 | 0 | 21.9178 | 146 | 11.6653 | 102.6815 | 124.7547 | 146 | 0 | 0 | 0 | 80.6963 | 0 | 66.0809 | 146 | 32.2195 | 53.7975 | 86.7792
147 | 0 | 138.1856 | 122.7676 | 52.2817 | 208.6716 | 52.2817 | 260.9533 | 147 | 45.5666 | 92.1238 | 132.6244 | 147 | 98.2141 | 98.2141 | 43.0389 | 0 | 0 | 147 | 0 | 138.1856 | 94.3658 | 52.2817 | 180.2698 | 52.2817 | 232.5515 | 147 | 45.5666 | 92.1238 | 132.6244 | 132.6244 | 147 | 75.4927 | 22.7214 | 98.2141 | 43.0389 | 0 | 0 | 147 | 5.3799 | 5.3799 | 147 | 4.5356 | 7.5318 | 12.0674 | 147 | 37.2966 | 0 | 21.9178 | 147 | 24.8644 | 103.1753 | 109.6328 | 147 | 0 | 0 | 0 | 115.906 | 0 | 52.2817 | 147 | 55.3537 | 77.2707 | 132.6244
148 | 0 | 123.0218 | 130.0651 | 48.2914 | 204.7955 | 48.2914 | 253.087 | 148 | 95.1366 | 82.0146 | 170.6965 | 148 | 104.0521 | 104.0521 | 44.0175 | 0 | 0 | 148 | 0 | 123.0218 | 115.9986 | 48.2914 | 190.7291 | 48.2914 | 239.0205 | 148 | 95.1366 | 82.0146 | 170.6965 | 170.6965 | 148 | 92.7989 | 11.2532 | 104.0521 | 44.0175 | 0 | 0 | 148 | 5.5022 | 5.5022 | 148 | 4.0783 | 7.7031 | 11.4286 | 148 | 10.9589 | 0 | 21.9178 | 148 | 7.3059 | 83.4659 | 109.1788 | 148 | 0 | 0 | 0 | 24.1266 | 0 | 48.2914 | 148 | 154.6122 | 16.0844 | 170.6965
149 | 0 | 144 | 156.8728 | 30.7837 | 270.0891 | 30.7837 | 300.8728 | 149 | 112.9494 | 96 | 213.972 | 149 | 125.4982 | 125.4982 | 54.9083 | 0 | 0 | 149 | 0 | 144 | 150.8928 | 30.7837 | 264.1091 | 30.7837 | 294.8928 | 149 | 112.9494 | 96 | 213.972 | 213.972 | 149 | 120.7142 | 4.784 | 125.4982 | 54.9083 | 0 | 0 | 149 | 6.8635 | 6.8635 | 149 | 2.5123 | 9.609 | 11.1468 | 149 | 16.5847 | 0 | 21.9178 | 149 | 11.0565 | 97.7548 | 108.8113 | 149 | 0 | 0 | 0 | 6 | 0 | 30.7837 | 149 | 209.972 | 4 | 213.972
150 | 0 | 144 | 130.263 | 55.5763 | 218.6868 | 55.5763 | 274.263 | 150 | 0 | 96 | 101.5197 | 150 | 104.2104 | 104.2104 | 56.2104 | 0 | 0 | 150 | 0 | 144 | 122.1202 | 55.5763 | 210.544 | 55.5763 | 266.1202 | 150 | 0 | 96 | 101.5197 | 101.5197 | 150 | 97.6962 | 6.5142 | 104.2104 | 56.2104 | 0 | 0 | 150 | 7.0263 | 7.0263 | 150 | 1.6225 | 9.8368 | 11.7002 | 150 | 22.8311 | 0 | 21.9178 | 150 | 15.2207 | 104.8645 | 120.0852 | 150 | 0 | 0 | 0 | 97.0545 | 0 | 55.5763 | 150 | 36.8168 | 64.703 | 101.5197
151 | 0 | 134.5179 | 136.1427 | 50.2808 | 220.3797 | 50.2808 | 270.6606 | 151 | 36.9015 | 89.6786 | 127.6256 | 151 | 108.9141 | 108.9141 | 56.6945 | 0 | 0 | 151 | 0 | 134.5179 | 120.1168 | 50.2808 | 204.3539 | 50.2808 | 254.6347 | 151 | 36.9015 | 89.6786 | 127.6256 | 127.6256 | 151 | 96.0935 | 12.8207 | 108.9141 | 56.6945 | 0 | 0 | 151 | 7.0868 | 7.0868 | 151 | 1.4898 | 9.9215 | 11.0558 | 151 | 26.3377 | 0 | 21.9178 | 151 | 17.5584 | 117.3456 | 127.3921 | 151 | 0 | 0 | 0 | 34.9925 | 0 | 50.2808 | 151 | 104.2973 | 23.3283 | 127.6256
152 | 0 | 115.7557 | 118.1829 | 71.9628 | 161.9758 | 71.9628 | 233.9386 | 152 | 0 | 77.1705 | 65.5826 | 152 | 94.5463 | 94.5463 | 55.9611 | 0 | 0 | 152 | 0 | 115.7557 | 103.5866 | 71.9628 | 147.3795 | 71.9628 | 219.3423 | 152 | 0 | 77.1705 | 65.5826 | 65.5826 | 152 | 82.8692 | 11.6771 | 94.5463 | 55.9611 | 0 | 0 | 152 | 6.9951 | 6.9951 | 152 | 1.9316 | 9.7932 | 12.9398 | 152 | 21.1509 | 0 | 21.9178 | 152 | 14.1006 | 116.3965 | 132.7751 | 152 | 0 | 0 | 0 | 32.7765 | 0 | 71.9628 | 152 | 43.7316 | 21.851 | 65.5826
153 | 0 | 85.7963 | 103.0781 | 75.6311 | 113.2433 | 75.6311 | 188.8744 | 153 | 1.7547 | 57.1975 | 64.4576 | 153 | 82.4625 | 82.4625 | 53.5128 | 0 | 0 | 153 | 0 | 85.7963 | 100.0032 | 75.6311 | 110.1684 | 75.6311 | 185.7995 | 153 | 1.7547 | 57.1975 | 64.4576 | 64.4576 | 153 | 80.0026 | 2.4599 | 82.4625 | 53.5128 | 0 | 0 | 153 | 6.6891 | 6.6891 | 153 | 2.7768 | 9.3647 | 12.3683 | 153 | 20.0913 | 0 | 21.9178 | 153 | 13.3942 | 131.7083 | 143.9354 | 153 | 0 | 0 | 0 | 50.7971 | 0 | 75.6311 | 153 | 30.5928 | 33.8648 | 64.4576
154 | 0 | 107.0277 | 108.1296 | 62.0331 | 153.1241 | 62.0331 | 215.1573 | 154 | 23.7468 | 71.3518 | 99.2952 | 154 | 86.5037 | 86.5037 | 46.0784 | 0 | 0 | 154 | 0 | 107.0277 | 78.9316 | 62.0331 | 123.9261 | 62.0331 | 185.9592 | 154 | 23.7468 | 71.3518 | 99.2952 | 99.2952 | 154 | 63.1452 | 23.3584 | 86.5037 | 46.0784 | 0 | 0 | 154 | 5.7598 | 5.7598 | 154 | 6.1296 | 8.0637 | 14.1933 | 154 | 35.4701 | 0 | 21.9178 | 154 | 23.6467 | 130.4808 | 144.3462 | 154 | 0 | 0 | 0 | 77.9689 | 0 | 62.0331 | 154 | 47.316 | 51.9792 | 99.2952
155 | 0 | 113.6103 | 103.4079 | 68.49 | 148.5282 | 68.49 | 217.0182 | 155 | 8.5944 | 75.7402 | 80.0163 | 155 | 82.7263 | 82.7263 | 43.1373 | 0 | 0 | 155 | 0 | 113.6103 | 86.7751 | 68.49 | 131.8953 | 68.49 | 200.3853 | 155 | 8.5944 | 75.7402 | 80.0163 | 80.0163 | 155 | 69.42 | 13.3063 | 82.7263 | 43.1373 | 0 | 0 | 155 | 5.3922 | 5.3922 | 155 | 6.6657 | 7.549 | 14.2147 | 155 | 7.4523 | 0 | 21.9178 | 155 | 4.9682 | 131.721 | 147.3295 | 155 | 0 | 0 | 0 | 60.3037 | 0 | 68.49 | 155 | 39.8138 | 40.2025 | 80.0163
156 | 0 | 85.4805 | 91.8884 | 77.1663 | 101.4822 | 77.1663 | 178.6484 | 156 | 0 | 56.987 | 53.514 | 156 | 73.5107 | 73.5107 | 45.0172 | 0 | 0 | 156 | 0 | 85.4805 | 60.1269 | 77.1663 | 70.2921 | 77.1663 | 147.4584 | 156 | 0 | 56.987 | 53.514 | 53.514 | 156 | 48.1015 | 25.4092 | 73.5107 | 45.0172 | 0 | 0 | 156 | 5.6272 | 5.6272 | 156 | 5.2341 | 7.878 | 13.1121 | 156 | 20.0913 | 0 | 21.9178 | 156 | 13.3942 | 123.2535 | 142.1898 | 156 | 0 | 6 | 0 | 82.0846 | 0 | 77.1663 | 156 | 1.3768 | 54.723 | 53.514
157 | 0 | 102 | 114.2249 | 62.7806 | 152.1648 | 62.7806 | 214.9454 | 157 | 13.8261 | 68 | 89.4001 | 157 | 91.3799 | 91.3799 | 54.6147 | 0 | 0 | 157 | 0 | 102 | 99.1168 | 62.7806 | 136.4853 | 62.7806 | 199.2658 | 157 | 13.8261 | 68 | 89.4001 | 89.4001 | 157 | 79.2934 | 12.0865 | 91.3799 | 54.6147 | 0 | 0 | 157 | 6.8268 | 6.8268 | 157 | 5.6477 | 9.5576 | 15.2053 | 157 | 37.2966 | 0 | 21.9178 | 157 | 24.8644 | 120.8705 | 140.59 | 157 | 6 | 6 | 0 | 109.4823 | 0 | 62.7806 | 157 | 13.8261 | 72.9882 | 89.4001
158 | 0 | 135.0215 | 135.3538 | 50.3268 | 220.0485 | 50.3268 | 270.3753 | 158 | 36.4479 | 90.0143 | 127.9453 | 158 | 108.2831 | 108.2831 | 55.9863 | 0 | 0 | 158 | 0 | 135.0215 | 134.3087 | 50.3268 | 219.0034 | 50.3268 | 269.3302 | 158 | 36.4479 | 90.0143 | 127.9453 | 127.9453 | 158 | 107.447 | 0.83608 | 108.2831 | 55.9863 | 0 | 0 | 158 | 6.9983 | 6.9983 | 158 | 5.9479 | 9.7976 | 15.7455 | 158 | 12.7854 | 0 | 21.9178 | 158 | 8.5236 | 135.4013 | 146.0432 | 158 | 0 | 0 | 0 | 40.9946 | 0 | 50.3268 | 158 | 100.6155 | 27.3298 | 127.9453
159 | 0 | 83.8621 | 103.9526 | 82.2662 | 105.5485 | 82.2662 | 187.8148 | 159 | 0 | 55.9081 | 46.5082 | 159 | 83.1621 | 83.1621 | 55.2081 | 0 | 0 | 159 | 0 | 83.8621 | 102.0076 | 82.2662 | 103.6035 | 82.2662 | 185.8697 | 159 | 0 | 55.9081 | 46.5082 | 46.5082 | 159 | 81.6061 | 1.556 | 83.1621 | 55.2081 | 0 | 0 | 159 | 6.901 | 6.901 | 159 | 5.3136 | 9.6614 | 14.975 | 159 | 17.498 | 0 | 21.9178 | 159 | 11.6653 | 143.5915 | 145.4433 | 159 | 0 | 0 | 0 | 34.3861 | 0 | 82.2662 | 159 | 24.0394 | 22.9241 | 46.5082
160 | 0 | 93.7282 | 106.9485 | 73.1012 | 127.5755 | 73.1012 | 200.6768 | 160 | 8.4955 | 62.4855 | 72.678 | 160 | 85.5588 | 85.5588 | 52.617 | 0 | 0 | 160 | 0 | 93.7282 | 94.8608 | 73.1012 | 115.4878 | 73.1012 | 188.5891 | 160 | 8.4955 | 62.4855 | 72.678 | 72.678 | 160 | 75.8887 | 9.6702 | 85.5588 | 52.617 | 0 | 0 | 160 | 6.5771 | 6.5771 | 160 | 4.4143 | 9.208 | 13.6222 | 160 | 22.8311 | 0 | 21.9178 | 160 | 15.2207 | 135.7842 | 153.9285 | 160 | 0 | 0 | 0 | 45.4802 | 0 | 73.1012 | 160 | 41.9025 | 30.3201 | 72.678
161 | 0 | 120.4706 | 115.3057 | 52.0632 | 183.713 | 52.0632 | 235.7762 | 161 | 45.7389 | 80.3137 | 134.3758 | 161 | 92.2445 | 92.2445 | 42.9399 | 0 | 0 | 161 | 0 | 120.4706 | 103.5485 | 52.0632 | 171.9559 | 52.0632 | 224.0191 | 161 | 45.7389 | 80.3137 | 134.3758 | 134.3758 | 161 | 82.8388 | 9.4057 | 92.2445 | 42.9399 | 0 | 0 | 161 | 5.3675 | 5.3675 | 161 | 3.2726 | 7.5145 | 10.5043 | 161 | 32.7303 | 0 | 21.9178 | 161 | 21.8202 | 131.3948 | 153.8852 | 161 | 0 | 0 | 0 | 94.8149 | 0 | 52.0632 | 161 | 74.7663 | 63.2099 | 134.3758
162 | 0 | 124.8145 | 113.602 | 56.9619 | 181.4545 | 56.9619 | 238.4165 | 162 | 33.3843 | 83.2097 | 112.0286 | 162 | 90.8816 | 90.8816 | 42.5999 | 0 | 0 | 162 | 0 | 124.8145 | 105.0459 | 56.9619 | 172.8985 | 56.9619 | 229.8604 | 162 | 33.3843 | 83.2097 | 112.0286 | 112.0286 | 162 | 84.0367 | 6.8448 | 90.8816 | 42.5999 | 0 | 0 | 162 | 5.325 | 5.325 | 162 | 1.7508 | 7.455 | 9.2116 | 162 | 11.1053 | 0 | 21.9178 | 162 | 7.4035 | 134.1117 | 150.7614 | 162 | 0 | 0 | 0 | 90.6076 | 0 | 56.9619 | 162 | 49.3722 | 60.4051 | 112.0286
163 | 0 | 144 | 151.5498 | 42.1163 | 253.4335 | 42.1163 | 295.5498 | 163 | 96.1272 | 96 | 185.1046 | 163 | 121.2398 | 121.2398 | 54.0144 | 0 | 0 | 163 | 0 | 144 | 125.4538 | 42.1163 | 227.3375 | 42.1163 | 269.4538 | 163 | 96.1272 | 96 | 185.1046 | 185.1046 | 163 | 100.3631 | 20.8768 | 121.2398 | 54.0144 | 0 | 0 | 163 | 6.7518 | 6.7518 | 163 | 1.2405 | 9.4525 | 10.97 | 163 | 25.4244 | 0 | 21.9178 | 163 | 16.9496 | 142.7046 | 155.1391 | 163 | 0 | 0 | 0 | 42 | 0 | 42.1163 | 163 | 155.7556 | 28 | 185.1046
164 | 0 | 144 | 133.2708 | 45.0371 | 232.2337 | 45.0371 | 277.2708 | 164 | 19.3446 | 96 | 125.2094 | 164 | 106.6167 | 106.6167 | 54.7477 | 0 | 0 | 164 | 0 | 144 | 122.2431 | 45.0371 | 221.206 | 45.0371 | 266.2431 | 164 | 19.3446 | 96 | 125.2094 | 125.2094 | 164 | 97.7945 | 8.8222 | 106.6167 | 54.7477 | 0 | 0 | 164 | 6.8435 | 6.8435 | 164 | 6.2331 | 9.5809 | 15.814 | 164 | 21.0046 | 0 | 21.9178 | 164 | 14.003 | 140.2041 | 158.7223 | 164 | 0 | 0 | 0 | 24.4285 | 0 | 45.0371 | 164 | 108.9237 | 16.2857 | 125.2094
165 | 0 | 137.106 | 124.6361 | 58.3993 | 203.3427 | 58.3993 | 261.7421 | 165 | 2.8509 | 91.404 | 95.2426 | 165 | 99.7089 | 99.7089 | 53.4367 | 0 | 0 | 165 | 0 | 137.106 | 124.166 | 58.3993 | 202.8726 | 58.3993 | 261.272 | 165 | 2.8509 | 91.404 | 95.2426 | 95.2426 | 165 | 99.3328 | 0.37608 | 99.7089 | 53.4367 | 0 | 0 | 165 | 6.6796 | 6.6796 | 165 | 4.8547 | 9.3514 | 14.2061 | 165 | 16.5847 | 0 | 21.9178 | 165 | 11.0565 | 155.4105 | 166.467 | 165 | 0 | 0 | 0 | 0 | 0 | 58.3993 | 165 | 95.2426 | 0 | 95.2426
166 | 0 | 128.8891 | 128.3885 | 55.8465 | 201.4311 | 55.8465 | 257.2776 | 166 | 29.4751 | 85.9261 | 110.9803 | 166 | 102.7108 | 102.7108 | 53.8528 | 0 | 0 | 166 | 0 | 128.8891 | 123.6713 | 55.8465 | 196.7139 | 55.8465 | 252.5604 | 166 | 29.4751 | 85.9261 | 110.9803 | 110.9803 | 166 | 98.937 | 3.7738 | 102.7108 | 53.8528 | 0 | 0 | 166 | 6.7316 | 6.7316 | 166 | 6.6757 | 9.4242 | 16.0999 | 166 | 38.2098 | 0 | 21.9178 | 166 | 25.4732 | 151.7662 | 163.0027 | 166 | 0 | 12 | 0 | 90 | 0 | 55.8465 | 166 | 51.495 | 60 | 110.9803
167 | 0 | 144 | 137.439 | 44.6461 | 236.7928 | 44.6461 | 281.439 | 167 | 47.3822 | 96 | 140.5891 | 167 | 109.9512 | 109.9512 | 52.4747 | 0 | 0 | 167 | 0 | 144 | 127.5205 | 44.6461 | 226.8744 | 44.6461 | 271.5205 | 167 | 47.3822 | 96 | 140.5891 | 140.5891 | 167 | 102.0164 | 7.9348 | 109.9512 | 52.4747 | 0 | 0 | 167 | 6.5593 | 6.5593 | 167 | 3.493 | 9.1831 | 12.6761 | 167 | 21.0046 | 0 | 21.9178 | 167 | 14.003 | 149.5486 | 164.2349 | 167 | 0 | 0 | 0 | 89.2242 | 0 | 44.6461 | 167 | 80.5916 | 59.4828 | 140.5891
168 | 0 | 144 | 118.7516 | 46.8598 | 215.8918 | 46.8598 | 262.7516 | 168 | 19.9688 | 96 | 123.9181 | 168 | 95.0012 | 95.0012 | 43.0075 | 0 | 0 | 168 | 0 | 144 | 111.2757 | 46.8598 | 208.4159 | 46.8598 | 255.2757 | 168 | 19.9688 | 96 | 123.9181 | 123.9181 | 168 | 89.0206 | 5.9807 | 95.0012 | 43.0075 | 0 | 0 | 168 | 5.3759 | 5.3759 | 168 | 5.614 | 7.5263 | 13.1403 | 168 | 21.9178 | 0 | 21.9178 | 168 | 14.6119 | 157.8584 | 164.3484 | 168 | 0 | 0 | 0 | 45.157 | 0 | 46.8598 | 168 | 93.8135 | 30.1046 | 123.9181
169 | 0 | 142.7689 | 124.8134 | 50.5453 | 217.037 | 50.5453 | 267.5823 | 169 | 46.4334 | 95.1792 | 133.5449 | 169 | 99.8507 | 99.8507 | 42.9744 | 0 | 0 | 169 | 0 | 142.7689 | 124.7155 | 50.5453 | 216.939 | 50.5453 | 267.4844 | 169 | 46.4334 | 95.1792 | 133.5449 | 133.5449 | 169 | 99.7724 | 0.078338 | 99.8507 | 42.9744 | 0 | 0 | 169 | 5.3718 | 5.3718 | 169 | 6.3041 | 7.5205 | 13.8246 | 169 | 10.0457 | 0 | 21.9178 | 169 | 6.6971 | 122.0273 | 150.1561 | 169 | 0 | 0 | 0 | 24 | 0 | 50.5453 | 169 | 117.5449 | 16 | 133.5449
170 | 0 | 144 | 153.1347 | 41.4838 | 255.6509 | 41.4838 | 297.1347 | 170 | 100.9219 | 96 | 193.4018 | 170 | 122.5078 | 122.5078 | 54.3234 | 0 | 0 | 170 | 0 | 144 | 147.8686 | 41.4838 | 250.3847 | 41.4838 | 291.8686 | 170 | 100.9219 | 96 | 193.4018 | 193.4018 | 170 | 118.2948 | 4.2129 | 122.5078 | 54.3234 | 0 | 0 | 170 | 6.7904 | 6.7904 | 170 | 5.3247 | 9.5066 | 14.8313 | 170 | 23.7443 | 0 | 21.9178 | 170 | 15.8295 | 133.8387 | 148.9995 | 170 | 0 | 0 | 0 | 40.7998 | 0 | 41.4838 | 170 | 166.2019 | 27.1999 | 193.4018
171 | 0 | 144 | 160.6194 | 31.2667 | 273.3528 | 31.2667 | 304.6194 | 171 | 123.9296 | 96 | 219.9296 | 171 | 128.4956 | 128.4956 | 55.7096 | 0 | 0 | 171 | 0 | 144 | 150.6019 | 31.2667 | 263.3352 | 31.2667 | 294.6019 | 171 | 123.9296 | 96 | 219.9296 | 219.9296 | 171 | 120.4815 | 8.0141 | 128.4956 | 55.7096 | 0 | 0 | 171 | 6.9637 | 6.9637 | 171 | 7.0234 | 9.7492 | 16.7725 | 171 | 21.9178 | 0 | 21.9178 | 171 | 14.6119 | 143.9549 | 159.4789 | 171 | 0 | 0 | 0 | 30 | 0 | 31.2667 | 171 | 199.9296 | 20 | 219.9296
172 | 0 | 144 | 139.7722 | 38.1318 | 245.6405 | 38.1318 | 283.7722 | 172 | 42.1874 | 96 | 147.5439 | 172 | 111.8178 | 111.8178 | 55.3803 | 0 | 0 | 172 | 0 | 144 | 128.39 | 38.1318 | 234.2582 | 38.1318 | 272.39 | 172 | 42.1874 | 96 | 147.5439 | 147.5439 | 172 | 102.712 | 9.1058 | 111.8178 | 55.3803 | 0 | 0 | 172 | 6.9225 | 6.9225 | 172 | 6.3737 | 9.6916 | 16.0653 | 172 | 17.498 | 0 | 21.9178 | 172 | 11.6653 | 152.3697 | 164.035 | 172 | 0 | 0 | 0 | 0 | 0 | 38.1318 | 172 | 147.5439 | 0 | 147.5439
173 | 0 | 144 | 134.2069 | 51.6607 | 226.5462 | 51.6607 | 278.2069 | 173 | 16.2968 | 96 | 113.1664 | 173 | 107.3655 | 107.3655 | 56.1062 | 0 | 0 | 173 | 0 | 144 | 131.0299 | 51.6607 | 223.3691 | 51.6607 | 275.0299 | 173 | 16.2968 | 96 | 113.1664 | 113.1664 | 173 | 104.8239 | 2.5417 | 107.3655 | 56.1062 | 0 | 0 | 173 | 7.0133 | 7.0133 | 173 | 2.7795 | 9.8186 | 12.1046 | 173 | 22.8311 | 0 | 21.9178 | 173 | 15.2207 | 152.9109 | 168.1316 | 173 | 0 | 0 | 0 | 30 | 0 | 51.6607 | 173 | 95.4116 | 20 | 113.1664
174 | 0 | 129.8771 | 136.6713 | 51.287 | 215.2615 | 51.287 | 266.5485 | 174 | 60.2828 | 86.5848 | 137.2012 | 174 | 109.3371 | 109.3371 | 53.9881 | 0 | 0 | 174 | 0 | 129.8771 | 136.508 | 51.287 | 215.0981 | 51.287 | 266.3851 | 174 | 60.2828 | 86.5848 | 137.2012 | 137.2012 | 174 | 109.2064 | 0.13069 | 109.3371 | 53.9881 | 0 | 0 | 174 | 6.7485 | 6.7485 | 174 | 1.7383 | 9.4479 | 11.2409 | 174 | 23.7443 | 0 | 21.9178 | 174 | 15.8295 | 167.6068 | 181.3944 | 174 | 0 | 0 | 0 | 64.4574 | 0 | 51.287 | 174 | 99.6326 | 42.9716 | 137.2012
175 | 0 | 144 | 126.147 | 42.7603 | 227.3867 | 42.7603 | 270.147 | 175 | 44.0238 | 96 | 139.4641 | 175 | 100.9176 | 100.9176 | 44.1128 | 0 | 0 | 175 | 0 | 144 | 121.3204 | 42.7603 | 222.5601 | 42.7603 | 265.3204 | 175 | 44.0238 | 96 | 139.4641 | 139.4641 | 175 | 97.0563 | 3.8613 | 100.9176 | 44.1128 | 0 | 0 | 175 | 5.5141 | 5.5141 | 175 | 7.8395 | 7.7197 | 15.9979 | 175 | 34.5568 | 0 | 21.9178 | 175 | 23.0379 | 200.7247 | 186.5774 | 175 | 0 | 12 | 0 | 102 | 0 | 42.7603 | 175 | 63.8159 | 68 | 139.4641
176 | 0 | 144 | 117.6331 | 49.5679 | 212.0653 | 49.5679 | 261.6331 | 176 | 9.5228 | 96 | 115.8639 | 176 | 94.1065 | 94.1065 | 44.2019 | 0 | 0 | 176 | 0 | 144 | 113.0339 | 49.5679 | 207.466 | 49.5679 | 257.0339 | 176 | 9.5228 | 96 | 115.8639 | 115.8639 | 176 | 90.4271 | 3.6794 | 94.1065 | 44.2019 | 0 | 0 | 176 | 5.5252 | 5.5252 | 176 | 4.554 | 7.7353 | 11.9933 | 176 | 21.9178 | 0 | 21.9178 | 176 | 14.6119 | 162.102 | 192.5764 | 176 | 0 | 0 | 0 | 51.9885 | 0 | 49.5679 | 176 | 82.2182 | 34.659 | 115.8639
177 | 0 | 134.0625 | 123.3978 | 62.5621 | 194.8982 | 62.5621 | 257.4603 | 177 | 0 | 89.375 | 86.5363 | 177 | 98.7182 | 98.7182 | 54.0307 | 0 | 0 | 177 | 0 | 134.0625 | 111.0231 | 62.5621 | 182.5236 | 62.5621 | 245.0857 | 177 | 0 | 89.375 | 86.5363 | 86.5363 | 177 | 88.8185 | 9.8997 | 98.7182 | 54.0307 | 0 | 0 | 177 | 6.7538 | 6.7538 | 177 | 1.668 | 9.4554 | 9.964 | 177 | 10.0457 | 0 | 21.9178 | 177 | 6.6971 | 167.329 | 193.5168 | 177 | 0 | 0 | 0 | 38.9381 | 0 | 62.5621 | 177 | 60.6799 | 25.9587 | 86.5363
178 | 0 | 122.9819 | 121.5034 | 58.5891 | 185.8962 | 58.5891 | 244.4853 | 178 | 15.0823 | 81.9879 | 98.3236 | 178 | 97.2027 | 97.2027 | 53.1923 | 0 | 0 | 178 | 0 | 122.9819 | 108.9153 | 58.5891 | 173.3082 | 58.5891 | 231.8973 | 178 | 15.0823 | 81.9879 | 98.3236 | 98.3236 | 178 | 87.1323 | 10.0704 | 97.2027 | 53.1923 | 0 | 0 | 178 | 6.649 | 6.649 | 178 | 2.742 | 9.3086 | 13.506 | 178 | 25.5847 | 0 | 21.9178 | 178 | 17.0565 | 192.3105 | 196.0083 | 178 | 0 | 0 | 0 | 46.8099 | 0 | 58.5891 | 178 | 66.0015 | 31.2066 | 98.3236
179 | 0 | 108.9454 | 115.9985 | 67.1906 | 157.7533 | 67.1906 | 224.9439 | 179 | 12.2858 | 72.6302 | 79.7094 | 179 | 92.7988 | 92.7988 | 54.0265 | 0 | 0 | 179 | 0 | 108.9454 | 110.4818 | 67.1906 | 152.2365 | 67.1906 | 219.4271 | 179 | 12.2858 | 72.6302 | 79.7094 | 79.7094 | 179 | 88.3854 | 4.4134 | 92.7988 | 54.0265 | 0 | 0 | 179 | 6.7533 | 6.7533 | 179 | 3.6465 | 9.4546 | 13.1012 | 179 | 19.1641 | 0 | 21.9178 | 179 | 12.7761 | 181.6712 | 209.5089 | 179 | 0 | 0 | 0 | 30.076 | 0 | 67.1906 | 179 | 59.6588 | 20.0507 | 79.7094
180 | 0 | 109.5348 | 123.4508 | 59.5493 | 173.4363 | 59.5493 | 232.9856 | 180 | 35.6254 | 73.0232 | 105.0994 | 180 | 98.7606 | 98.7606 | 55.1239 | 0 | 0 | 180 | 0 | 109.5348 | 114.9821 | 59.5493 | 164.9676 | 59.5493 | 224.5169 | 180 | 35.6254 | 73.0232 | 105.0994 | 105.0994 | 180 | 91.9856 | 6.775 | 98.7606 | 55.1239 | 0 | 0 | 180 | 6.8905 | 6.8905 | 180 | 3.2453 | 9.6467 | 12.892 | 180 | 21.9178 | 0 | 21.9178 | 180 | 14.6119 | 207.9179 | 219.0749 | 180 | 0 | 0 | 0 | 50.5359 | 0 | 59.5493 | 180 | 76.0158 | 33.6906 | 105.0994
181 | 0 | 144 | 133.7336 | 45.0831 | 232.6505 | 45.0831 | 277.7336 | 181 | 34.5022 | 96 | 130.5022 | 181 | 106.9869 | 106.9869 | 52.0864 | 0 | 0 | 181 | 0 | 144 | 132.3289 | 45.0831 | 231.2458 | 45.0831 | 276.3289 | 181 | 34.5022 | 96 | 130.5022 | 130.5022 | 181 | 105.8632 | 1.1237 | 106.9869 | 52.0864 | 0 | 0 | 181 | 6.5108 | 6.5108 | 181 | 2.3803 | 9.1151 | 10.6262 | 181 | 18.4112 | 0 | 21.9178 | 181 | 12.2741 | 231.5386 | 249.2756 | 181 | 0 | 0 | 0 | 36 | 0 | 45.0831 | 181 | 101.8952 | 24 | 130.5022
182 | 0 | 144 | 112.7468 | 52.8279 | 203.9189 | 52.8279 | 256.7468 | 182 | 0.53863 | 96 | 107.6307 | 182 | 90.1974 | 90.1974 | 42.0897 | 0 | 0 | 182 | 0 | 144 | 112.2919 | 52.8279 | 203.464 | 52.8279 | 256.2919 | 182 | 0.53863 | 96 | 107.6307 | 107.6307 | 182 | 89.8335 | 0.3639 | 90.1974 | 42.0897 | 0 | 0 | 182 | 5.2612 | 5.2612 | 182 | 1.0673 | 7.3657 | 7.8532 | 182 | 25.6893 | 0 | 21.9178 | 182 | 17.1262 | 240 | 247.0219 | 182 | 0 | 0 | 0 | 120 | 0 | 52.8279 | 182 | 27.6307 | 80 | 107.6307
183 | 0 | 139.8766 | 114.5184 | 56.111 | 198.284 | 56.111 | 254.395 | 183 | 12.5772 | 93.2511 | 103.9232 | 183 | 91.6147 | 91.6147 | 42.4737 | 0 | 0 | 183 | 0 | 139.8766 | 113.6775 | 56.111 | 197.4431 | 56.111 | 253.5541 | 183 | 12.5772 | 93.2511 | 103.9232 | 103.9232 | 183 | 90.942 | 0.67271 | 91.6147 | 42.4737 | 0 | 0 | 183 | 5.3092 | 5.3092 | 183 | 1.9947 | 7.4329 | 10.8767 | 183 | 22.5662 | 0 | 21.9178 | 183 | 15.0441 | 240 | 249.027 | 183 | 0 | 12 | 0 | 60.8747 | 0 | 56.111 | 183 | 63.3401 | 40.5832 | 103.9232
184 | 0 | 144 | 125.8856 | 58.4798 | 211.4057 | 58.4798 | 269.8856 | 184 | 0 | 96 | 95.0636 | 184 | 100.7084 | 100.7084 | 52.7084 | 0 | 0 | 184 | 0 | 144 | 118.5913 | 58.4798 | 204.1115 | 58.4798 | 262.5913 | 184 | 0 | 96 | 95.0636 | 95.0636 | 184 | 94.8731 | 5.8354 | 100.7084 | 52.7084 | 0 | 0 | 184 | 6.5886 | 6.5886 | 184 | 3.2392 | 9.224 | 12.4632 | 184 | 21.9178 | 0 | 21.9178 | 184 | 14.6119 | 211.4154 | 224.339 | 184 | 0 | 0 | 0 | 61.1976 | 0 | 58.4798 | 184 | 54.2652 | 40.7984 | 95.0636
185 | 0 | 135.3133 | 123.7341 | 59.5493 | 199.4981 | 59.5493 | 259.0474 | 185 | 2.8442 | 90.2089 | 92.6857 | 185 | 98.9872 | 98.9872 | 53.314 | 0 | 0 | 185 | 0 | 135.3133 | 119.8696 | 59.5493 | 195.6336 | 59.5493 | 255.1829 | 185 | 2.8442 | 90.2089 | 92.6857 | 92.6857 | 185 | 95.8956 | 3.0916 | 98.9872 | 53.314 | 0 | 0 | 185 | 6.6642 | 6.6642 | 185 | 4.6391 | 9.3299 | 13.9691 | 185 | 21.0046 | 0 | 21.9178 | 185 | 14.003 | 176.0008 | 200.3157 | 185 | 0 | 0 | 0 | 36 | 0 | 59.5493 | 185 | 68.6857 | 24 | 92.6857
186 | 0 | 111.7835 | 118.9702 | 59.9173 | 170.8365 | 59.9173 | 230.7537 | 186 | 26.8629 | 74.5223 | 105.0355 | 186 | 95.1762 | 95.1762 | 52.5424 | 0 | 0 | 186 | 0 | 111.7835 | 111.2319 | 59.9173 | 163.0981 | 59.9173 | 223.0154 | 186 | 26.8629 | 74.5223 | 105.0355 | 105.0355 | 186 | 88.9855 | 6.1907 | 95.1762 | 52.5424 | 0 | 0 | 186 | 6.5678 | 6.5678 | 186 | 4.4781 | 9.1949 | 13.673 | 186 | 21.0046 | 0 | 21.9178 | 186 | 14.003 | 159.6762 | 181.3403 | 186 | 0 | 0 | 0 | 20.1141 | 0 | 59.9173 | 186 | 91.6261 | 13.4094 | 105.0355
187 | 0 | 129.7137 | 126.4492 | 56.272 | 199.891 | 56.272 | 256.163 | 187 | 25.8212 | 86.4758 | 112.003 | 187 | 101.1594 | 101.1594 | 52.7572 | 0 | 0 | 187 | 0 | 129.7137 | 110.7742 | 56.272 | 184.216 | 56.272 | 240.4879 | 187 | 25.8212 | 86.4758 | 112.003 | 112.003 | 187 | 88.6194 | 12.54 | 101.1594 | 52.7572 | 0 | 0 | 187 | 6.5947 | 6.5947 | 187 | 4.9281 | 9.2325 | 14.1606 | 187 | 20.2377 | 0 | 21.9178 | 187 | 13.4918 | 163.2871 | 176.7789 | 187 | 0 | 0 | 0 | 41.791 | 0 | 56.272 | 187 | 84.1423 | 27.8607 | 112.003
188 | 0 | 130.8026 | 127.4872 | 55.8407 | 202.4491 | 55.8407 | 258.2898 | 188 | 36.1061 | 87.2017 | 118.7404 | 188 | 101.9898 | 101.9898 | 51.1677 | 0 | 0 | 188 | 0 | 130.8026 | 110.1169 | 55.8407 | 185.0788 | 55.8407 | 240.9195 | 188 | 36.1061 | 87.2017 | 118.7404 | 118.7404 | 188 | 88.0935 | 13.8962 | 101.9898 | 51.1677 | 0 | 0 | 188 | 6.396 | 6.396 | 188 | 2.827 | 8.9543 | 11.7051 | 188 | 35.4701 | 0 | 21.9178 | 188 | 23.6467 | 199.4883 | 185.3451 | 188 | 0 | 0 | 0 | 67.1763 | 0 | 55.8407 | 188 | 73.9562 | 44.7842 | 118.7404
189 | 0 | 134.4462 | 126.1588 | 46.3251 | 214.2799 | 46.3251 | 260.605 | 189 | 62.6669 | 89.6308 | 147.3137 | 189 | 100.9271 | 100.9271 | 43.5783 | 0 | 0 | 189 | 0 | 134.4462 | 95.2849 | 46.3251 | 183.406 | 46.3251 | 229.7311 | 189 | 62.6669 | 89.6308 | 147.3137 | 147.3137 | 189 | 76.2279 | 24.6992 | 100.9271 | 43.5783 | 0 | 0 | 189 | 5.4473 | 5.4473 | 189 | 3.5538 | 7.6262 | 11.2563 | 189 | 15.5251 | 0 | 21.9178 | 189 | 10.3501 | 154.2588 | 181.7781 | 189 | 0 | 0 | 0 | 87.4194 | 0 | 46.3251 | 189 | 89.0341 | 58.2796 | 147.3137
190 | 0 | 144 | 123.6461 | 41.7138 | 225.9323 | 41.7138 | 267.6461 | 190 | 42.9736 | 96 | 148.8734 | 190 | 98.9169 | 98.9169 | 42.3222 | 0 | 0 | 190 | 0 | 144 | 106.7263 | 41.7138 | 209.0125 | 41.7138 | 250.7263 | 190 | 42.9736 | 96 | 148.8734 | 148.8734 | 190 | 85.3811 | 13.5358 | 98.9169 | 42.3222 | 0 | 0 | 190 | 5.2903 | 5.2903 | 190 | 5.404 | 7.4064 | 12.8104 | 190 | 17.3516 | 0 | 21.9178 | 190 | 11.5677 | 160.6621 | 187.1881 | 190 | 0 | 0 | 0 | 30 | 0 | 41.7138 | 190 | 128.8734 | 20 | 148.8734
191 | 0 | 126.9289 | 125.8526 | 56.6687 | 196.1129 | 56.6687 | 252.7816 | 191 | 32.4019 | 84.6193 | 116.273 | 191 | 100.6821 | 100.6821 | 51.8921 | 0 | 0 | 191 | 0 | 126.9289 | 106.0138 | 56.6687 | 176.274 | 56.6687 | 232.9427 | 191 | 32.4019 | 84.6193 | 116.273 | 116.273 | 191 | 84.811 | 15.8711 | 100.6821 | 51.8921 | 0 | 0 | 191 | 6.4865 | 6.4865 | 191 | 2.3215 | 9.0811 | 10.8143 | 191 | 19.3244 | 0 | 21.9178 | 191 | 12.883 | 190.7048 | 195.1652 | 191 | 0 | 0 | 0 | 25.994 | 0 | 56.6687 | 191 | 98.9437 | 17.3293 | 116.273
192 | 0 | 131.3395 | 133.932 | 50.0106 | 215.261 | 50.0106 | 265.2716 | 192 | 52.0808 | 87.5597 | 134.1969 | 192 | 107.1456 | 107.1456 | 52.9496 | 0 | 0 | 192 | 0 | 131.3395 | 124.3362 | 50.0106 | 205.6651 | 50.0106 | 255.6757 | 192 | 52.0808 | 87.5597 | 134.1969 | 134.1969 | 192 | 99.4689 | 7.6767 | 107.1456 | 52.9496 | 0 | 0 | 192 | 6.6187 | 6.6187 | 192 | 0.77358 | 9.2662 | 9.4791 | 192 | 19.1781 | 0 | 21.9178 | 192 | 12.7854 | 168.7656 | 190.2903 | 192 | 0 | 0 | 0 | 48.8818 | 0 | 50.0106 | 192 | 101.609 | 32.5878 | 134.1969
193 | 0 | 144 | 147.2723 | 41.0871 | 250.1852 | 41.0871 | 291.2723 | 193 | 84.3371 | 96 | 174.941 | 193 | 117.8178 | 117.8178 | 52.9504 | 0 | 0 | 193 | 0 | 144 | 139.533 | 41.0871 | 242.4459 | 41.0871 | 283.533 | 193 | 84.3371 | 96 | 174.941 | 174.941 | 193 | 111.6264 | 6.1914 | 117.8178 | 52.9504 | 0 | 0 | 193 | 6.6188 | 6.6188 | 193 | 2.687 | 9.2663 | 13.1023 | 193 | 36.3833 | 0 | 21.9178 | 193 | 24.2555 | 183.8329 | 193.9492 | 193 | 0 | 0 | 0 | 72 | 0 | 41.0871 | 193 | 126.941 | 48 | 174.941
194 | 0 | 144 | 127.7436 | 51.4538 | 220.2898 | 51.4538 | 271.7436 | 194 | 9.9132 | 96 | 110.6862 | 194 | 102.1949 | 102.1949 | 52.2122 | 0 | 0 | 194 | 0 | 144 | 126.4433 | 51.4538 | 218.9895 | 51.4538 | 270.4433 | 194 | 9.9132 | 96 | 110.6862 | 110.6862 | 194 | 101.1546 | 1.0403 | 102.1949 | 52.2122 | 0 | 0 | 194 | 6.5265 | 6.5265 | 194 | 3.3475 | 9.1371 | 12.4846 | 194 | 12.7854 | 0 | 21.9178 | 194 | 8.5236 | 166.908 | 194.9166 | 194 | 0 | 0 | 0 | 16.4631 | 0 | 51.4538 | 194 | 99.7108 | 10.9754 | 110.6862
195 | 0 | 144 | 129.4483 | 45.8363 | 227.612 | 45.8363 | 273.4483 | 195 | 32.8811 | 96 | 135.437 | 195 | 103.5587 | 103.5587 | 48.9824 | 0 | 0 | 195 | 0 | 144 | 127.1838 | 45.8363 | 225.3475 | 45.8363 | 271.1838 | 195 | 32.8811 | 96 | 135.437 | 135.437 | 195 | 101.747 | 1.8116 | 103.5587 | 48.9824 | 0 | 0 | 195 | 6.1228 | 6.1228 | 195 | 4.2031 | 8.5719 | 12.775 | 195 | 19.3244 | 0 | 21.9178 | 195 | 12.883 | 194.8435 | 199.3159 | 195 | 0 | 0 | 0 | 36 | 0 | 45.8363 | 195 | 111.437 | 24 | 135.437
196 | 0 | 133.238 | 109.9169 | 58.3763 | 184.7786 | 58.3763 | 243.1549 | 196 | 11.7678 | 88.8254 | 95.3065 | 196 | 87.9335 | 87.9335 | 41.1673 | 0 | 0 | 196 | 0 | 133.238 | 97.5566 | 58.3763 | 172.4183 | 58.3763 | 230.7947 | 196 | 11.7678 | 88.8254 | 95.3065 | 95.3065 | 196 | 78.0453 | 9.8882 | 87.9335 | 41.1673 | 0 | 0 | 196 | 5.1459 | 5.1459 | 196 | 4.4102 | 7.2043 | 11.6144 | 196 | 35.4701 | 0 | 21.9178 | 196 | 23.6467 | 193.8476 | 184.1885 | 196 | 0 | 0 | 0 | 112.4069 | 0 | 58.3763 | 196 | 20.3686 | 74.9379 | 95.3065
197 | 0 | 117.1438 | 121.9754 | 51.2065 | 187.9127 | 51.2065 | 239.1192 | 197 | 85.9863 | 78.0959 | 158.0399 | 197 | 97.5803 | 97.5803 | 41.3351 | 0 | 0 | 197 | 0 | 117.1438 | 114.2918 | 51.2065 | 180.229 | 51.2065 | 231.4356 | 197 | 85.9863 | 78.0959 | 158.0399 | 158.0399 | 197 | 91.4334 | 6.1469 | 97.5803 | 41.3351 | 0 | 0 | 197 | 5.1669 | 5.1669 | 197 | 3.1589 | 7.2337 | 10.3925 | 197 | 26.484 | 0 | 21.9178 | 197 | 17.656 | 159.0202 | 176.6762 | 197 | 0 | 0 | 0 | 71.7357 | 0 | 51.2065 | 197 | 110.2161 | 47.8238 | 158.0399
198 | 0 | 144 | 122.9381 | 47.1128 | 219.8253 | 47.1128 | 266.9381 | 198 | 18.5716 | 96 | 120.3385 | 198 | 98.3505 | 98.3505 | 46.6361 | 0 | 0 | 198 | 0 | 144 | 109.5715 | 47.1128 | 206.4588 | 47.1128 | 253.5715 | 198 | 18.5716 | 96 | 120.3385 | 120.3385 | 198 | 87.6572 | 10.6932 | 98.3505 | 46.6361 | 0 | 0 | 198 | 5.8295 | 5.8295 | 198 | 1.4309 | 8.1613 | 8.8324 | 198 | 7.3059 | 0 | 21.9178 | 198 | 4.8706 | 120.8798 | 167.4669 | 198 | 0 | 0 | 0 | 42 | 0 | 47.1128 | 198 | 92.3385 | 28 | 120.3385
199 | 0 | 144 | 133.8529 | 42.2888 | 235.5641 | 42.2888 | 277.8529 | 199 | 60.3618 | 96 | 152.1207 | 199 | 107.0823 | 107.0823 | 47.01 | 0 | 0 | 199 | 0 | 144 | 120.3702 | 42.2888 | 222.0814 | 42.2888 | 264.3702 | 199 | 60.3618 | 96 | 152.1207 | 152.1207 | 199 | 96.2962 | 10.7861 | 107.0823 | 47.01 | 0 | 0 | 199 | 5.8762 | 5.8762 | 199 | 2.403 | 8.2267 | 11.3895 | 199 | 15.6715 | 0 | 21.9178 | 199 | 10.4477 | 154.171 | 164.6187 | 199 | 0 | 0 | 0 | 6 | 0 | 42.2888 | 199 | 149.447 | 4 | 152.1207
200 | 0 | 144 | 126.1498 | 44.8646 | 225.2852 | 44.8646 | 270.1498 | 200 | 31.4255 | 96 | 125.8997 | 200 | 100.9199 | 100.9199 | 46.6348 | 0 | 0 | 200 | 0 | 144 | 98.5462 | 44.8646 | 197.6816 | 44.8646 | 242.5462 | 200 | 31.4255 | 96 | 125.8997 | 125.8997 | 200 | 78.837 | 22.0829 | 100.9199 | 46.6348 | 0 | 0 | 200 | 5.8293 | 5.8293 | 200 | 4.5872 | 8.1611 | 12.7483 | 200 | 28.1641 | 0 | 21.9178 | 200 | 18.7761 | 159.1363 | 174.8549 | 200 | 0 | 0 | 0 | 36 | 0 | 44.8646 | 200 | 100.5735 | 24 | 125.8997
201 | 0 | 144 | 134.9101 | 36.2056 | 242.7045 | 36.2056 | 278.9101 | 201 | 61.8249 | 96 | 159.6124 | 201 | 107.9281 | 107.9281 | 47.5631 | 0 | 0 | 201 | 0 | 144 | 117.8935 | 36.2056 | 225.6879 | 36.2056 | 261.8935 | 201 | 61.8249 | 96 | 159.6124 | 159.6124 | 201 | 94.3148 | 13.6133 | 107.9281 | 47.5631 | 0 | 0 | 201 | 5.9454 | 5.9454 | 201 | 4.4932 | 8.3235 | 12.8168 | 201 | 21.0046 | 0 | 21.9178 | 201 | 14.003 | 166.0354 | 179.2866 | 201 | 0 | 0 | 0 | 24 | 0 | 36.2056 | 201 | 143.6124 | 16 | 159.6124
202 | 0 | 144 | 139.5004 | 39.7762 | 243.7242 | 39.7762 | 283.5004 | 202 | 87.6066 | 96 | 181.819 | 202 | 111.6003 | 111.6003 | 46.079 | 0 | 0 | 202 | 0 | 144 | 135.3057 | 39.7762 | 239.5295 | 39.7762 | 279.3057 | 202 | 87.6066 | 96 | 181.819 | 181.819 | 202 | 108.2446 | 3.3558 | 111.6003 | 46.079 | 0 | 0 | 202 | 5.7599 | 5.7599 | 202 | 2.2812 | 8.0638 | 9.7684 | 202 | 16.5847 | 0 | 21.9178 | 202 | 11.0565 | 167.9338 | 182.7996 | 202 | 0 | 0 | 0 | 30 | 0 | 39.7762 | 202 | 163.5192 | 20 | 181.819
203 | 0 | 144 | 119.1816 | 43.6285 | 219.5532 | 43.6285 | 263.1816 | 203 | 33.4794 | 96 | 129.4794 | 203 | 95.3453 | 95.3453 | 40.6494 | 0 | 0 | 203 | 0 | 144 | 116.0323 | 43.6285 | 216.4038 | 43.6285 | 260.0323 | 203 | 33.4794 | 96 | 129.4794 | 129.4794 | 203 | 92.8258 | 2.5195 | 95.3453 | 40.6494 | 0 | 0 | 203 | 5.0812 | 5.0812 | 203 | 1.7454 | 7.1137 | 8.8591 | 203 | 38.2098 | 0 | 21.9178 | 203 | 25.4732 | 183.6248 | 183.2698 | 203 | 0 | 0 | 0 | 100.3461 | 0 | 43.6285 | 203 | 60.8819 | 66.8974 | 129.4794
204 | 0 | 144 | 129.6881 | 37.0681 | 236.62 | 37.0681 | 273.6881 | 204 | 75.6554 | 96 | 171.6554 | 204 | 103.7504 | 103.7504 | 40.6194 | 0 | 0 | 204 | 0 | 144 | 119.5604 | 37.0681 | 226.4923 | 37.0681 | 263.5604 | 204 | 75.6554 | 96 | 171.6554 | 171.6554 | 204 | 95.6483 | 8.1021 | 103.7504 | 40.6194 | 0 | 0 | 204 | 5.0774 | 5.0774 | 204 | 1.6989 | 7.1084 | 8.9099 | 204 | 6.3927 | 0 | 21.9178 | 204 | 4.2618 | 160.3354 | 190.4254 | 204 | 0 | 0 | 0 | 6 | 0 | 37.0681 | 204 | 173.4163 | 4 | 171.6554
205 | 0 | 144 | 132.0428 | 35.4237 | 240.6191 | 35.4237 | 276.0428 | 205 | 59.0688 | 96 | 166.6566 | 205 | 105.6342 | 105.6342 | 45.8205 | 0 | 0 | 205 | 0 | 144 | 115.1448 | 35.4237 | 223.7212 | 35.4237 | 259.1448 | 205 | 59.0688 | 96 | 166.6566 | 166.6566 | 205 | 92.1159 | 13.5183 | 105.6342 | 45.8205 | 0 | 0 | 205 | 5.7276 | 5.7276 | 205 | 1.462 | 8.0186 | 8.466 | 205 | 22.0642 | 0 | 21.9178 | 205 | 14.7094 | 185.9618 | 195.7651 | 205 | 0 | 0 | 0 | 30 | 0 | 35.4237 | 205 | 140.8957 | 20 | 166.6566
206 | 0 | 140.4585 | 128.8112 | 46.4918 | 222.7779 | 46.4918 | 269.2697 | 206 | 49.3715 | 93.639 | 131.4226 | 206 | 103.049 | 103.049 | 46.3552 | 0 | 0 | 206 | 0 | 140.4585 | 114.9133 | 46.4918 | 208.88 | 46.4918 | 255.3718 | 206 | 49.3715 | 93.639 | 131.4226 | 131.4226 | 206 | 91.9306 | 11.1184 | 103.049 | 46.3552 | 0 | 0 | 206 | 5.7944 | 5.7944 | 206 | 0 | 8.1122 | 9.2432 | 206 | 26.3377 | 0 | 21.9178 | 206 | 17.5584 | 185.1882 | 197.9593 | 206 | 0 | 0 | 0 | 36 | 0 | 46.4918 | 206 | 107.4226 | 24 | 131.4226
207 | 0 | 144 | 132.2583 | 37.3268 | 238.9315 | 37.3268 | 276.2583 | 207 | 58.2941 | 96 | 154.2941 | 207 | 105.8067 | 105.8067 | 46.1479 | 0 | 0 | 207 | 0 | 144 | 123.3678 | 37.3268 | 230.0409 | 37.3268 | 267.3678 | 207 | 58.2941 | 96 | 154.2941 | 154.2941 | 207 | 98.6942 | 7.1124 | 105.8067 | 46.1479 | 0 | 0 | 207 | 5.7685 | 5.7685 | 207 | 2.4948 | 8.0759 | 10.8255 | 207 | 21.1509 | 0 | 21.9178 | 207 | 14.1006 | 169.5336 | 193.3276 | 207 | 0 | 0 | 0 | 30 | 0 | 37.3268 | 207 | 140.1828 | 20 | 154.2941
208 | 0 | 144 | 139.8115 | 34.8717 | 248.9398 | 34.8717 | 283.8115 | 208 | 85.2716 | 96 | 184.2609 | 208 | 111.8492 | 111.8492 | 46.7949 | 0 | 0 | 208 | 0 | 144 | 131.1269 | 34.8717 | 240.2552 | 34.8717 | 275.1269 | 208 | 85.2716 | 96 | 184.2609 | 184.2609 | 208 | 104.9015 | 6.9476 | 111.8492 | 46.7949 | 0 | 0 | 208 | 5.8494 | 5.8494 | 208 | 1.8271 | 8.1891 | 8.9111 | 208 | 19.1781 | 0 | 21.9178 | 208 | 12.7854 | 173.6839 | 186.4693 | 208 | 0 | 0 | 0 | 28.7545 | 0 | 34.8717 | 208 | 163.1991 | 19.1697 | 184.2609
209 | 0 | 144 | 134.4896 | 39.2645 | 239.2252 | 39.2645 | 278.4896 | 209 | 71.3087 | 96 | 166.6694 | 209 | 107.5917 | 107.5917 | 45.33 | 0 | 0 | 209 | 0 | 144 | 127.2593 | 39.2645 | 231.9948 | 39.2645 | 271.2593 | 209 | 71.3087 | 96 | 166.6694 | 166.6694 | 209 | 101.8074 | 5.7843 | 107.5917 | 45.33 | 0 | 0 | 209 | 5.6662 | 5.6662 | 209 | 1.5053 | 7.9327 | 10.6457 | 209 | 33.79 | 0 | 21.9178 | 209 | 22.5266 | 170.014 | 184.8479 | 209 | 0 | 0 | 0 | 78 | 0 | 39.2645 | 209 | 110.6728 | 52 | 166.6694
210 | 0 | 144 | 128.8585 | 41.0814 | 231.7771 | 41.0814 | 272.8585 | 210 | 66.1926 | 96 | 159.8425 | 210 | 103.0868 | 103.0868 | 41.8482 | 0 | 0 | 210 | 0 | 144 | 85.9194 | 41.0814 | 188.838 | 41.0814 | 229.9194 | 210 | 66.1926 | 96 | 159.8425 | 159.8425 | 210 | 68.7355 | 34.3513 | 103.0868 | 41.8482 | 0 | 0 | 210 | 5.231 | 5.231 | 210 | 3.4807 | 7.3234 | 10.8041 | 210 | 25.4244 | 0 | 21.9178 | 210 | 16.9496 | 172.9938 | 187.0313 | 210 | 0 | 12 | 0 | 84.9141 | 0 | 41.0814 | 210 | 103.2331 | 56.6094 | 159.8425
211 | 0 | 144 | 122.7892 | 41.8518 | 224.9374 | 41.8518 | 266.7892 | 211 | 47.0399 | 96 | 143.6318 | 211 | 98.2314 | 98.2314 | 40.8234 | 0 | 0 | 211 | 0 | 144 | 96.5721 | 41.8518 | 198.7203 | 41.8518 | 240.5721 | 211 | 47.0399 | 96 | 143.6318 | 143.6318 | 211 | 77.2577 | 20.9737 | 98.2314 | 40.8234 | 0 | 0 | 211 | 5.1029 | 5.1029 | 211 | 4.9556 | 7.1441 | 12.0997 | 211 | 10.0457 | 0 | 21.9178 | 211 | 6.6971 | 195.2515 | 195.6894 | 211 | 0 | 0 | 0 | 18 | 0 | 41.8518 | 211 | 131.6318 | 12 | 143.6318
212 | 0 | 144 | 141.1526 | 36.7519 | 248.4008 | 36.7519 | 285.1526 | 212 | 88.0857 | 96 | 183.4938 | 212 | 112.9221 | 112.9221 | 47.305 | 0 | 0 | 212 | 0 | 144 | 136.2203 | 36.7519 | 243.4685 | 36.7519 | 280.2203 | 212 | 88.0857 | 96 | 183.4938 | 183.4938 | 212 | 108.9763 | 3.9459 | 112.9221 | 47.305 | 0 | 0 | 212 | 5.9131 | 5.9131 | 212 | 3.9685 | 8.2784 | 12.2468 | 212 | 21.0046 | 0 | 21.9178 | 212 | 14.003 | 159.8664 | 190.7335 | 212 | 0 | 0 | 0 | 0 | 0 | 36.7519 | 212 | 183.4938 | 0 | 183.4938
213 | 0 | 144 | 144.2378 | 36.8956 | 251.3422 | 36.8956 | 288.2378 | 213 | 95.4202 | 96 | 191.4202 | 213 | 115.3903 | 115.3903 | 48.3062 | 0 | 0 | 213 | 0 | 144 | 137.9885 | 36.8956 | 245.0929 | 36.8956 | 281.9885 | 213 | 95.4202 | 96 | 191.4202 | 191.4202 | 213 | 110.3908 | 4.9995 | 115.3903 | 48.3062 | 0 | 0 | 213 | 6.0383 | 6.0383 | 213 | 4.7371 | 8.4536 | 13.1907 | 213 | 19.3244 | 0 | 21.9178 | 213 | 12.883 | 171.31 | 181.5781 | 213 | 0 | 0 | 0 | 5.5143 | 0 | 36.8956 | 213 | 187.744 | 3.6762 | 191.4202
214 | 0 | 144 | 144.5286 | 35.004 | 253.5247 | 35.004 | 288.5286 | 214 | 94.3335 | 96 | 190.3335 | 214 | 115.6229 | 115.6229 | 48.7562 | 0 | 0 | 214 | 0 | 144 | 141.2954 | 35.004 | 250.2914 | 35.004 | 285.2954 | 214 | 94.3335 | 96 | 190.3335 | 190.3335 | 214 | 113.0363 | 2.5866 | 115.6229 | 48.7562 | 0 | 0 | 214 | 6.0945 | 6.0945 | 214 | 3.5421 | 8.5323 | 11.9 | 214 | 21.9178 | 0 | 21.9178 | 214 | 14.6119 | 183.9004 | 179.7352 | 214 | 0 | 0 | 0 | 30 | 0 | 35.004 | 214 | 170.3335 | 20 | 190.3335
215 | 0 | 144 | 148.9166 | 37.2636 | 255.653 | 37.2636 | 292.9166 | 215 | 97.6063 | 96 | 193.6063 | 215 | 119.1333 | 119.1333 | 51.612 | 0 | 0 | 215 | 0 | 144 | 147.2022 | 37.2636 | 253.9387 | 37.2636 | 291.2022 | 215 | 97.6063 | 96 | 193.6063 | 193.6063 | 215 | 117.7618 | 1.3715 | 119.1333 | 51.612 | 0 | 0 | 215 | 6.4515 | 6.4515 | 215 | 1.9631 | 9.0321 | 10.0378 | 215 | 36.3833 | 0 | 21.9178 | 215 | 24.2555 | 143.9511 | 189.5985 | 215 | 0 | 0 | 0 | 56.1906 | 0 | 37.2636 | 215 | 156.1459 | 37.4604 | 193.6063
216 | 0 | 144 | 140.6419 | 31.9854 | 252.6565 | 31.9854 | 284.6419 | 216 | 72.4081 | 96 | 168.4081 | 216 | 112.5135 | 112.5135 | 50.0319 | 0 | 0 | 216 | 0 | 144 | 140.533 | 31.9854 | 252.5476 | 31.9854 | 284.533 | 216 | 72.4081 | 96 | 168.4081 | 168.4081 | 216 | 112.4264 | 0.087128 | 112.5135 | 50.0319 | 0 | 0 | 216 | 6.254 | 6.254 | 216 | 0.178 | 8.7556 | 9.2391 | 216 | 7.4523 | 0 | 21.9178 | 216 | 4.9682 | 209.4954 | 197.2189 | 216 | 0 | 0 | 0 | 38.5722 | 0 | 31.9854 | 216 | 142.6933 | 25.7148 | 168.4081
217 | 0 | 144 | 129.8125 | 30.8642 | 242.9483 | 30.8642 | 273.8125 | 217 | 66.3355 | 96 | 162.3355 | 217 | 103.85 | 103.85 | 42.5829 | 0 | 0 | 217 | 0 | 144 | 128.0759 | 30.8642 | 241.2117 | 30.8642 | 272.0759 | 217 | 66.3355 | 96 | 162.3355 | 162.3355 | 217 | 102.4607 | 1.3893 | 103.85 | 42.5829 | 0 | 0 | 217 | 5.3229 | 5.3229 | 217 | 3.8405 | 7.452 | 12.1189 | 217 | 36.3833 | 0 | 21.9178 | 217 | 24.2555 | 195.7315 | 202.791 | 217 | 0 | 0 | 0 | 102 | 0 | 30.8642 | 217 | 94.3355 | 68 | 162.3355
218 | 0 | 144 | 131.5186 | 33.486 | 242.0326 | 33.486 | 275.5186 | 218 | 74.8617 | 96 | 173.0872 | 218 | 105.2149 | 105.2149 | 42.2425 | 0 | 0 | 218 | 0 | 144 | 123.768 | 33.486 | 234.2819 | 33.486 | 267.768 | 218 | 74.8617 | 96 | 173.0872 | 173.0872 | 218 | 99.0144 | 6.2005 | 105.2149 | 42.2425 | 0 | 0 | 218 | 5.2803 | 5.2803 | 218 | 4.465 | 7.3924 | 11.8575 | 218 | 10.0457 | 0 | 21.9178 | 218 | 6.6971 | 174.1005 | 209.4332 | 218 | 0 | 0 | 0 | 14.8514 | 0 | 33.486 | 218 | 163.1863 | 9.9009 | 173.0872
219 | 0 | 144 | 134.9596 | 43.2432 | 235.7164 | 43.2432 | 278.9596 | 219 | 40.9711 | 96 | 141.1133 | 219 | 107.9677 | 107.9677 | 51.7735 | 0 | 0 | 219 | 0 | 144 | 130.8765 | 43.2432 | 231.6333 | 43.2432 | 274.8765 | 219 | 40.9711 | 96 | 141.1133 | 141.1133 | 219 | 104.7012 | 3.2665 | 107.9677 | 51.7735 | 0 | 0 | 219 | 6.4717 | 6.4717 | 219 | 4.1127 | 9.0604 | 13.173 | 219 | 17.498 | 0 | 21.9178 | 219 | 11.6653 | 193.9434 | 203.7422 | 219 | 0 | 0 | 0 | 24 | 0 | 43.2432 | 219 | 125.2506 | 16 | 141.1133
220 | 0 | 144 | 145.1362 | 42.5475 | 246.5887 | 42.5475 | 289.1362 | 220 | 72.6009 | 96 | 162.2332 | 220 | 116.109 | 116.109 | 53.5888 | 0 | 0 | 220 | 0 | 144 | 144.8358 | 42.5475 | 246.2883 | 42.5475 | 288.8358 | 220 | 72.6009 | 96 | 162.2332 | 162.2332 | 220 | 115.8686 | 0.24034 | 116.109 | 53.5888 | 0 | 0 | 220 | 6.6986 | 6.6986 | 220 | 4.5647 | 9.378 | 13.9428 | 220 | 37.2966 | 0 | 21.9178 | 220 | 24.8644 | 188.7758 | 199.9861 | 220 | 0 | 0 | 0 | 42 | 0 | 42.5475 | 220 | 140.9819 | 28 | 162.2332
221 | 0 | 144 | 159.1429 | 30.2145 | 272.9285 | 30.2145 | 303.1429 | 221 | 120.9508 | 96 | 216.9508 | 221 | 127.3144 | 127.3144 | 55.1242 | 0 | 0 | 221 | 0 | 144 | 156.0717 | 30.2145 | 269.8572 | 30.2145 | 300.0717 | 221 | 120.9508 | 96 | 216.9508 | 216.9508 | 221 | 124.8574 | 2.457 | 127.3144 | 55.1242 | 0 | 0 | 221 | 6.8905 | 6.8905 | 221 | 4.106 | 9.6467 | 13.7528 | 221 | 11.3701 | 0 | 21.9178 | 221 | 7.5801 | 179.9662 | 194.6085 | 221 | 0 | 0 | 0 | 0 | 0 | 30.2145 | 221 | 210.0648 | 0 | 216.9508
222 | 0 | 144 | 160.8239 | 27.3224 | 277.5015 | 27.3224 | 304.8239 | 222 | 134.2211 | 96 | 230.2211 | 222 | 128.6591 | 128.6591 | 53.8149 | 0 | 0 | 222 | 0 | 144 | 152.157 | 27.3224 | 268.8345 | 27.3224 | 296.157 | 222 | 134.2211 | 96 | 230.2211 | 230.2211 | 222 | 121.7256 | 6.9336 | 128.6591 | 53.8149 | 0 | 0 | 222 | 6.7269 | 6.7269 | 222 | 3.8657 | 9.4176 | 13.2833 | 222 | 18 | 0 | 21.9178 | 222 | 12 | 168.0641 | 194.3275 | 222 | 0 | 0 | 0 | 0 | 0 | 27.3224 | 222 | 230.2211 | 0 | 230.2211
223 | 0 | 144 | 145.9278 | 33.5033 | 256.4245 | 33.5033 | 289.9278 | 223 | 86.5245 | 96 | 184.4654 | 223 | 116.7423 | 116.7423 | 51.4374 | 0 | 0 | 223 | 0 | 144 | 132.9218 | 33.5033 | 243.4185 | 33.5033 | 276.9218 | 223 | 86.5245 | 96 | 184.4654 | 184.4654 | 223 | 106.3374 | 10.4049 | 116.7423 | 51.4374 | 0 | 0 | 223 | 6.4297 | 6.4297 | 223 | 2.5307 | 9.0015 | 11.511 | 223 | 24.6575 | 0 | 21.9178 | 223 | 16.4384 | 183.5639 | 200.0023 | 223 | 0 | 0 | 0 | 61.1958 | 0 | 33.5033 | 223 | 144.8027 | 40.7972 | 184.4654
224 | 0 | 144 | 133.3151 | 40.3626 | 236.9525 | 40.3626 | 277.3151 | 224 | 74.8221 | 96 | 168.8811 | 224 | 106.6521 | 106.6521 | 43.6877 | 0 | 0 | 224 | 0 | 144 | 112.9585 | 40.3626 | 216.5958 | 40.3626 | 256.9585 | 224 | 74.8221 | 96 | 168.8811 | 168.8811 | 224 | 90.3668 | 16.2853 | 106.6521 | 43.6877 | 0 | 0 | 224 | 5.461 | 5.461 | 224 | 2.3802 | 7.6453 | 10.0468 | 224 | 34.5568 | 0 | 21.9178 | 224 | 23.0379 | 203.9487 | 204.0611 | 224 | 0 | 0 | 0 | 108 | 0 | 40.3626 | 224 | 95.7467 | 72 | 168.8811
225 | 0 | 144 | 125.9259 | 40.1614 | 229.7645 | 40.1614 | 269.9259 | 225 | 46.5451 | 96 | 142.5451 | 225 | 100.7407 | 100.7407 | 43.4317 | 0 | 0 | 225 | 0 | 144 | 118.6298 | 40.1614 | 222.4684 | 40.1614 | 262.6298 | 225 | 46.5451 | 96 | 142.5451 | 142.5451 | 225 | 94.9038 | 5.8369 | 100.7407 | 43.4317 | 0 | 0 | 225 | 5.429 | 5.429 | 225 | 2.2233 | 7.6005 | 9.2052 | 225 | 6.5391 | 0 | 21.9178 | 225 | 4.3594 | 161.4921 | 188.777 | 225 | 0 | 0 | 0 | 22.195 | 0 | 40.1614 | 225 | 127.7485 | 14.7967 | 142.5451
226 | 0 | 144 | 136.3892 | 41.2941 | 239.0951 | 41.2941 | 280.3892 | 226 | 37.821 | 96 | 145.4088 | 226 | 109.1114 | 109.1114 | 53.5472 | 0 | 0 | 226 | 0 | 144 | 114.5042 | 41.2941 | 217.2101 | 41.2941 | 258.5042 | 226 | 37.821 | 96 | 145.4088 | 145.4088 | 226 | 91.6034 | 17.508 | 109.1114 | 53.5472 | 0 | 0 | 226 | 6.6934 | 6.6934 | 226 | 0.88737 | 9.3708 | 9.8106 | 226 | 27.2509 | 0 | 21.9178 | 226 | 18.1673 | 170.9688 | 177.7355 | 226 | 0 | 0 | 0 | 45.4506 | 0 | 41.2941 | 226 | 115.1084 | 30.3004 | 145.4088
227 | 0 | 138.2865 | 139.2604 | 51.241 | 226.3059 | 51.241 | 277.5469 | 227 | 47.7985 | 92.191 | 130.451 | 227 | 111.4083 | 111.4083 | 55.7531 | 0 | 0 | 227 | 0 | 138.2865 | 107.8476 | 51.241 | 194.8931 | 51.241 | 246.1341 | 227 | 47.7985 | 92.191 | 130.451 | 130.451 | 227 | 86.2781 | 25.1302 | 111.4083 | 55.7531 | 0 | 0 | 227 | 6.9691 | 6.9691 | 227 | 0.9225 | 9.7568 | 10.733 | 227 | 21.0046 | 0 | 21.9178 | 227 | 14.003 | 176.9806 | 189.0689 | 227 | 0 | 0 | 0 | 30 | 0 | 51.241 | 227 | 110.451 | 20 | 130.451
228 | 0 | 144 | 152.6363 | 37.2578 | 259.3784 | 37.2578 | 296.6363 | 228 | 95.245 | 96 | 189.1957 | 228 | 122.109 | 122.109 | 55.06 | 0 | 0 | 228 | 0 | 144 | 129.6946 | 37.2578 | 236.4368 | 37.2578 | 273.6946 | 228 | 95.245 | 96 | 189.1957 | 189.1957 | 228 | 103.7557 | 18.3533 | 122.109 | 55.06 | 0 | 0 | 228 | 6.8825 | 6.8825 | 228 | 1.0135 | 9.6355 | 11.6615 | 228 | 16.5847 | 0 | 21.9178 | 228 | 11.0565 | 170.8378 | 187.5826 | 228 | 0 | 0 | 0 | 0 | 0 | 37.2578 | 228 | 189.1957 | 0 | 189.1957
229 | 0 | 144 | 155.1967 | 29.7085 | 269.4882 | 29.7085 | 299.1967 | 229 | 102.6818 | 96 | 198.6818 | 229 | 124.1574 | 124.1574 | 55.621 | 0 | 0 | 229 | 0 | 144 | 145.0469 | 29.7085 | 259.3384 | 29.7085 | 289.0469 | 229 | 102.6818 | 96 | 198.6818 | 198.6818 | 229 | 116.0375 | 8.1198 | 124.1574 | 55.621 | 0 | 0 | 229 | 6.9526 | 6.9526 | 229 | 1.4673 | 9.7337 | 10.6269 | 229 | 22.8311 | 0 | 21.9178 | 229 | 15.2207 | 162.9405 | 185.7883 | 229 | 0 | 0 | 0 | 6 | 0 | 29.7085 | 229 | 194.6818 | 4 | 198.6818
230 | 0 | 144 | 148.1231 | 37.2348 | 254.8883 | 37.2348 | 292.1231 | 230 | 84.7196 | 96 | 180.7196 | 230 | 118.4985 | 118.4985 | 53.5546 | 0 | 0 | 230 | 0 | 144 | 138.5831 | 37.2348 | 245.3482 | 37.2348 | 282.5831 | 230 | 84.7196 | 96 | 180.7196 | 180.7196 | 230 | 110.8665 | 7.632 | 118.4985 | 53.5546 | 0 | 0 | 230 | 6.6943 | 6.6943 | 230 | 1.6265 | 9.372 | 11.2555 | 230 | 35.4701 | 0 | 21.9178 | 230 | 23.6467 | 178.2347 | 183.6211 | 230 | 0 | 18 | 0 | 59.8531 | 0 | 37.2348 | 230 | 140.8175 | 39.9021 | 180.7196
231 | 0 | 144 | 138.0872 | 31.2264 | 250.8607 | 31.2264 | 282.0872 | 231 | 85.1287 | 96 | 181.1287 | 231 | 110.4697 | 110.4697 | 45.444 | 0 | 0 | 231 | 0 | 144 | 113.2982 | 31.2264 | 226.0717 | 31.2264 | 257.2982 | 231 | 85.1287 | 96 | 181.1287 | 181.1287 | 231 | 90.6385 | 19.8312 | 110.4697 | 45.444 | 0 | 0 | 231 | 5.6805 | 5.6805 | 231 | 2.5742 | 7.9527 | 10.5362 | 231 | 23.7443 | 0 | 21.9178 | 231 | 15.8295 | 167.9424 | 183.5508 | 231 | 0 | 18 | 0 | 66 | 0 | 31.2264 | 231 | 137.1287 | 44 | 181.1287
232 | 0 | 144 | 127.8836 | 36.1999 | 235.6837 | 36.1999 | 271.8836 | 232 | 47.5891 | 96 | 150.4459 | 232 | 102.3068 | 102.3068 | 44.789 | 0 | 0 | 232 | 0 | 144 | 123.1843 | 36.1999 | 230.9844 | 36.1999 | 267.1843 | 232 | 47.5891 | 96 | 150.4459 | 150.4459 | 232 | 98.5474 | 3.7594 | 102.3068 | 44.789 | 0 | 0 | 232 | 5.5986 | 5.5986 | 232 | 3.2854 | 7.8381 | 11.4312 | 232 | 19.1781 | 0 | 21.9178 | 232 | 12.7854 | 160.1354 | 178.9678 | 232 | 0 | 0 | 0 | 36.329 | 0 | 36.1999 | 232 | 130.2488 | 24.2194 | 150.4459
233 | 0 | 144 | 133.053 | 49.3034 | 227.7496 | 49.3034 | 277.053 | 233 | 18.9818 | 96 | 117.1296 | 233 | 106.4424 | 106.4424 | 54.646 | 0 | 0 | 233 | 0 | 144 | 126.9346 | 49.3034 | 221.6313 | 49.3034 | 270.9346 | 233 | 18.9818 | 96 | 117.1296 | 117.1296 | 233 | 101.5477 | 4.8947 | 106.4424 | 54.646 | 0 | 0 | 233 | 6.8308 | 6.8308 | 233 | 2.0687 | 9.5631 | 11.6317 | 233 | 13.6986 | 0 | 21.9178 | 233 | 9.1324 | 164.6848 | 178.7083 | 233 | 0 | 0 | 0 | 26.9611 | 0 | 49.3034 | 233 | 95.1333 | 17.9741 | 117.1296
234 | 0 | 144 | 139.6767 | 48.2397 | 235.437 | 48.2397 | 283.6767 | 234 | 42.7259 | 96 | 129.7734 | 234 | 111.7413 | 111.7413 | 55.1962 | 0 | 0 | 234 | 0 | 144 | 137.8144 | 48.2397 | 233.5747 | 48.2397 | 281.8144 | 234 | 42.7259 | 96 | 129.7734 | 129.7734 | 234 | 110.2516 | 1.4898 | 111.7413 | 55.1962 | 0 | 0 | 234 | 6.8995 | 6.8995 | 234 | 2.2343 | 9.6593 | 10.6991 | 234 | 16.5847 | 0 | 21.9178 | 234 | 11.0565 | 155.0333 | 171.2446 | 234 | 0 | 0 | 0 | 40.0024 | 0 | 48.2397 | 234 | 103.1052 | 26.6683 | 129.7734
235 | 0 | 144 | 139.691 | 42.9902 | 240.7008 | 42.9902 | 283.691 | 235 | 43.2851 | 96 | 146.1759 | 235 | 111.7528 | 111.7528 | 55.0958 | 0 | 0 | 235 | 0 | 144 | 117.8885 | 42.9902 | 218.8983 | 42.9902 | 261.8885 | 235 | 43.2851 | 96 | 146.1759 | 146.1759 | 235 | 94.3108 | 17.442 | 111.7528 | 55.0958 | 0 | 0 | 235 | 6.887 | 6.887 | 235 | 0.032306 | 9.6418 | 9.6857 | 235 | 27.2509 | 0 | 21.9178 | 235 | 18.1673 | 153.967 | 169.8503 | 235 | 0 | 0 | 0 | 36 | 0 | 42.9902 | 235 | 122.1759 | 24 | 146.1759
236 | 0 | 144 | 137.5491 | 49.2574 | 232.2917 | 49.2574 | 281.5491 | 236 | 30.3786 | 96 | 127.5234 | 236 | 110.0393 | 110.0393 | 55.9635 | 0 | 0 | 236 | 0 | 144 | 131.3126 | 49.2574 | 226.0552 | 49.2574 | 275.3126 | 236 | 30.3786 | 96 | 127.5234 | 127.5234 | 236 | 105.05 | 4.9892 | 110.0393 | 55.9635 | 0 | 0 | 236 | 6.9954 | 6.9954 | 236 | 0.71733 | 9.7936 | 9.0875 | 236 | 21.0046 | 0 | 21.9178 | 236 | 14.003 | 155.6714 | 174.3469 | 236 | 0 | 0 | 0 | 24 | 0 | 49.2574 | 236 | 111.5234 | 16 | 127.5234
237 | 0 | 118.4095 | 129.8954 | 52.6094 | 195.6955 | 52.6094 | 248.3049 | 237 | 54.6771 | 78.9396 | 125.529 | 237 | 103.9163 | 103.9163 | 53.5111 | 0 | 0 | 237 | 0 | 118.4095 | 119.6838 | 52.6094 | 185.4839 | 52.6094 | 238.0933 | 237 | 54.6771 | 78.9396 | 125.529 | 125.529 | 237 | 95.7471 | 8.1693 | 103.9163 | 53.5111 | 0 | 0 | 237 | 6.6889 | 6.6889 | 237 | 0.47203 | 9.3644 | 12.4428 | 237 | 19.3244 | 0 | 21.9178 | 237 | 12.883 | 164.712 | 177.595 | 237 | 0 | 0 | 0 | 25.5265 | 0 | 52.6094 | 237 | 108.5113 | 17.0177 | 125.529
238 | 0 | 144 | 137.1838 | 36.2516 | 244.9322 | 36.2516 | 281.1838 | 238 | 81.842 | 96 | 178.0732 | 238 | 109.747 | 109.747 | 45.3786 | 0 | 0 | 238 | 0 | 144 | 121.7608 | 36.2516 | 229.5092 | 36.2516 | 265.7608 | 238 | 81.842 | 96 | 178.0732 | 178.0732 | 238 | 97.4086 | 12.3384 | 109.747 | 45.3786 | 0 | 0 | 238 | 5.6723 | 5.6723 | 238 | 4.0313 | 7.9413 | 11.9726 | 238 | 35.4701 | 0 | 21.9178 | 238 | 23.6467 | 160.3322 | 171.0825 | 238 | 0 | 0 | 0 | 90 | 0 | 36.2516 | 238 | 118.0732 | 60 | 178.0732
239 | 0 | 144 | 133.795 | 40.4891 | 237.3059 | 40.4891 | 277.795 | 239 | 72.0001 | 96 | 167.7689 | 239 | 107.036 | 107.036 | 44.636 | 0 | 0 | 239 | 0 | 144 | 103.3828 | 40.4891 | 206.8936 | 40.4891 | 247.3828 | 239 | 72.0001 | 96 | 167.7689 | 167.7689 | 239 | 82.7062 | 24.3298 | 107.036 | 44.636 | 0 | 0 | 239 | 5.5795 | 5.5795 | 239 | 3.4333 | 7.8113 | 11.2446 | 239 | 11.8721 | 0 | 21.9178 | 239 | 7.9148 | 148.5846 | 166.5427 | 239 | 0 | 0 | 0 | 24 | 0 | 40.4891 | 239 | 151.7689 | 16 | 167.7689
240 | 0 | 144 | 138.0346 | 40.1729 | 241.8617 | 40.1729 | 282.0346 | 240 | 39.004 | 96 | 143.7469 | 240 | 110.4277 | 110.4277 | 54.6269 | 0 | 0 | 240 | 0 | 144 | 104.0016 | 40.1729 | 207.8287 | 40.1729 | 248.0016 | 240 | 39.004 | 96 | 143.7469 | 143.7469 | 240 | 83.2013 | 27.2264 | 110.4277 | 54.6269 | 0 | 0 | 240 | 6.8284 | 6.8284 | 240 | 2.8143 | 9.5597 | 12.374 | 240 | 28.3105 | 0 | 21.9178 | 240 | 18.8737 | 173.6557 | 176.3303 | 240 | 0 | 0 | 0 | 44.4489 | 0 | 40.1729 | 240 | 114.2582 | 29.6326 | 143.7469
241 | 0 | 144 | 142.3694 | 47.8602 | 238.5092 | 47.8602 | 286.3694 | 241 | 50.9029 | 96 | 138.1601 | 241 | 113.8956 | 113.8956 | 55.715 | 0 | 0 | 241 | 0 | 144 | 120.0963 | 47.8602 | 216.2361 | 47.8602 | 264.0963 | 241 | 50.9029 | 96 | 138.1601 | 138.1601 | 241 | 96.077 | 17.8185 | 113.8956 | 55.715 | 0 | 0 | 241 | 6.9644 | 6.9644 | 241 | 2.163 | 9.7501 | 11.9131 | 241 | 10.192 | 0 | 21.9178 | 241 | 6.7947 | 161.1841 | 184.5398 | 241 | 0 | 0 | 0 | 42 | 0 | 47.8602 | 241 | 110.0161 | 28 | 138.1601
242 | 0 | 144 | 157.7353 | 34.6877 | 267.0476 | 34.6877 | 301.7353 | 242 | 109.6749 | 96 | 205.6749 | 242 | 126.1883 | 126.1883 | 56.2533 | 0 | 0 | 242 | 0 | 144 | 136.6571 | 34.6877 | 245.9693 | 34.6877 | 280.6571 | 242 | 109.6749 | 96 | 205.6749 | 205.6749 | 242 | 109.3257 | 16.8626 | 126.1883 | 56.2533 | 0 | 0 | 242 | 7.0317 | 7.0317 | 242 | 2.6527 | 9.8443 | 12.497 | 242 | 27.2509 | 0 | 21.9178 | 242 | 18.1673 | 144.2354 | 163.4351 | 242 | 0 | 0 | 0 | 36 | 0 | 34.6877 | 242 | 181.6749 | 24 | 205.6749
243 | 0 | 144 | 157.1806 | 27.3224 | 273.8582 | 27.3224 | 301.1806 | 243 | 111.0044 | 96 | 207.0044 | 243 | 125.7445 | 125.7445 | 55.5436 | 0 | 0 | 243 | 0 | 144 | 136.0362 | 27.3224 | 252.7138 | 27.3224 | 280.0362 | 243 | 111.0044 | 96 | 207.0044 | 207.0044 | 243 | 108.829 | 16.9156 | 125.7445 | 55.5436 | 0 | 0 | 243 | 6.943 | 6.943 | 243 | 4.486 | 9.7201 | 14.2061 | 243 | 21.9178 | 0 | 21.9178 | 243 | 14.6119 | 143.8246 | 159.8951 | 243 | 0 | 0 | 0 | 24 | 0 | 27.3224 | 243 | 191.0044 | 16 | 207.0044
244 | 0 | 144 | 135.7628 | 38.7872 | 240.9756 | 38.7872 | 279.7628 | 244 | 40.5832 | 96 | 145.281 | 244 | 108.6103 | 108.6103 | 52.4936 | 0 | 0 | 244 | 0 | 144 | 107.0216 | 38.7872 | 212.2343 | 38.7872 | 251.0216 | 244 | 40.5832 | 96 | 145.281 | 145.281 | 244 | 85.6172 | 22.993 | 108.6103 | 52.4936 | 0 | 0 | 244 | 6.5617 | 6.5617 | 244 | 5.3252 | 9.1864 | 14.5116 | 244 | 31.9635 | 0 | 21.9178 | 244 | 21.309 | 148.4332 | 169.7422 | 244 | 0 | 0 | 0 | 30 | 0 | 38.7872 | 244 | 129.1498 | 20 | 145.281
245 | 0 | 144 | 119.9654 | 51.2065 | 212.7589 | 51.2065 | 263.9654 | 245 | 18.419 | 96 | 115.4548 | 245 | 95.9723 | 95.9723 | 44.2885 | 0 | 0 | 245 | 0 | 144 | 91.3755 | 51.2065 | 184.169 | 51.2065 | 235.3755 | 245 | 18.419 | 96 | 115.4548 | 115.4548 | 245 | 73.1004 | 22.8719 | 95.9723 | 44.2885 | 0 | 0 | 245 | 5.5361 | 5.5361 | 245 | 6.427 | 7.7505 | 14.1775 | 245 | 7.4523 | 0 | 21.9178 | 245 | 4.9682 | 179.7619 | 171.8824 | 245 | 0 | 0 | 0 | 96 | 0 | 51.2065 | 245 | 47.586 | 64 | 115.4548
246 | 0 | 132.1657 | 112.9088 | 57.9221 | 188.7212 | 57.9221 | 246.6433 | 246 | 11.0074 | 88.1104 | 97.2497 | 246 | 90.327 | 90.327 | 44.0703 | 0 | 0 | 246 | 0 | 132.6596 | 53.4626 | 57.9221 | 131.4204 | 57.9221 | 189.3425 | 246 | 11.0074 | 88.4397 | 97.2497 | 97.2497 | 246 | 42.7701 | 47.7216 | 90.4917 | 44.0703 | 0 | 0 | 246 | 5.5088 | 5.5088 | 246 | 6.0555 | 7.7123 | 13.7678 | 246 | 26.3377 | 0 | 21.9178 | 246 | 17.5584 | 166.4134 | 187.9339 | 246 | 0 | 0 | 0 | 36 | 0 | 57.9221 | 246 | 73.2497 | 24 | 97.2497
247 | 0 | 107.845 | 118.1639 | 67.8575 | 156.5825 | 67.8575 | 224.4401 | 247 | 22.5996 | 71.8967 | 96.1758 | 247 | 94.5311 | 94.5311 | 54.0629 | 0 | 0 | 247 | 0 | 107.3511 | 80.7067 | 67.8575 | 116.9798 | 67.8575 | 184.8374 | 247 | 22.5996 | 71.5674 | 96.1758 | 96.1758 | 247 | 64.5653 | 29.8012 | 94.3665 | 54.0629 | 0 | 0 | 247 | 6.7579 | 6.7579 | 247 | 3.2862 | 9.461 | 12.7472 | 247 | 17.498 | 0 | 21.9178 | 247 | 11.6653 | 157.2115 | 177.7625 | 247 | 0 | 0 | 0 | 20.7971 | 0 | 67.8575 | 247 | 82.3111 | 13.8648 | 96.1758
248 | 0 | 136.8325 | 127.0504 | 62.3206 | 201.5623 | 62.3206 | 263.8829 | 248 | 4.8276 | 91.2217 | 86.5236 | 248 | 101.6403 | 101.6403 | 55.064 | 0 | 0 | 248 | 0 | 136.8325 | 116.1921 | 62.3206 | 190.704 | 62.3206 | 253.0246 | 248 | 4.8276 | 91.2217 | 86.5236 | 86.5236 | 248 | 92.9537 | 8.6866 | 101.6403 | 55.064 | 0 | 0 | 248 | 6.883 | 6.883 | 248 | 2.5141 | 9.6362 | 12.0166 | 248 | 21.0046 | 0 | 21.9178 | 248 | 14.003 | 160.7596 | 172.6877 | 248 | 0 | 0 | 0 | 65.2662 | 0 | 62.3206 | 248 | 43.0127 | 43.5108 | 86.5236
249 | 0 | 144 | 142.0385 | 41.9496 | 244.089 | 41.9496 | 286.0385 | 249 | 42.9849 | 96 | 138.9655 | 249 | 113.6308 | 113.6308 | 57.0338 | 0 | 0 | 249 | 0 | 144 | 128.8985 | 41.9496 | 230.9489 | 41.9496 | 272.8985 | 249 | 42.9849 | 96 | 138.9655 | 138.9655 | 249 | 103.1188 | 10.5121 | 113.6308 | 57.0338 | 0 | 0 | 249 | 7.1292 | 7.1292 | 249 | 2.1029 | 9.9809 | 11.6333 | 249 | 27.2509 | 0 | 21.9178 | 249 | 18.1673 | 145.3925 | 165.6347 | 249 | 0 | 0 | 0 | 36 | 0 | 41.9496 | 249 | 114.9655 | 24 | 138.9655
250 | 0 | 144 | 139.0318 | 38.9425 | 244.0893 | 38.9425 | 283.0318 | 250 | 33.7077 | 96 | 141.1644 | 250 | 111.2254 | 111.2254 | 56.4839 | 0 | 0 | 250 | 0 | 144 | 132.8174 | 38.9425 | 237.8749 | 38.9425 | 276.8174 | 250 | 33.7077 | 96 | 141.1644 | 141.1644 | 250 | 106.2539 | 4.9715 | 111.2254 | 56.4839 | 0 | 0 | 250 | 7.0605 | 7.0605 | 250 | 0.59948 | 9.8847 | 10.7593 | 250 | 21.9178 | 0 | 21.9178 | 250 | 14.6119 | 160.5126 | 172.0986 | 250 | 0 | 0 | 0 | 78.019 | 0 | 38.9425 | 250 | 91.9718 | 52.0126 | 141.1644
251 | 0 | 96.8808 | 107.2718 | 77.3387 | 126.8139 | 77.3387 | 204.1526 | 251 | 0 | 64.5872 | 53.1305 | 251 | 85.8174 | 85.8174 | 53.5238 | 0 | 0 | 251 | 0 | 96.8808 | 101.0949 | 77.3387 | 120.637 | 77.3387 | 197.9757 | 251 | 0 | 64.5872 | 53.1305 | 53.1305 | 251 | 80.8759 | 4.9415 | 85.8174 | 53.5238 | 0 | 0 | 251 | 6.6905 | 6.6905 | 251 | 2.1942 | 9.3667 | 11.8699 | 251 | 19.3244 | 0 | 21.9178 | 251 | 12.883 | 166.3362 | 174.9306 | 251 | 0 | 0 | 0 | 42 | 0 | 77.3387 | 251 | 22.3105 | 28 | 53.1305
252 | 0 | 112.8405 | 103.6314 | 67.2308 | 149.2411 | 67.2308 | 216.4719 | 252 | 0 | 75.227 | 75.6056 | 252 | 82.9051 | 82.9051 | 45.2917 | 0 | 0 | 252 | 0 | 112.8405 | 96.0811 | 67.2308 | 141.6908 | 67.2308 | 208.9216 | 252 | 0 | 75.227 | 75.6056 | 75.6056 | 252 | 76.8649 | 6.0402 | 82.9051 | 45.2917 | 0 | 0 | 252 | 5.6615 | 5.6615 | 252 | 4.9652 | 7.926 | 12.8913 | 252 | 19.1781 | 0 | 21.9178 | 252 | 12.7854 | 163.0566 | 176.5735 | 252 | 0 | 0 | 0 | 96.239 | 0 | 67.2308 | 252 | 12.2967 | 64.1593 | 75.6056
253 | 0 | 118.8292 | 106.7604 | 62.4701 | 164.2724 | 62.4701 | 226.7426 | 253 | 0 | 79.2195 | 86.1912 | 253 | 85.4083 | 85.4083 | 45.7985 | 0 | 0 | 253 | 0 | 118.8292 | 102.4456 | 62.4701 | 160.2672 | 62.4701 | 222.7373 | 253 | 0 | 79.2195 | 86.1912 | 86.1912 | 253 | 81.9565 | 3.4518 | 85.4083 | 45.7985 | 0 | 0 | 253 | 5.7248 | 5.7248 | 253 | 8.3334 | 8.0147 | 16.3482 | 253 | 27.2509 | 0 | 21.9178 | 253 | 18.1673 | 165.2128 | 183.5454 | 253 | 0 | 36 | 0 | 67.7168 | 0 | 62.4701 | 253 | 41.2524 | 45.1445 | 86.1912
254 | 0 | 108.1077 | 117.8581 | 64.0973 | 160.7156 | 64.0973 | 224.8129 | 254 | 7.8591 | 72.0718 | 83.6343 | 254 | 94.2865 | 94.2865 | 56.6788 | 0 | 0 | 254 | 0 | 108.1077 | 110.337 | 64.0973 | 152.8849 | 64.0973 | 216.9822 | 254 | 7.8591 | 72.0718 | 83.6343 | 83.6343 | 254 | 88.2696 | 6.0169 | 94.2865 | 56.6788 | 0 | 0 | 254 | 7.0849 | 7.0849 | 254 | 7.0968 | 9.9188 | 17.0156 | 254 | 21.0046 | 0 | 21.9178 | 254 | 14.003 | 157.5095 | 177.9301 | 254 | 6 | 0 | 0 | 33.2382 | 0 | 64.0973 | 254 | 60.6015 | 22.1588 | 83.6343
255 | 0 | 134.6423 | 126.6933 | 60.866 | 200.8753 | 60.866 | 261.7413 | 255 | 0 | 89.7615 | 89.758 | 255 | 101.3547 | 101.3547 | 56.4739 | 0 | 0 | 255 | 0 | 134.6423 | 100.4603 | 60.866 | 174.9016 | 60.866 | 235.7676 | 255 | 0 | 89.7615 | 89.758 | 89.758 | 255 | 80.3682 | 20.9864 | 101.3547 | 56.4739 | 0 | 0 | 255 | 7.0592 | 7.0592 | 255 | 6.8347 | 9.8829 | 16.7176 | 255 | 30.2694 | 0 | 21.9178 | 255 | 20.1796 | 180.1325 | 184.2156 | 255 | 0 | 0 | 0 | 96 | 0 | 60.866 | 255 | 31.0327 | 64 | 89.758
256 | 0 | 138 | 128.1269 | 59.8023 | 206.5231 | 59.8023 | 266.3253 | 256 | 0 | 92 | 92.1232 | 256 | 102.5015 | 102.5015 | 56.5015 | 0 | 0 | 256 | 0 | 138 | 114.9289 | 59.8023 | 193.1461 | 59.8023 | 252.9484 | 256 | 0 | 92 | 92.1232 | 92.1232 | 256 | 91.9431 | 10.5584 | 102.5015 | 56.5015 | 0 | 0 | 256 | 7.0627 | 7.0627 | 256 | 7.2583 | 9.8878 | 17.1461 | 256 | 14.4795 | 0 | 21.9178 | 256 | 9.653 | 166.0421 | 182.2483 | 256 | 0 | 0 | 0 | 64.4856 | 0 | 59.8023 | 256 | 46.086 | 42.9904 | 92.1232
257 | 0 | 83.9216 | 105.2988 | 79.8629 | 109.3229 | 79.8629 | 189.1858 | 257 | 0 | 55.9477 | 47.5181 | 257 | 84.2391 | 84.2391 | 56.2652 | 0 | 0 | 257 | 0 | 83.9216 | 100.4822 | 79.8629 | 104.4283 | 79.8629 | 184.2912 | 257 | 0 | 55.9477 | 47.5181 | 47.5181 | 257 | 80.3857 | 3.8534 | 84.2391 | 56.2652 | 0 | 0 | 257 | 7.0332 | 7.0332 | 257 | 7.694 | 9.8464 | 17.5404 | 257 | 21.9178 | 0 | 21.9178 | 257 | 14.6119 | 169.3158 | 185.2154 | 257 | 9.0876 | 0 | 0 | 69.5463 | 0 | 79.8629 | 257 | 0 | 46.3642 | 47.5181
258 | 0 | 58.5174 | 92.2152 | 84.9226 | 65.2406 | 84.9226 | 150.1632 | 258 | 0 | 39.0116 | 36.2678 | 258 | 73.7721 | 73.7721 | 54.2664 | 0 | 0 | 258 | 0 | 58.5174 | 87.9515 | 84.9226 | 60.9745 | 84.9226 | 145.897 | 258 | 0 | 39.0116 | 36.2678 | 36.2678 | 258 | 70.3612 | 3.4109 | 73.7721 | 54.2664 | 0 | 0 | 258 | 6.7833 | 6.7833 | 258 | 7.5957 | 9.4966 | 17.0923 | 258 | 18.4112 | 0 | 21.9178 | 258 | 12.2741 | 164.583 | 185.1127 | 258 | 27.69 | 0 | 0 | 52.5174 | 0 | 84.9226 | 258 | 0 | 35.0116 | 36.2678
259 | 0 | 55.7117 | 81.252 | 81.4038 | 58.7579 | 81.4038 | 140.1616 | 259 | 0 | 37.1411 | 44.0919 | 259 | 65.0016 | 65.0016 | 46.431 | 0 | 0 | 259 | 0 | 55.7117 | 80.6119 | 81.4038 | 58.1203 | 81.4038 | 139.5241 | 259 | 0 | 37.1411 | 44.0919 | 44.0919 | 259 | 64.4896 | 0.51203 | 65.0016 | 46.431 | 0 | 0 | 259 | 5.8039 | 5.8039 | 259 | 10.0707 | 8.1254 | 18.1961 | 259 | 35.4701 | 0 | 21.9178 | 259 | 23.6467 | 178.5132 | 184.4318 | 259 | 28.4046 | 0 | 0 | 68.5673 | 0 | 81.4038 | 259 | 0 | 45.7115 | 44.0919
260 | 0 | 51.2657 | 77.9902 | 89.367 | 43.1885 | 89.367 | 132.5556 | 260 | 0 | 34.1771 | 31.7549 | 260 | 62.3921 | 62.3921 | 45.3036 | 0 | 0 | 260 | 0 | 51.2657 | 77.3142 | 89.367 | 42.6302 | 89.367 | 131.9972 | 260 | 0 | 34.1771 | 31.7549 | 31.7549 | 260 | 61.8514 | 0.54076 | 62.3921 | 45.3036 | 0 | 0 | 260 | 5.6629 | 5.6629 | 260 | 9.8647 | 7.9281 | 17.7928 | 260 | 9 | 0 | 21.9178 | 260 | 6 | 162.3455 | 181.6268 | 260 | 16.3561 | 0 | 0 | 45.2029 | 0 | 89.367 | 260 | 0 | 30.1352 | 31.7549
261 | 0 | 62.4443 | 95.1797 | 89.9995 | 67.7293 | 89.9995 | 157.7289 | 261 | 0 | 41.6295 | 44.0919 | 261 | 76.1438 | 76.1438 | 55.329 | 0 | 0 | 261 | 0 | 62.4443 | 93.107 | 89.9995 | 65.5366 | 89.9995 | 155.5361 | 261 | 0 | 41.6295 | 44.0919 | 44.0919 | 261 | 74.4856 | 1.6582 | 76.1438 | 55.329 | 0 | 0 | 261 | 6.9161 | 6.9161 | 261 | 8.6331 | 9.6826 | 18.3157 | 261 | 20.3701 | 0 | 21.9178 | 261 | 13.5801 | 195.3066 | 198.7106 | 261 | 0 | 0 | 0 | 66.1378 | 0 | 89.9995 | 261 | 0 | 44.0919 | 44.0919
262 | 0 | 60.687 | 95.9922 | 95.4444 | 57.7118 | 95.4444 | 153.1563 | 262 | 0 | 40.458 | 41.8674 | 262 | 76.7938 | 76.7938 | 56.5648 | 0 | 0 | 262 | 0 | 60.687 | 94.855 | 95.4444 | 56.9363 | 95.4444 | 152.3807 | 262 | 0 | 40.458 | 41.8674 | 41.8674 | 262 | 75.884 | 0.9098 | 76.7938 | 56.5648 | 0 | 0 | 262 | 7.0706 | 7.0706 | 262 | 7.8255 | 9.8988 | 17.7243 | 262 | 26.3377 | 0 | 21.9178 | 262 | 17.5584 | 173.4352 | 201.6507 | 262 | 6 | 0 | 0 | 62.8011 | 0 | 95.4444 | 262 | 0 | 41.8674 | 41.8674
263 | 0 | 71.143 | 100.2822 | 84.9513 | 87.2844 | 84.9513 | 172.2357 | 263 | 0 | 47.4286 | 44.6672 | 263 | 80.2258 | 80.2258 | 56.5114 | 0 | 0 | 263 | 0 | 71.143 | 87.5777 | 84.9513 | 78.0213 | 84.9513 | 162.9726 | 263 | 0 | 47.4286 | 44.6672 | 44.6672 | 263 | 70.0621 | 10.1636 | 80.2258 | 56.5114 | 0 | 0 | 263 | 7.0639 | 7.0639 | 263 | 5.6875 | 9.8895 | 15.577 | 263 | 21.0046 | 0 | 21.9178 | 263 | 14.003 | 170.8958 | 185.5343 | 263 | 11.0876 | 0 | 0 | 67.0008 | 0 | 84.9513 | 263 | 0 | 44.6672 | 44.6672
264 | 0 | 78.9142 | 103.6257 | 79.4949 | 101.8285 | 79.4949 | 181.3234 | 264 | 0 | 52.6094 | 50.0367 | 264 | 82.9005 | 82.9005 | 56.5958 | 0 | 0 | 264 | 0 | 78.9142 | 67.2943 | 79.4949 | 64.9558 | 79.4949 | 144.4507 | 264 | 0 | 52.6094 | 50.0367 | 50.0367 | 264 | 53.8354 | 29.0651 | 82.9005 | 56.5958 | 0 | 0 | 264 | 7.0745 | 7.0745 | 264 | 5.4639 | 9.9043 | 15.3682 | 264 | 22.8311 | 0 | 21.9178 | 264 | 15.2207 | 152.0287 | 170.5799 | 264 | 0 | 0 | 0 | 75.055 | 0 | 79.4949 | 264 | 0 | 50.0367 | 50.0367
265 | 0 | 85.7335 | 102.8976 | 76.712 | 111.2358 | 76.712 | 187.9479 | 265 | 0 | 57.1556 | 55.8536 | 265 | 82.3181 | 82.3181 | 53.7403 | 0 | 0 | 265 | 0 | 85.7335 | 83.1197 | 76.712 | 88.539 | 76.712 | 165.251 | 265 | 0 | 57.1556 | 55.8536 | 55.8536 | 265 | 66.4957 | 15.8224 | 82.3181 | 53.7403 | 0 | 0 | 265 | 6.7175 | 6.7175 | 265 | 7.3435 | 9.4045 | 16.7481 | 265 | 28.3105 | 0 | 21.9178 | 265 | 18.8737 | 140.054 | 158.9277 | 265 | 3.7085 | 0 | 0 | 83.7804 | 0 | 76.712 | 265 | 0 | 55.8536 | 55.8536
266 | 0 | 36.1214 | 73.1684 | 101.9186 | 9.4735 | 101.9186 | 111.3921 | 266 | 0 | 24.0809 | 23.2276 | 266 | 58.5347 | 58.5347 | 46.4942 | 0 | 0 | 266 | 0 | 36.1214 | 52.2109 | 101.9186 | 0 | 101.9186 | 101.9186 | 266 | 0 | 24.0809 | 23.2276 | 23.2276 | 266 | 41.7687 | 16.766 | 58.5347 | 46.4942 | 0 | 0 | 266 | 5.8118 | 5.8118 | 266 | 8.5074 | 8.1365 | 16.6439 | 266 | 10.192 | 0 | 21.9178 | 266 | 6.7947 | 148.1769 | 154.9715 | 266 | 63.1958 | 0 | 0 | 34.8414 | 0 | 101.9186 | 266 | 0 | 23.2276 | 23.2276
267 | 0 | 84.7822 | 92.5256 | 78.9487 | 94.2662 | 78.9487 | 173.2148 | 267 | 0 | 56.5214 | 55.6107 | 267 | 74.0205 | 74.0205 | 45.7598 | 0 | 0 | 267 | 0 | 84.7822 | 87.377 | 78.9487 | 77.2907 | 78.9487 | 156.2393 | 267 | 0 | 56.5214 | 55.6107 | 55.6107 | 267 | 69.9016 | 4.1189 | 74.0205 | 45.7598 | 0 | 0 | 267 | 5.72 | 5.72 | 267 | 9.9349 | 8.008 | 17.9429 | 267 | 25.4244 | 0 | 21.9178 | 267 | 16.9496 | 134.1854 | 151.0154 | 267 | 0 | 0 | 0 | 71.1857 | 0 | 78.9487 | 267 | 11.1679 | 47.4571 | 55.6107
268 | 0 | 132.8226 | 129.867 | 50.804 | 211.8856 | 50.804 | 262.6896 | 268 | 17.1211 | 88.5484 | 117.2574 | 268 | 103.8936 | 103.8936 | 56.1952 | 0 | 0 | 268 | 0 | 132.8226 | 125.1739 | 50.804 | 207.1925 | 50.804 | 257.9965 | 268 | 17.1211 | 88.5484 | 117.2574 | 117.2574 | 268 | 100.1391 | 3.7545 | 103.8936 | 56.1952 | 0 | 0 | 268 | 7.0244 | 7.0244 | 268 | 7.4459 | 9.8342 | 17.28 | 268 | 31.8311 | 0 | 21.9178 | 268 | 21.2207 | 144.4212 | 152.8854 | 268 | 0 | 0 | 0 | 53.7085 | 0 | 50.804 | 268 | 83.3575 | 35.8057 | 117.2574
269 | 0 | 142.6155 | 132.752 | 56.226 | 219.1415 | 56.226 | 275.3675 | 269 | 7.9263 | 95.077 | 101.3791 | 269 | 106.2016 | 106.2016 | 57.0779 | 0 | 0 | 269 | 0 | 142.6155 | 118.2311 | 56.226 | 204.6206 | 56.226 | 260.8466 | 269 | 7.9263 | 95.077 | 101.3791 | 101.3791 | 269 | 94.5849 | 11.6167 | 106.2016 | 57.0779 | 0 | 0 | 269 | 7.1347 | 7.1347 | 269 | 6.6033 | 9.9886 | 16.592 | 269 | 8.498 | 0 | 21.9178 | 269 | 5.6653 | 133.5332 | 152.0747 | 269 | 0 | 0 | 0 | 54 | 0 | 56.226 | 269 | 61.9649 | 36 | 101.3791
270 | 0 | 142.6291 | 132.3551 | 60.82 | 214.1643 | 60.82 | 274.9843 | 270 | 0 | 95.0861 | 89.8603 | 270 | 105.8841 | 105.8841 | 58.3411 | 0 | 0 | 270 | 0 | 142.6291 | 112.8186 | 60.82 | 194.6277 | 60.82 | 255.4477 | 270 | 0 | 95.0861 | 89.8603 | 89.8603 | 270 | 90.2548 | 15.6293 | 105.8841 | 58.3411 | 0 | 0 | 270 | 7.2926 | 7.2926 | 270 | 5.3026 | 10.2097 | 15.5123 | 270 | 40.1826 | 0 | 21.9178 | 270 | 26.7884 | 131.7662 | 148.4753 | 270 | 0 | 0 | 0 | 57.9522 | 0 | 60.82 | 270 | 50.439 | 38.6348 | 89.8603
271 | 0 | 144 | 136.63 | 51.7757 | 228.8542 | 51.7757 | 280.63 | 271 | 10.6877 | 96 | 112.1053 | 271 | 109.304 | 109.304 | 59.1664 | 0 | 0 | 271 | 0 | 144 | 123.7966 | 51.7757 | 216.0208 | 51.7757 | 267.7966 | 271 | 10.6877 | 96 | 112.1053 | 112.1053 | 271 | 99.0372 | 10.2667 | 109.304 | 59.1664 | 0 | 0 | 271 | 7.3958 | 7.3958 | 271 | 4.3696 | 10.3541 | 14.7237 | 271 | 3.653 | 0 | 21.9178 | 271 | 2.4353 | 136.5551 | 149.0698 | 271 | 0 | 0 | 0 | 58.2574 | 0 | 51.7757 | 271 | 73.9802 | 38.8383 | 112.1053
272 | 0 | 139.1084 | 129.469 | 63.9363 | 204.6411 | 63.9363 | 268.5774 | 272 | 0 | 92.7389 | 82.9311 | 272 | 103.5752 | 103.5752 | 57.2058 | 0 | 0 | 272 | 0 | 139.1084 | 121.2503 | 63.9363 | 196.4224 | 63.9363 | 260.3587 | 272 | 0 | 92.7389 | 82.9311 | 82.9311 | 272 | 97.0002 | 6.575 | 103.5752 | 57.2058 | 0 | 0 | 272 | 7.1507 | 7.1507 | 272 | 5.3372 | 10.011 | 15.3482 | 272 | 22.8311 | 0 | 21.9178 | 272 | 15.2207 | 112.8632 | 128.0839 | 272 | 0 | 0 | 0 | 77.3994 | 0 | 63.9363 | 272 | 31.0658 | 51.5996 | 82.9311
273 | 0 | 118.0986 | 111.0954 | 65.023 | 164.9707 | 65.023 | 229.9937 | 273 | 0 | 78.7324 | 80.5149 | 273 | 88.8763 | 88.8763 | 49.5101 | 0 | 0 | 273 | 0 | 118.0986 | 88.4509 | 65.023 | 144.6011 | 65.023 | 209.624 | 273 | 0 | 78.7324 | 80.5149 | 80.5149 | 273 | 70.7607 | 18.1156 | 88.8763 | 49.5101 | 0 | 0 | 273 | 6.1888 | 6.1888 | 273 | 6.5737 | 8.6643 | 15.238 | 273 | 21.0046 | 0 | 21.9178 | 273 | 14.003 | 103.7419 | 117.745 | 273 | 6 | 12 | 0 | 81.2404 | 0 | 65.023 | 273 | 27.0577 | 54.1603 | 80.5149
274 | 0 | 81.6326 | 95.2613 | 75.9358 | 100.1584 | 75.9358 | 176.0942 | 274 | 0 | 54.4217 | 56.2499 | 274 | 76.209 | 76.209 | 48.9982 | 0 | 0 | 274 | 0 | 81.6326 | 65.2141 | 75.9358 | 69.2839 | 75.9358 | 145.2197 | 274 | 0 | 54.4217 | 56.2499 | 56.2499 | 274 | 52.1712 | 24.0378 | 76.209 | 48.9982 | 0 | 0 | 274 | 6.1248 | 6.1248 | 274 | 7.8281 | 8.5747 | 16.4027 | 274 | 27.2509 | 0 | 21.9178 | 274 | 18.1673 | 107.1971 | 119.0421 | 274 | 0 | 12 | 0 | 86.1052 | 0 | 75.9358 | 274 | 0 | 57.4034 | 56.2499
275 | 0 | 61.9944 | 101.3314 | 82.4674 | 86.9633 | 82.4674 | 169.4308 | 275 | 0 | 41.3296 | 44.4243 | 275 | 81.0651 | 81.0651 | 60.4003 | 0 | 0 | 275 | 0 | 61.9944 | 73.6849 | 82.4674 | 68.1218 | 82.4674 | 150.5892 | 275 | 0 | 41.3296 | 44.4243 | 44.4243 | 275 | 58.9479 | 22.1172 | 81.0651 | 60.4003 | 0 | 0 | 275 | 7.55 | 7.55 | 275 | 7.956 | 10.5701 | 18.526 | 275 | 17.498 | 0 | 21.9178 | 275 | 11.6653 | 106.0862 | 124.0737 | 275 | 6 | 0 | 0 | 62.1014 | 0 | 82.4674 | 275 | 0 | 41.4009 | 44.4243
276 | 0 | 53.1552 | 97.5213 | 86.4635 | 59.5728 | 86.4635 | 146.0363 | 276 | 0 | 35.4368 | 33.1739 | 276 | 78.017 | 78.017 | 60.2986 | 0 | 0 | 276 | 0 | 52.3683 | 70.2596 | 86.4635 | 28.3432 | 86.4635 | 114.8066 | 276 | 0 | 34.9122 | 33.1739 | 33.1739 | 276 | 56.2076 | 21.5471 | 77.7547 | 60.2986 | 0 | 0 | 276 | 7.5373 | 7.5373 | 276 | 7.7552 | 10.5523 | 18.3074 | 276 | 21.0046 | 0 | 21.9178 | 276 | 14.003 | 104.304 | 118.3071 | 276 | 6 | 30 | 0 | 53.352 | 0 | 86.4635 | 276 | 0 | 35.568 | 33.1739
277 | 0 | 58.1603 | 103.0027 | 82.8929 | 78.9721 | 82.8929 | 161.865 | 277 | 0 | 38.7735 | 41.5094 | 277 | 82.4022 | 82.4022 | 63.0154 | 0 | 0 | 277 | 0 | 58.9472 | 67.7396 | 82.8929 | 37.6509 | 82.8929 | 120.5439 | 277 | 0 | 39.2981 | 41.5094 | 41.5094 | 277 | 54.1917 | 28.4728 | 82.6645 | 63.0154 | 0 | 0 | 277 | 7.8769 | 7.8769 | 277 | 8.0201 | 11.0277 | 19.0478 | 277 | 26.3377 | 0 | 21.9178 | 277 | 17.5584 | 115.7566 | 128.8568 | 277 | 6 | 24 | 0 | 62.444 | 0 | 82.8929 | 277 | 0 | 41.6294 | 41.5094
278 | 0 | 30.9307 | 89.4247 | 102.7005 | 21.2877 | 102.7005 | 123.9882 | 278 | 0 | 20.6205 | 13.5498 | 278 | 71.5397 | 71.5397 | 61.2295 | 0 | 0 | 278 | 0 | 30.9307 | 88.7284 | 102.7005 | 20.9818 | 102.7005 | 123.6823 | 278 | 0 | 20.6205 | 13.5498 | 13.5498 | 278 | 70.9827 | 0.55704 | 71.5397 | 61.2295 | 0 | 0 | 278 | 7.6537 | 7.6537 | 278 | 8.5294 | 10.7152 | 19.2446 | 278 | 19.3244 | 0 | 21.9178 | 278 | 12.883 | 126.3997 | 143.7409 | 278 | 36 | 10.6927 | 0 | 17.9199 | 0 | 102.7005 | 278 | 0 | 11.9466 | 13.5498
279 | 0 | 5.1592 | 72.4126 | 111.1008 | 0 | 111.1008 | 111.1008 | 279 | 0 | 3.4394 | 10.929 | 279 | 57.93 | 57.93 | 56.2103 | 0 | 0 | 279 | 0 | 5.1592 | 64.3846 | 111.1008 | 0 | 111.1008 | 111.1008 | 279 | 0 | 3.4394 | 10.929 | 10.929 | 279 | 51.5076 | 6.4224 | 57.93 | 56.2103 | 0 | 0 | 279 | 7.0263 | 7.0263 | 279 | 9.5074 | 9.8368 | 19.3443 | 279 | 29.9906 | 0 | 21.9178 | 279 | 19.9937 | 144.392 | 161.0409 | 279 | 102 | 38.2543 | 0 | 29.5294 | 0 | 111.1008 | 279 | 0 | 19.6862 | 10.929
280 | 0 | 34.1008 | 74.5031 | 102.1773 | 0 | 102.1773 | 102.1773 | 280 | 0 | 22.7339 | 23.1893 | 280 | 59.6025 | 59.6025 | 48.2355 | 0 | 0 | 280 | 0 | 34.1008 | 63.0657 | 102.1773 | 0 | 102.1773 | 102.1773 | 280 | 0 | 22.7339 | 23.1893 | 23.1893 | 280 | 50.4526 | 9.1499 | 59.6025 | 48.2355 | 0 | 0 | 280 | 6.0294 | 6.0294 | 280 | 11.0874 | 8.4412 | 19.5286 | 280 | 27.3973 | 0 | 21.9178 | 280 | 18.2648 | 143.4494 | 159.8519 | 280 | 67.3636 | 0 | 0 | 36.9071 | 0 | 102.1773 | 280 | 0 | 24.6047 | 23.1893
281 | 0 | 23.8245 | 68.4701 | 113.3834 | 0 | 113.3834 | 113.3834 | 281 | 0 | 15.883 | 10.929 | 281 | 54.7761 | 54.7761 | 46.8346 | 0 | 0 | 281 | 0 | 23.8245 | 63.987 | 113.3834 | 0 | 113.3834 | 113.3834 | 281 | 0 | 15.883 | 10.929 | 10.929 | 281 | 51.1896 | 3.5865 | 54.7761 | 46.8346 | 0 | 0 | 281 | 5.8543 | 5.8543 | 281 | 12.366 | 8.1961 | 20.562 | 281 | 11.8721 | 0 | 21.9178 | 281 | 7.9148 | 101.2072 | 114.3293 | 281 | 34.2226 | 0 | 0 | 4.1719 | 0 | 113.3834 | 281 | 0 | 2.7813 | 10.929
282 | 0 | 12 | 76.2125 | 126.4696 | 0 | 126.4696 | 126.4696 | 282 | 0 | 8 | 10.929 | 282 | 60.97 | 60.97 | 56.97 | 0 | 0 | 282 | 41.2988 | 12 | 47.4362 | 126.4696 | 0 | 126.4696 | 126.4696 | 282 | 0 | 8 | 10.929 | 10.929 | 282 | 37.9489 | 23.0211 | 60.97 | 56.97 | 0 | 0 | 282 | 7.1213 | 7.1213 | 282 | 12.0531 | 9.9698 | 22.0228 | 282 | 16.5847 | 0 | 21.9178 | 282 | 11.0565 | 111.7256 | 122.782 | 282 | 96 | 0 | 0 | 17.3067 | 0 | 126.4696 | 282 | 0 | 11.5378 | 10.929
283 | 8.117 | 17.7596 | 81.5192 | 118.0119 | 0 | 118.0119 | 118.0119 | 283 | 0 | 11.8397 | 10.9929 | 283 | 65.2154 | 65.2154 | 59.2955 | 0 | 0 | 283 | 47.8621 | 17.7596 | 52.3903 | 118.0119 | 0 | 118.0119 | 118.0119 | 283 | 0 | 11.8397 | 10.9929 | 10.9929 | 283 | 41.9122 | 23.3032 | 65.2154 | 59.2955 | 0 | 0 | 283 | 7.4119 | 7.4119 | 283 | 11.4749 | 10.3767 | 21.8516 | 283 | 21.9178 | 0 | 21.9178 | 283 | 14.6119 | 113.5531 | 128.165 | 283 | 100.272 | 0 | 0 | 11.1724 | 0 | 118.0119 | 283 | 0 | 7.4483 | 10.9929
284 | 25.5501 | 14.8087 | 80.6361 | 122.4219 | 0 | 122.4219 | 122.4219 | 284 | 0 | 9.8725 | 12.7444 | 284 | 64.5089 | 64.5089 | 59.5727 | 0 | 0 | 284 | 29.547 | 14.8087 | 78.0661 | 122.4219 | 0 | 122.4219 | 122.4219 | 284 | 0 | 9.8725 | 12.7444 | 12.7444 | 284 | 62.4529 | 2.056 | 64.5089 | 59.5727 | 0 | 0 | 284 | 7.4466 | 7.4466 | 284 | 9.2892 | 10.4252 | 19.7144 | 284 | 37.2966 | 0 | 21.9178 | 284 | 24.8644 | 117.9248 | 134.9855 | 284 | 72 | 43.9045 | 0 | 29.224 | 0 | 122.4219 | 284 | 0 | 19.4827 | 12.7444
285 | 12.7905 | 64.5197 | 103.7837 | 89.5338 | 0 | 89.5338 | 89.5338 | 285 | 0 | 43.0131 | 35.1172 | 285 | 83.027 | 83.027 | 61.5204 | 0 | 0 | 285 | 17.6615 | 64.5197 | 91.1085 | 89.5338 | 0 | 89.5338 | 89.5338 | 285 | 0 | 43.0131 | 35.1172 | 35.1172 | 285 | 72.8868 | 10.1401 | 83.027 | 61.5204 | 0 | 0 | 285 | 7.6901 | 7.6901 | 285 | 10.8136 | 10.7661 | 21.5796 | 285 | 9.1324 | 0 | 21.9178 | 285 | 6.0883 | 127.5412 | 141.4331 | 285 | 17.6749 | 0 | 0 | 42.5683 | 0 | 89.5338 | 285 | 0 | 28.3789 | 35.1172
286 | 0 | 29.2582 | 83.7489 | 92.1211 | 17.379 | 92.1211 | 109.5001 | 286 | 0 | 19.5054 | 26.8328 | 286 | 66.9991 | 66.9991 | 57.2464 | 0 | 0 | 286 | 0 | 29.2582 | 81.2331 | 92.1211 | 7.3158 | 92.1211 | 99.4369 | 286 | 0 | 19.5054 | 26.8328 | 26.8328 | 286 | 64.9865 | 2.0127 | 66.9991 | 57.2464 | 0 | 0 | 286 | 7.1558 | 7.1558 | 286 | 10.8945 | 10.0181 | 20.9126 | 286 | 31.1966 | 0 | 21.9178 | 286 | 20.7977 | 128.4261 | 139.1038 | 286 | 65.5452 | 0 | 0 | 40.9323 | 0 | 92.1211 | 286 | 0 | 27.2882 | 26.8328
287 | 0 | 53.3274 | 84.1531 | 94.8867 | 34.4581 | 94.8867 | 129.3448 | 287 | 0 | 35.5516 | 29.8244 | 287 | 67.3224 | 67.3224 | 49.5467 | 0 | 0 | 287 | 0 | 53.3274 | 58.3179 | 94.8867 | 9.8738 | 94.8867 | 104.7605 | 287 | 0 | 35.5516 | 29.8244 | 29.8244 | 287 | 46.6543 | 20.6681 | 67.3224 | 49.5467 | 0 | 0 | 287 | 6.1933 | 6.1933 | 287 | 9.4716 | 8.6707 | 18.1423 | 287 | 19.2966 | 0 | 21.9178 | 287 | 12.8644 | 121.4212 | 144.4056 | 287 | 24 | 0 | 0 | 56.2711 | 0 | 94.8867 | 287 | 0 | 37.5141 | 29.8244
288 | 0 | 140.8372 | 117.6417 | 56.6859 | 200.7046 | 56.6859 | 257.3906 | 288 | 0 | 93.8914 | 99.0523 | 288 | 94.1134 | 94.1134 | 47.1676 | 0 | 0 | 288 | 0 | 140.8372 | 101.1385 | 56.6859 | 182.6938 | 56.6859 | 239.3798 | 288 | 0 | 93.8914 | 99.0523 | 99.0523 | 288 | 80.9108 | 13.2026 | 94.1134 | 47.1676 | 0 | 0 | 288 | 5.896 | 5.896 | 288 | 6.9404 | 8.2543 | 15.1948 | 288 | 18 | 0 | 21.9178 | 288 | 12 | 114.5022 | 126.3653 | 288 | 0 | 0 | 0 | 64.6497 | 0 | 56.6859 | 288 | 47.9198 | 43.0998 | 99.0523
289 | 0 | 138 | 128.2563 | 62.6828 | 203.5734 | 62.6828 | 266.2563 | 289 | 0 | 92 | 85.7181 | 289 | 102.605 | 102.605 | 56.605 | 0 | 0 | 289 | 0 | 138 | 115.769 | 62.6828 | 191.0861 | 62.6828 | 253.769 | 289 | 0 | 92 | 85.7181 | 85.7181 | 289 | 92.6152 | 9.9898 | 102.605 | 56.605 | 0 | 0 | 289 | 7.0756 | 7.0756 | 289 | 4.9921 | 9.9059 | 14.8979 | 289 | 18.4112 | 0 | 21.9178 | 289 | 12.2741 | 131.9946 | 144.4056 | 289 | 0 | 6 | 0 | 131.9389 | 0 | 62.6828 | 289 | 2.247 | 87.9593 | 85.7181
290 | 0 | 107.9227 | 119.497 | 69.318 | 158.1018 | 69.318 | 227.4197 | 290 | 0 | 71.9485 | 70.9649 | 290 | 95.5976 | 95.5976 | 59.6234 | 0 | 0 | 290 | 0 | 107.9227 | 88.1564 | 69.318 | 126.7611 | 69.318 | 196.0791 | 290 | 0 | 71.9485 | 70.9649 | 70.9649 | 290 | 70.5251 | 25.0725 | 95.5976 | 59.6234 | 0 | 0 | 290 | 7.4529 | 7.4529 | 290 | 6.4645 | 10.4341 | 16.8986 | 290 | 25.4244 | 0 | 21.9178 | 290 | 16.9496 | 114.6959 | 131.6455 | 290 | 0 | 0 | 0 | 64.4306 | 0 | 69.318 | 290 | 26.2939 | 42.9537 | 70.9649
291 | 0 | 103.1741 | 115.3452 | 67.7886 | 153.1792 | 67.7886 | 220.9677 | 291 | 0 | 68.7827 | 74.3655 | 291 | 92.2762 | 92.2762 | 57.8848 | 0 | 0 | 291 | 0 | 103.1741 | 97.1642 | 67.7886 | 140.3649 | 67.7886 | 208.1534 | 291 | 0 | 68.7827 | 74.3655 | 74.3655 | 291 | 77.7313 | 14.5448 | 92.2762 | 57.8848 | 0 | 0 | 291 | 7.2356 | 7.2356 | 291 | 8.9014 | 10.1298 | 19.0313 | 291 | 37.4429 | 0 | 21.9178 | 291 | 24.9619 | 109.6823 | 132.2616 | 291 | 0 | 0 | 0 | 85.3507 | 0 | 67.7886 | 291 | 17.2444 | 56.9005 | 74.3655
292 | 0 | 39.6972 | 87.8326 | 91.8567 | 38.7319 | 91.8567 | 130.5886 | 292 | 0 | 26.4648 | 22.7035 | 292 | 70.266 | 70.266 | 57.0336 | 0 | 0 | 292 | 0 | 39.6972 | 43.7927 | 91.8567 | 0 | 91.8567 | 91.8567 | 292 | 0 | 26.4648 | 22.7035 | 22.7035 | 292 | 35.0341 | 35.2319 | 70.266 | 57.0336 | 0 | 0 | 292 | 7.1292 | 7.1292 | 292 | 10.3923 | 9.9809 | 20.3732 | 292 | 20.2377 | 0 | 21.9178 | 292 | 13.4918 | 125.3925 | 129.1054 | 292 | 2.5136 | 0 | 0 | 46.0123 | 0 | 91.8567 | 292 | 0 | 30.6748 | 22.7035
293 | 0 | 16.405 | 76.8297 | 102.0623 | 0 | 102.0623 | 102.0623 | 293 | 0 | 10.9366 | 11.76 | 293 | 61.4638 | 61.4638 | 55.9954 | 0 | 0 | 293 | 0 | 16.405 | 46.1081 | 102.0623 | 0 | 102.0623 | 102.0623 | 293 | 0 | 10.9366 | 11.76 | 11.76 | 293 | 36.8865 | 24.5773 | 61.4638 | 55.9954 | 0 | 0 | 293 | 6.9994 | 6.9994 | 293 | 10.1869 | 9.7992 | 19.9861 | 293 | 2.7397 | 0 | 21.9178 | 293 | 1.8265 | 122.4026 | 136.3907 | 293 | 113.4119 | 0 | 0 | 7.006 | 0 | 102.0623 | 293 | 0 | 4.6707 | 11.76
294 | 0 | 11.2385 | 64.5634 | 99.7107 | 0 | 99.7107 | 99.7107 | 294 | 0 | 7.4923 | 12.1818 | 294 | 51.6507 | 51.6507 | 47.9046 | 0 | 0 | 294 | 0 | 11.2385 | 43.6443 | 99.7107 | 0 | 99.7107 | 99.7107 | 294 | 0 | 7.4923 | 12.1818 | 12.1818 | 294 | 34.9155 | 16.7353 | 51.6507 | 47.9046 | 0 | 0 | 294 | 5.9881 | 5.9881 | 294 | 12.1674 | 8.3833 | 20.5507 | 294 | 31.6986 | 0 | 21.9178 | 294 | 21.1324 | 123.1189 | 136.3204 | 294 | 102.1994 | 0 | 0 | 17.6514 | 0 | 99.7107 | 294 | 0 | 11.7676 | 12.1818
295 | 0 | 33.0474 | 72.4007 | 95.249 | 0 | 95.249 | 95.249 | 295 | 0 | 22.0316 | 15.6081 | 295 | 57.9206 | 57.9206 | 46.9047 | 0 | 0 | 295 | 18.7302 | 33.5104 | 39.2765 | 95.249 | 0 | 95.249 | 95.249 | 295 | 0 | 22.3403 | 15.6081 | 15.6081 | 295 | 31.4212 | 26.6537 | 58.0749 | 46.9047 | 0 | 0 | 295 | 5.8631 | 5.8631 | 295 | 12.5674 | 8.2083 | 20.7757 | 295 | 16.5568 | 0 | 21.9178 | 295 | 11.0379 | 121.0803 | 136.1691 | 295 | 24 | 0 | 0 | 19.0666 | 0 | 95.249 | 295 | 0 | 12.7111 | 15.6081
296 | 0 | 7.6522 | 75.1394 | 106.4206 | 0 | 106.4206 | 106.4206 | 296 | 0 | 5.1015 | 12.0923 | 296 | 60.1115 | 60.1115 | 57.5608 | 0 | 0 | 296 | 67.9906 | 7.1892 | 31.2407 | 106.4206 | 0 | 106.4206 | 106.4206 | 296 | 0 | 4.7928 | 12.0923 | 12.0923 | 296 | 24.9926 | 34.9646 | 59.9572 | 57.5608 | 0 | 0 | 296 | 7.1951 | 7.1951 | 296 | 11.3831 | 10.0731 | 21.4562 | 296 | 17.498 | 0 | 21.9178 | 296 | 11.6653 | 128.1686 | 143.7139 | 296 | 90 | 0 | 0 | 17.7884 | 0 | 106.4206 | 296 | 0 | 11.8589 | 12.0923
297 | 0 | 18.6831 | 84.6006 | 140.6771 | 0 | 140.6771 | 140.6771 | 297 | 0 | 12.4554 | 10.929 | 297 | 67.6805 | 67.6805 | 61.4528 | 0 | 0 | 297 | 69.0391 | 18.6831 | 52.9549 | 140.6771 | 0 | 140.6771 | 140.6771 | 297 | 0 | 12.4554 | 10.929 | 10.929 | 297 | 42.3639 | 25.3166 | 67.6805 | 61.4528 | 0 | 0 | 297 | 7.6816 | 7.6816 | 297 | 7.9625 | 10.7542 | 18.7167 | 297 | 27.2509 | 0 | 21.9178 | 297 | 18.1673 | 101.7666 | 119.9338 | 297 | 96 | 0 | 0 | 20.7971 | 0 | 140.6771 | 297 | 0 | 13.8648 | 10.929
298 | 12.5258 | 24.083 | 88.2554 | 133.2255 | 0 | 133.2255 | 133.2255 | 298 | 0 | 16.0553 | 10.929 | 298 | 70.6043 | 70.6043 | 62.5767 | 0 | 0 | 298 | 60.9784 | 24.083 | 48.1642 | 133.2255 | 0 | 133.2255 | 133.2255 | 298 | 0 | 16.0553 | 10.929 | 10.929 | 298 | 38.5314 | 32.073 | 70.6043 | 62.5767 | 0 | 0 | 298 | 7.8221 | 7.8221 | 298 | 5.5872 | 10.9509 | 16.5382 | 298 | 17.498 | 0 | 21.9178 | 298 | 11.6653 | 99.3078 | 110.9731 | 298 | 109.102 | 0 | 0 | 11.9898 | 0 | 133.2255 | 298 | 0 | 7.9932 | 10.929
299 | 0 | 56.3517 | 101.4887 | 87.7571 | 0 | 87.7571 | 87.7571 | 299 | 0 | 37.5678 | 36.3189 | 299 | 81.191 | 81.191 | 62.4071 | 0 | 0 | 299 | 12.7433 | 56.3517 | 79.7698 | 87.7571 | 0 | 87.7571 | 87.7571 | 299 | 0 | 37.5678 | 36.3189 | 36.3189 | 299 | 63.8158 | 17.3751 | 81.191 | 62.4071 | 0 | 0 | 299 | 7.8009 | 7.8009 | 299 | 7.0465 | 10.9212 | 17.9677 | 299 | 21.9178 | 0 | 21.9178 | 299 | 14.6119 | 88.249 | 102.8609 | 299 | 29.9077 | 0 | 0 | 54.4784 | 0 | 87.7571 | 299 | 0 | 36.3189 | 36.3189
300 | 0 | 16.1465 | 81.8181 | 101.5793 | 0 | 101.5793 | 101.5793 | 300 | 0 | 10.7643 | 14.6109 | 300 | 65.4545 | 65.4545 | 60.0723 | 0 | 0 | 300 | 0 | 16.1465 | 61.6612 | 101.5793 | 0 | 101.5793 | 101.5793 | 300 | 0 | 10.7643 | 14.6109 | 14.6109 | 300 | 49.329 | 16.1255 | 65.4545 | 60.0723 | 0 | 0 | 300 | 7.509 | 7.509 | 300 | 10.1133 | 10.5126 | 20.626 | 300 | 21.0046 | 0 | 21.9178 | 300 | 14.003 | 89.6469 | 103.6499 | 300 | 30 | 73.2797 | 0 | 33.4457 | 0 | 101.5793 | 300 | 0 | 22.2971 | 14.6109
301 | 0 | 9.5628 | 71.6625 | 123.4683 | 0 | 123.4683 | 123.4683 | 301 | 0 | 6.3752 | 10.929 | 301 | 57.33 | 57.33 | 54.1424 | 0 | 0 | 301 | 25.8562 | 9.5628 | 50.7132 | 123.4683 | 0 | 123.4683 | 123.4683 | 301 | 0 | 6.3752 | 10.929 | 10.929 | 301 | 40.5706 | 16.7595 | 57.33 | 54.1424 | 0 | 0 | 301 | 6.7678 | 6.7678 | 301 | 13.693 | 9.4749 | 23.168 | 301 | 37.2966 | 0 | 21.9178 | 301 | 24.8644 | 110.9234 | 118.8421 | 301 | 44.7182 | 93.0034 | 0 | 17.4645 | 0 | 123.4683 | 301 | 0 | 11.643 | 10.929
302 | 0 | 17.7596 | 75.5622 | 112.4347 | 0 | 112.4347 | 112.4347 | 302 | 0 | 11.8397 | 10.929 | 302 | 60.4498 | 60.4498 | 54.5299 | 0 | 0 | 302 | 23.6674 | 17.7596 | 72.9215 | 112.4347 | 0 | 112.4347 | 112.4347 | 302 | 0 | 11.8397 | 10.929 | 10.929 | 302 | 58.3372 | 2.1126 | 60.4498 | 54.5299 | 0 | 0 | 302 | 6.8162 | 6.8162 | 302 | 13.8314 | 9.5427 | 23.3741 | 302 | 13.6986 | 0 | 21.9178 | 302 | 9.1324 | 73.1491 | 96.1538 | 302 | 96.0646 | 36 | 0 | 10.2459 | 0 | 112.4347 | 302 | 0 | 6.8306 | 10.929
303 | 32.0913 | 27.6277 | 85.4811 | 149.1578 | 0 | 149.1578 | 149.1578 | 303 | 0 | 18.4185 | 10.929 | 303 | 68.3849 | 68.3849 | 59.1756 | 0 | 0 | 303 | 42.2732 | 27.6277 | 85.3301 | 149.1578 | 0 | 149.1578 | 149.1578 | 303 | 0 | 18.4185 | 10.929 | 10.929 | 303 | 68.2641 | 0.12083 | 68.3849 | 59.1756 | 0 | 0 | 303 | 7.397 | 7.397 | 303 | 12.9142 | 10.3557 | 23.2699 | 303 | 14.7582 | 0 | 21.9178 | 303 | 9.8388 | 98.6824 | 111.5946 | 303 | 132 | 0 | 0 | 10.6236 | 0 | 149.1578 | 303 | 0 | 7.0824 | 10.929
304 | 82.499 | 5.3067 | 76.8676 | 172.6912 | 0 | 172.6912 | 172.6912 | 304 | 0 | 3.5378 | 10.929 | 304 | 61.4941 | 61.4941 | 59.7252 | 0 | 0 | 304 | 82.7664 | 5.3067 | 76.6312 | 172.6912 | 0 | 172.6912 | 172.6912 | 304 | 0 | 3.5378 | 10.929 | 10.929 | 304 | 61.3049 | 0.18918 | 61.4941 | 59.7252 | 0 | 0 | 304 | 7.4657 | 7.4657 | 304 | 13.8702 | 10.4519 | 24.3222 | 304 | 21.9178 | 0 | 21.9178 | 304 | 14.6119 | 76.6454 | 91.2573 | 304 | 120 | 0 | 0 | 15.7104 | 0 | 172.6912 | 304 | 0 | 10.4736 | 10.929
305 | 53.2254 | 16.9939 | 84.4132 | 151.6072 | 0 | 151.6072 | 151.6072 | 305 | 0 | 11.3292 | 10.929 | 305 | 67.5306 | 67.5306 | 61.8659 | 0 | 0 | 305 | 83.2234 | 15.783 | 52.6008 | 151.6072 | 0 | 151.6072 | 151.6072 | 305 | 0 | 10.522 | 10.929 | 10.929 | 305 | 42.0806 | 25.0463 | 67.1269 | 61.8659 | 0 | 0 | 305 | 7.7332 | 7.7332 | 305 | 14.4956 | 10.8265 | 25.3221 | 305 | 36.3833 | 0 | 21.9178 | 305 | 24.2555 | 72.2519 | 71.1415 | 305 | 78 | 36 | 0 | 28.9939 | 0 | 151.6072 | 305 | 0 | 19.3292 | 10.929
306 | 15.3338 | 27.5345 | 86.145 | 105.4949 | 0 | 105.4949 | 105.4949 | 306 | 0 | 18.3563 | 12.7316 | 306 | 68.916 | 68.916 | 59.7378 | 0 | 0 | 306 | 34.1456 | 28.7454 | 48.493 | 105.4949 | 0 | 105.4949 | 105.4949 | 306 | 0 | 19.1636 | 12.7316 | 12.7316 | 306 | 38.7944 | 30.5252 | 69.3196 | 59.7378 | 0 | 0 | 306 | 7.4672 | 7.4672 | 306 | 15.3002 | 10.4541 | 25.7543 | 306 | 7.4523 | 0 | 21.9178 | 306 | 4.9682 | 36.554 | 66.8882 | 306 | 102 | 0 | 0 | 6.4969 | 0 | 105.4949 | 306 | 0 | 4.3313 | 12.7316
307 | 12.6922 | 7.2083 | 74.891 | 121.3352 | 0 | 121.3352 | 121.3352 | 307 | 0 | 4.8056 | 10.929 | 307 | 59.9128 | 59.9128 | 57.51 | 0 | 0 | 307 | 42.6637 | 7.2083 | 65.5741 | 121.3352 | 0 | 121.3352 | 121.3352 | 307 | 0 | 4.8056 | 10.929 | 10.929 | 307 | 52.4592 | 7.4535 | 59.9128 | 57.51 | 0 | 0 | 307 | 7.1887 | 7.1887 | 307 | 19.0691 | 10.0642 | 29.1334 | 307 | 21.9178 | 0 | 21.9178 | 307 | 14.6119 | 82.5148 | 97.1266 | 307 | 108 | 0 | 0 | 16.3934 | 0 | 121.3352 | 307 | 0 | 10.929 | 10.929
308 | 52.2666 | 21.1749 | 70.9535 | 141.7868 | 0 | 141.7868 | 141.7868 | 308 | 0 | 14.1166 | 10.929 | 308 | 56.7628 | 56.7628 | 49.7045 | 0 | 0 | 308 | 73.1939 | 21.1749 | 47.8258 | 141.7868 | 0 | 141.7868 | 141.7868 | 308 | 0 | 14.1166 | 10.929 | 10.929 | 308 | 38.2606 | 18.5022 | 56.7628 | 49.7045 | 0 | 0 | 308 | 6.2131 | 6.2131 | 308 | 22.2495 | 8.6983 | 30.9478 | 308 | 42.776 | 0 | 21.9178 | 308 | 28.5173 | 70.5117 | 99.029 | 308 | 96 | 36 | 0 | 23.5294 | 0 | 141.7868 | 308 | 0 | 15.6862 | 10.929
309 | 44.6845 | 22.1633 | 70.2099 | 126.9871 | 0 | 126.9871 | 126.9871 | 309 | 0 | 14.7755 | 10.929 | 309 | 56.1679 | 56.1679 | 48.7802 | 0 | 0 | 309 | 55.9784 | 22.1633 | 59.3905 | 126.9871 | 0 | 126.9871 | 126.9871 | 309 | 0 | 14.7755 | 10.929 | 10.929 | 309 | 47.5124 | 8.6555 | 56.1679 | 48.7802 | 0 | 0 | 309 | 6.0975 | 6.0975 | 309 | 20.2617 | 8.5365 | 28.7982 | 309 | 6.3927 | 0 | 22.7866 | 309 | 4.2618 | 81.8903 | 83.0316 | 309 | 96 | 0 | 0 | 15.0273 | 0 | 126.9871 | 309 | 0 | 10.0182 | 10.929
310 | 30.6931 | 4.4761 | 76.1205 | 123.9685 | 0 | 123.9685 | 123.9685 | 310 | 0 | 2.9841 | 10.929 | 310 | 60.8964 | 60.8964 | 59.4044 | 0 | 0 | 310 | 33.9155 | 4.4761 | 74.624 | 123.9685 | 0 | 123.9685 | 123.9685 | 310 | 0 | 2.9841 | 10.929 | 10.929 | 310 | 59.6992 | 1.1972 | 60.8964 | 59.4044 | 0 | 0 | 310 | 7.4256 | 7.4256 | 310 | 18.8437 | 10.3958 | 29.2395 | 310 | 46.1535 | 0 | 44.1735 | 310 | 30.769 | 65.5986 | 78.8647 | 310 | 120 | 0 | 0 | 15.7104 | 0 | 123.9685 | 310 | 0 | 10.4736 | 10.929
311 | 42.2802 | 28.9939 | 89.067 | 158.8748 | 0 | 158.8748 | 158.8748 | 311 | 0 | 19.3292 | 10.929 | 311 | 71.2536 | 71.2536 | 61.589 | 0 | 0 | 311 | 49.8844 | 28.9939 | 79.9965 | 158.8748 | 0 | 158.8748 | 158.8748 | 311 | 0 | 19.3292 | 10.929 | 10.929 | 311 | 63.9972 | 7.2564 | 71.2536 | 61.589 | 0 | 0 | 311 | 7.6986 | 7.6986 | 311 | 18.791 | 10.7781 | 29.569 | 311 | 47.0955 | 0 | 53.5399 | 311 | 31.397 | 39.0097 | 91.0303 | 311 | 36 | 0 | 44.0724 | 15.0171 | 0 | 158.8748 | 311 | 0 | 10.0114 | 10.929
312 | 88.3884 | 6.8306 | 79.4844 | 176.1698 | 0 | 176.1698 | 176.1698 | 312 | 0 | 4.5537 | 10.929 | 312 | 63.5875 | 63.5875 | 61.3107 | 0 | 0 | 312 | 98.3548 | 6.8306 | 70.9843 | 176.1698 | 0 | 176.1698 | 176.1698 | 312 | 0 | 4.5537 | 10.929 | 10.929 | 312 | 56.7875 | 6.8 | 63.5875 | 61.3107 | 0 | 0 | 312 | 7.6638 | 7.6638 | 312 | 18.2979 | 10.7294 | 29.0273 | 312 | 23.4412 | 0 | 23.4412 | 312 | 15.6275 | 95.2916 | 110.919 | 312 | 126 | 0 | 37.4867 | 12.6831 | 0 | 176.1698 | 312 | 0 | 8.4554 | 10.929
313 | 43.3796 | 23.224 | 88.9421 | 155.5457 | 0 | 155.5457 | 155.5457 | 313 | 0 | 15.4827 | 10.929 | 313 | 71.1537 | 71.1537 | 63.4123 | 0 | 0 | 313 | 44.8012 | 23.224 | 87.5204 | 155.5457 | 0 | 155.5457 | 155.5457 | 313 | 0 | 15.4827 | 10.929 | 10.929 | 313 | 70.0164 | 1.1373 | 71.1537 | 63.4123 | 0 | 0 | 313 | 7.9265 | 7.9265 | 313 | 17.3617 | 11.0972 | 28.4589 | 313 | 21.9178 | 0 | 21.9178 | 313 | 14.6119 | 89.7515 | 104.3633 | 313 | 108 | 6 | 25.1542 | 16.3934 | 0 | 155.5457 | 313 | 0 | 10.929 | 10.929
314 | 61.1963 | 9.2575 | 81.6306 | 152.0844 | 0 | 152.0844 | 152.0844 | 314 | 0 | 6.1717 | 10.929 | 314 | 65.3045 | 65.3045 | 62.2186 | 0 | 0 | 314 | 98.4797 | 9.2575 | 44.3472 | 152.0844 | 0 | 152.0844 | 152.0844 | 314 | 0 | 6.1717 | 10.929 | 10.929 | 314 | 35.4778 | 29.8267 | 65.3045 | 62.2186 | 0 | 0 | 314 | 7.7773 | 7.7773 | 314 | 11.3362 | 10.8883 | 22.2245 | 314 | 29.0774 | 0 | 24.7146 | 314 | 19.3849 | 77.9546 | 93.4948 | 314 | 102 | 66 | 0.0421 | 23.5294 | 0 | 152.0844 | 314 | 0 | 15.6862 | 10.929
315 | 74.2472 | 15.0273 | 72.9926 | 162.2671 | 0 | 162.2671 | 162.2671 | 315 | 0 | 10.0182 | 10.929 | 315 | 58.3941 | 58.3941 | 53.3849 | 0 | 0 | 315 | 127.6634 | 14.9961 | 19.6076 | 162.2671 | 0 | 162.2671 | 162.2671 | 315 | 0 | 9.9974 | 10.929 | 10.929 | 315 | 15.6861 | 42.6976 | 58.3836 | 53.3849 | 0 | 0 | 315 | 6.6731 | 6.6731 | 315 | 11.2069 | 9.3424 | 20.5492 | 315 | 45.8755 | 0 | 29.38 | 315 | 30.5836 | 73.112 | 105.3415 | 315 | 102 | 30 | 0 | 16.3934 | 0 | 162.2671 | 315 | 0 | 10.929 | 10.929
316 | 76.6113 | 26.9447 | 74.3329 | 177.8889 | 0 | 177.8889 | 177.8889 | 316 | 0 | 17.9631 | 10.929 | 316 | 59.4664 | 59.4664 | 50.4848 | 0 | 0 | 316 | 113.0246 | 26.9759 | 37.8884 | 177.8889 | 0 | 177.8889 | 177.8889 | 316 | 0 | 17.984 | 10.929 | 10.929 | 316 | 30.3107 | 29.166 | 59.4768 | 50.4848 | 0 | 0 | 316 | 6.3106 | 6.3106 | 316 | 14.0081 | 8.8348 | 22.8429 | 316 | 15.3927 | 0 | 21.9178 | 316 | 10.2618 | 107.1586 | 118.3125 | 316 | 96 | 0 | 41.9292 | 14.3443 | 0 | 177.8889 | 316 | 0 | 9.5628 | 10.929
317 | 80.44 | 7.5137 | 79.7814 | 167.735 | 0 | 167.735 | 167.735 | 317 | 0 | 5.0091 | 10.929 | 317 | 63.8251 | 63.8251 | 61.3205 | 0 | 0 | 317 | 84.6694 | 7.5137 | 75.5519 | 167.735 | 0 | 167.735 | 167.735 | 317 | 0 | 5.0091 | 10.929 | 10.929 | 317 | 60.4415 | 3.3836 | 63.8251 | 61.3205 | 0 | 0 | 317 | 7.6651 | 7.6651 | 317 | 10.8369 | 10.7311 | 21.568 | 317 | 28.4429 | 0 | 21.9178 | 317 | 18.9619 | 93.9255 | 114.1942 | 317 | 132 | 0 | 24.4283 | 11.3067 | 0 | 167.735 | 317 | 0 | 7.5378 | 10.929
318 | 83.4209 | 25.9563 | 90.5329 | 199.9101 | 0 | 199.9101 | 199.9101 | 318 | 0 | 17.3042 | 10.929 | 318 | 72.4263 | 72.4263 | 63.7742 | 0 | 0 | 318 | 97.9776 | 25.9563 | 75.9762 | 199.9101 | 0 | 199.9101 | 199.9101 | 318 | 0 | 17.3042 | 10.929 | 10.929 | 318 | 60.781 | 11.6453 | 72.4263 | 63.7742 | 0 | 0 | 318 | 7.9718 | 7.9718 | 318 | 9.9779 | 11.1605 | 21.1384 | 318 | 2.8861 | 0 | 21.9178 | 318 | 1.9241 | 121.6743 | 117.1559 | 318 | 96 | 0 | 84.544 | 19.3661 | 0 | 199.9101 | 318 | 0 | 12.9107 | 10.929
319 | 78.8559 | 13.6612 | 82.7327 | 175.2498 | 0 | 175.2498 | 175.2498 | 319 | 0 | 9.1075 | 10.929 | 319 | 66.1862 | 66.1862 | 61.6324 | 0 | 0 | 319 | 79.1765 | 13.6612 | 82.4121 | 175.2498 | 0 | 175.2498 | 175.2498 | 319 | 0 | 9.1075 | 10.929 | 10.929 | 319 | 65.9297 | 0.25646 | 66.1862 | 61.6324 | 0 | 0 | 319 | 7.7041 | 7.7041 | 319 | 12.3432 | 10.7857 | 23.1288 | 319 | 28.1781 | 0 | 21.9178 | 319 | 18.7854 | 96.1748 | 120.3554 | 319 | 114 | 0 | 47.829 | 13.4208 | 0 | 175.2498 | 319 | 0 | 8.9472 | 10.929
320 | 52.884 | 17.7596 | 87.1791 | 157.8226 | 0 | 157.8226 | 157.8226 | 320 | 0 | 11.8397 | 10.929 | 320 | 69.7432 | 69.7432 | 63.8234 | 0 | 0 | 320 | 65.9435 | 17.7596 | 74.1195 | 157.8226 | 0 | 157.8226 | 157.8226 | 320 | 0 | 11.8397 | 10.929 | 10.929 | 320 | 59.2956 | 10.4477 | 69.7432 | 63.8234 | 0 | 0 | 320 | 7.9779 | 7.9779 | 320 | 16.0682 | 11.1691 | 27.2373 | 320 | 13.8311 | 0 | 21.9178 | 320 | 9.2207 | 108.5471 | 118.8151 | 320 | 114 | 0 | 26.7461 | 17.0765 | 0 | 157.8226 | 320 | 0 | 11.3843 | 10.929
321 | 68.385 | 11.3067 | 82.3454 | 162.0371 | 0 | 162.0371 | 162.0371 | 321 | 0 | 7.5378 | 10.929 | 321 | 65.8763 | 65.8763 | 62.1074 | 0 | 0 | 321 | 87.4243 | 11.3067 | 63.3061 | 162.0371 | 0 | 162.0371 | 162.0371 | 321 | 0 | 7.5378 | 10.929 | 10.929 | 321 | 50.6448 | 15.2315 | 65.8763 | 62.1074 | 0 | 0 | 321 | 7.7634 | 7.7634 | 321 | 18.8714 | 10.8688 | 29.7402 | 321 | 21.9178 | 0 | 21.9178 | 321 | 14.6119 | 92.0538 | 106.6657 | 321 | 84 | 72 | 19.8872 | 15.7104 | 0 | 162.0371 | 321 | 0 | 10.4736 | 10.929
322 | 79.9982 | 10.2459 | 72.8969 | 163.141 | 0 | 163.141 | 163.141 | 322 | 0 | 6.8306 | 10.929 | 322 | 58.3175 | 58.3175 | 54.9022 | 0 | 0 | 322 | 97.9138 | 10.2459 | 54.9813 | 163.141 | 0 | 163.141 | 163.141 | 322 | 0 | 6.8306 | 10.929 | 10.929 | 322 | 43.9851 | 14.3325 | 58.3175 | 54.9022 | 0 | 0 | 322 | 6.8628 | 6.8628 | 322 | 14.3038 | 9.6079 | 23.9117 | 322 | 31.1687 | 0 | 21.9178 | 322 | 20.7791 | 91.9474 | 91.9545 | 322 | 102 | 60 | 0 | 25.5786 | 0 | 163.141 | 322 | 0 | 17.0524 | 10.929
323 | 84.8271 | 17.0765 | 74.7894 | 176.693 | 0 | 176.693 | 176.693 | 323 | 0 | 11.3843 | 10.929 | 323 | 59.8315 | 59.8315 | 54.1393 | 0 | 0 | 323 | 84.9868 | 17.0765 | 74.6297 | 176.693 | 0 | 176.693 | 176.693 | 323 | 0 | 11.3843 | 10.929 | 10.929 | 323 | 59.7037 | 0.12776 | 59.8315 | 54.1393 | 0 | 0 | 323 | 6.7674 | 6.7674 | 323 | 12.0383 | 9.4744 | 21.5127 | 323 | 18 | 0 | 21.9178 | 323 | 12 | 66.0786 | 98.8507 | 323 | 114 | 0 | 0 | 12.9781 | 0 | 176.693 | 323 | 0 | 8.6521 | 10.929
324 | 77.6843 | 26.9447 | 89.06 | 193.689 | 0 | 193.689 | 193.689 | 324 | 0 | 17.9631 | 10.929 | 324 | 71.248 | 71.248 | 62.2664 | 0 | 0 | 324 | 79.4574 | 26.9447 | 87.2869 | 193.689 | 0 | 193.689 | 193.689 | 324 | 0 | 17.9631 | 10.929 | 10.929 | 324 | 69.8295 | 1.4185 | 71.248 | 62.2664 | 0 | 0 | 324 | 7.7833 | 7.7833 | 324 | 15.4416 | 10.8966 | 26.3382 | 324 | 16.5847 | 0 | 21.9178 | 324 | 11.0565 | 68.0784 | 79.1349 | 324 | 60 | 0 | 118.7821 | 10.6236 | 0 | 193.689 | 324 | 0 | 7.0824 | 10.929
325 | 117.792 | 15.7104 | 85.7151 | 219.2175 | 0 | 219.2175 | 219.2175 | 325 | 0 | 10.4736 | 10.929 | 325 | 68.5721 | 68.5721 | 63.3353 | 0 | 0 | 325 | 131.7482 | 15.7104 | 71.7589 | 219.2175 | 0 | 219.2175 | 219.2175 | 325 | 0 | 10.4736 | 10.929 | 10.929 | 325 | 57.4071 | 11.165 | 68.5721 | 63.3353 | 0 | 0 | 325 | 7.9169 | 7.9169 | 325 | 17.0746 | 11.0837 | 28.1583 | 325 | 22.8311 | 0 | 21.9178 | 325 | 15.2207 | 31.0512 | 43.8486 | 325 | 108 | 24 | 60.141 | 17.0765 | 10 | 219.2175 | 325 | 0 | 11.3843 | 10.929
326 | 127.5663 | 5.8422 | 84.7683 | 218.1768 | 0 | 218.1768 | 218.1768 | 326 | 0 | 3.8948 | 10.929 | 326 | 67.8147 | 67.8147 | 65.8672 | 0 | 0 | 326 | 168.821 | 5.8422 | 43.5136 | 218.1768 | 0 | 218.1768 | 218.1768 | 326 | 0 | 3.8948 | 10.929 | 10.929 | 326 | 34.8109 | 33.0038 | 67.8147 | 65.8672 | 0 | 0 | 326 | 8.2334 | 8.2334 | 326 | 17.2767 | 11.5268 | 28.8035 | 326 | 34.5568 | 0 | 21.9178 | 326 | 23.0379 | 65.3781 | 77.9189 | 326 | 90 | 60 | 40.5491 | 27.6277 | 0 | 218.1768 | 326 | 0 | 18.4185 | 10.929
327 | 41.3389 | 26.9447 | 94.2997 | 156.7761 | 0 | 156.7761 | 156.7761 | 327 | 0 | 17.9631 | 10.929 | 327 | 75.4398 | 75.4398 | 66.4582 | 0 | 0 | 327 | 63.2204 | 26.9447 | 66.611 | 156.7761 | 0 | 156.7761 | 156.7761 | 327 | 0 | 17.9631 | 10.929 | 10.929 | 327 | 53.2888 | 22.1509 | 75.4398 | 66.4582 | 0 | 0 | 327 | 8.3073 | 8.3073 | 327 | 18.4463 | 11.6302 | 30.0765 | 327 | 26.6304 | 0 | 21.9178 | 327 | 17.7536 | 56.6055 | 87.2795 | 327 | 108 | 0 | 44.3144 | 10.2459 | 0 | 156.7761 | 327 | 0 | 6.8306 | 10.929
328 | 40.4083 | 18.4426 | 82.9138 | 141.4188 | 0 | 141.4188 | 141.4188 | 328 | 0 | 12.2951 | 10.929 | 328 | 66.3311 | 66.3311 | 60.1835 | 0 | 0 | 328 | 52.8597 | 18.4426 | 73.1797 | 141.4188 | 0 | 141.4188 | 141.4188 | 328 | 0 | 12.2951 | 10.929 | 10.929 | 328 | 58.5438 | 7.7873 | 66.3311 | 60.1835 | 0 | 0 | 328 | 7.5229 | 7.5229 | 328 | 14.5842 | 10.5321 | 25.1163 | 328 | 3.653 | 0 | 21.9178 | 328 | 2.4353 | 88.2977 | 90.733 | 328 | 132 | 0 | 0 | 10.6236 | 0 | 141.4188 | 328 | 0 | 7.0824 | 10.929
329 | 91.4202 | 3.793 | 68.5593 | 169.9256 | 0 | 169.9256 | 169.9256 | 329 | 0 | 2.5287 | 10.929 | 329 | 54.8474 | 54.8474 | 53.5831 | 0 | 0 | 329 | 99.7366 | 3.793 | 63.3328 | 169.9256 | 0 | 169.9256 | 169.9256 | 329 | 0 | 2.5287 | 10.929 | 10.929 | 329 | 50.6662 | 4.1812 | 54.8474 | 53.5831 | 0 | 0 | 329 | 6.6979 | 6.6979 | 329 | 12.145 | 9.377 | 21.5221 | 329 | 47.3392 | 0 | 47.3392 | 329 | 31.5595 | 56.801 | 88.3604 | 329 | 108 | 42 | 0 | 19.8736 | 0 | 169.9256 | 329 | 0 | 13.2491 | 10.929
330 | 112.3184 | 17.0765 | 74.7182 | 204.1131 | 0 | 204.1131 | 204.1131 | 330 | 0 | 11.3843 | 10.929 | 330 | 59.7746 | 59.7746 | 54.0824 | 0 | 0 | 330 | 113.0169 | 17.0765 | 74.0198 | 204.1131 | 0 | 204.1131 | 204.1131 | 330 | 0 | 11.3843 | 10.929 | 10.929 | 330 | 59.2158 | 0.55875 | 59.7746 | 54.0824 | 0 | 0 | 330 | 6.7603 | 6.7603 | 330 | 9.1139 | 9.4644 | 18.5783 | 330 | 104.2756 | 0 | 104.2756 | 330 | 69.5171 | 31.7936 | 93.8893 | 330 | 120 | 30 | 28.493 | 18.6831 | 0 | 204.1131 | 330 | 0 | 12.4554 | 10.929
331 | 87.1246 | 16.3934 | 87.2789 | 190.7969 | 0 | 190.7969 | 190.7969 | 331 | 0 | 10.929 | 10.929 | 331 | 69.8231 | 69.8231 | 64.3586 | 0 | 0 | 331 | 89.0708 | 16.3934 | 85.3327 | 190.7969 | 0 | 190.7969 | 190.7969 | 331 | 0 | 10.929 | 10.929 | 10.929 | 331 | 68.2661 | 1.5569 | 69.8231 | 64.3586 | 0 | 0 | 331 | 8.0448 | 8.0448 | 331 | 7.6865 | 11.2628 | 18.9492 | 331 | 35.4867 | 0 | 33.6526 | 331 | 23.6578 | 56.1085 | 87.1877 | 331 | 120 | 0 | 54.4035 | 16.3934 | 0 | 190.7969 | 331 | 0 | 10.929 | 10.929
332 | 66.5529 | 25.5786 | 91.8118 | 183.9433 | 0 | 183.9433 | 183.9433 | 332 | 0 | 17.0524 | 10.929 | 332 | 73.4495 | 73.4495 | 64.9233 | 0 | 0 | 332 | 98.352 | 25.5786 | 60.0127 | 183.9433 | 0 | 183.9433 | 183.9433 | 332 | 0 | 17.0524 | 10.929 | 10.929 | 332 | 48.0102 | 25.4393 | 73.4495 | 64.9233 | 0 | 0 | 332 | 8.1154 | 8.1154 | 332 | 11.7161 | 11.3616 | 23.0777 | 332 | 24.5036 | 0 | 21.9178 | 332 | 16.3357 | 51.6658 | 68.0015 | 332 | 90 | 0 | 78.2329 | 15.7104 | 0 | 183.9433 | 332 | 0 | 10.4736 | 10.929
333 | 83.7395 | 15.7104 | 87.3338 | 186.7836 | 0 | 186.7836 | 186.7836 | 333 | 0 | 10.4736 | 10.929 | 333 | 69.867 | 69.867 | 64.6302 | 0 | 0 | 333 | 97.8969 | 15.7104 | 73.1763 | 186.7836 | 0 | 186.7836 | 186.7836 | 333 | 0 | 10.4736 | 10.929 | 10.929 | 333 | 58.5411 | 11.3259 | 69.867 | 64.6302 | 0 | 0 | 333 | 8.0788 | 8.0788 | 333 | 11.2208 | 11.3103 | 22.5311 | 333 | 21.9178 | 0 | 21.9178 | 333 | 14.6119 | 51.017 | 65.6289 | 333 | 102 | 0 | 72.1108 | 12.6728 | 0 | 186.7836 | 333 | 0 | 8.4485 | 10.929
334 | 99.2506 | 19.8087 | 90.3434 | 209.4028 | 0 | 209.4028 | 209.4028 | 334 | 0 | 13.2058 | 10.929 | 334 | 72.2748 | 72.2748 | 65.6718 | 0 | 0 | 334 | 103.2483 | 19.8087 | 86.3458 | 209.4028 | 0 | 209.4028 | 209.4028 | 334 | 0 | 13.2058 | 10.929 | 10.929 | 334 | 69.0767 | 3.1981 | 72.2748 | 65.6718 | 0 | 0 | 334 | 8.209 | 8.209 | 334 | 12.2694 | 11.4926 | 23.762 | 334 | 18.4112 | 0 | 21.9178 | 334 | 12.2741 | 82.161 | 94.4352 | 334 | 114 | 0 | 77.4028 | 18 | 0 | 209.4028 | 334 | 0 | 12 | 10.929
335 | 141.3634 | 13.6612 | 84.1902 | 239.2148 | 0 | 239.2148 | 239.2148 | 335 | 0 | 9.1075 | 10.929 | 335 | 67.3522 | 67.3522 | 62.7985 | 0 | 0 | 335 | 142.1232 | 13.6612 | 83.4305 | 239.2148 | 0 | 239.2148 | 239.2148 | 335 | 0 | 9.1075 | 10.929 | 10.929 | 335 | 66.7444 | 0.60782 | 67.3522 | 62.7985 | 0 | 0 | 335 | 7.8498 | 7.8498 | 335 | 10.3232 | 10.9897 | 21.3129 | 335 | 37.1781 | 0 | 21.9178 | 335 | 24.7854 | 115.3035 | 104.0823 | 335 | 108 | 0 | 47.7941 | 13.4208 | 70 | 239.2148 | 335 | 0 | 8.9472 | 10.929
336 | 152.0412 | 6.5253 | 70.5922 | 229.1587 | 0 | 229.1587 | 229.1587 | 336 | 0 | 4.3502 | 10.929 | 336 | 56.4737 | 56.4737 | 54.2986 | 0 | 0 | 336 | 173.379 | 6.5253 | 49.2544 | 229.1587 | 0 | 229.1587 | 229.1587 | 336 | 0 | 4.3502 | 10.929 | 10.929 | 336 | 39.4035 | 17.0702 | 56.4737 | 54.2986 | 0 | 0 | 336 | 6.7873 | 6.7873 | 336 | 8.2484 | 9.5023 | 17.7507 | 336 | 6.6845 | 0 | 22.858 | 336 | 4.4563 | 68.0565 | 108.5194 | 336 | 126 | 0 | 86.0822 | 17.0765 | 0 | 229.1587 | 336 | 0 | 11.3843 | 10.929
337 | 114.5626 | 28.3108 | 79.4259 | 222.2993 | 0 | 222.2993 | 222.2993 | 337 | 0 | 18.8739 | 10.929 | 337 | 63.5408 | 63.5408 | 54.1038 | 0 | 0 | 337 | 118.7095 | 28.3108 | 75.279 | 222.2993 | 0 | 222.2993 | 222.2993 | 337 | 0 | 18.8739 | 10.929 | 10.929 | 337 | 60.2232 | 3.3175 | 63.5408 | 54.1038 | 0 | 0 | 337 | 6.763 | 6.763 | 337 | 7.4537 | 9.4682 | 16.9219 | 337 | 51.0882 | 0 | 51.0882 | 337 | 34.0588 | 70.5964 | 104.6552 | 337 | 114 | 30 | 36.8191 | 21.4802 | 20 | 222.2993 | 337 | 0 | 14.3201 | 10.929
338 | 109.2199 | 8.1967 | 84.4369 | 201.8535 | 0 | 201.8535 | 201.8535 | 338 | 0 | 5.4645 | 10.929 | 338 | 67.5495 | 67.5495 | 64.8173 | 0 | 0 | 338 | 146.7329 | 8.1967 | 46.9239 | 201.8535 | 0 | 201.8535 | 201.8535 | 338 | 0 | 5.4645 | 10.929 | 10.929 | 338 | 37.5391 | 30.0104 | 67.5495 | 64.8173 | 0 | 0 | 338 | 8.1022 | 8.1022 | 338 | 5.7312 | 11.343 | 17.0743 | 338 | 57.2769 | 0 | 57.2769 | 338 | 38.1846 | 53.8293 | 92.0139 | 338 | 132 | 6 | 53.2299 | 10.6236 | 0 | 201.8535 | 338 | 0 | 7.0824 | 10.929
339 | 86.9109 | 25.2732 | 93.7804 | 205.9645 | 0 | 205.9645 | 205.9645 | 339 | 0 | 16.8488 | 10.929 | 339 | 75.0243 | 75.0243 | 66.5999 | 0 | 0 | 339 | 111.3618 | 25.2732 | 69.3295 | 205.9645 | 0 | 205.9645 | 205.9645 | 339 | 0 | 16.8488 | 10.929 | 10.929 | 339 | 55.4636 | 19.5607 | 75.0243 | 66.5999 | 0 | 0 | 339 | 8.325 | 8.325 | 339 | 7.3165 | 11.655 | 18.9714 | 339 | 27.4413 | 0 | 22.1082 | 339 | 18.2942 | 42.3257 | 49.3018 | 339 | 114 | 42 | 27.8013 | 22.1633 | 0 | 205.9645 | 339 | 0 | 14.7755 | 10.929
340 | 68.6069 | 8.1967 | 88.7178 | 165.5214 | 0 | 165.5214 | 165.5214 | 340 | 0 | 5.4645 | 10.929 | 340 | 70.9742 | 70.9742 | 68.242 | 0 | 0 | 340 | 76.5729 | 8.1967 | 80.7518 | 165.5214 | 0 | 165.5214 | 165.5214 | 340 | 0 | 5.4645 | 10.929 | 10.929 | 340 | 64.6014 | 6.3728 | 70.9742 | 68.242 | 0 | 0 | 340 | 8.5302 | 8.5302 | 340 | 8.0463 | 11.9423 | 19.9887 | 340 | 16.5847 | 0 | 21.9178 | 340 | 11.0565 | 0 | 18.4472 | 340 | 126 | 0 | 28.8977 | 10.6236 | 0 | 165.5214 | 340 | 0 | 7.0824 | 10.929
341 | 36.6071 | 23.224 | 94.2426 | 154.0738 | 0 | 154.0738 | 154.0738 | 341 | 0 | 15.4827 | 10.929 | 341 | 75.3941 | 75.3941 | 67.6528 | 0 | 0 | 341 | 39.6534 | 23.224 | 91.1963 | 154.0738 | 0 | 154.0738 | 154.0738 | 341 | 0 | 15.4827 | 10.929 | 10.929 | 341 | 72.9571 | 2.437 | 75.3941 | 67.6528 | 0 | 0 | 341 | 8.4566 | 8.4566 | 341 | 9.4786 | 11.8392 | 21.3178 | 341 | 21.9178 | 0 | 21.9178 | 341 | 14.6119 | 33.7295 | 52.2689 | 341 | 120 | 24 | 5.7738 | 16.3934 | 0 | 154.0738 | 341 | 0 | 10.929 | 10.929
342 | 80.7154 | 7.8914 | 83.1013 | 171.708 | 0 | 171.708 | 171.708 | 342 | 0 | 5.2609 | 10.929 | 342 | 66.481 | 66.481 | 63.8505 | 0 | 0 | 342 | 87.6469 | 7.8914 | 76.1697 | 171.708 | 0 | 171.708 | 171.708 | 342 | 0 | 5.2609 | 10.929 | 10.929 | 342 | 60.9358 | 5.5452 | 66.481 | 63.8505 | 0 | 0 | 342 | 7.9813 | 7.9813 | 342 | 8.3231 | 11.1738 | 19.497 | 342 | 28.429 | 0 | 21.9178 | 342 | 18.9527 | 51.2971 | 70.2498 | 342 | 114 | 108 | 0 | 22.8463 | 0 | 171.708 | 342 | 0 | 15.2309 | 10.929
343 | 109.801 | 13.6612 | 75.9822 | 199.4444 | 0 | 199.4444 | 199.4444 | 343 | 0 | 9.1075 | 10.929 | 343 | 60.7858 | 60.7858 | 56.232 | 0 | 0 | 343 | 113.0582 | 13.6612 | 72.725 | 199.4444 | 0 | 199.4444 | 199.4444 | 343 | 0 | 9.1075 | 10.929 | 10.929 | 343 | 58.18 | 2.6058 | 60.7858 | 56.232 | 0 | 0 | 343 | 7.029 | 7.029 | 343 | 9.29 | 9.8406 | 19.1306 | 343 | 25.3059 | 0 | 25.2026 | 343 | 16.8706 | 62.9062 | 73.6006 | 343 | 108 | 42 | 0 | 15.7104 | 0 | 199.4444 | 343 | 0 | 10.4736 | 10.929
344 | 104.7929 | 25.5786 | 79.9399 | 210.3113 | 0 | 210.3113 | 210.3113 | 344 | 0 | 17.0524 | 10.929 | 344 | 63.9519 | 63.9519 | 55.4257 | 0 | 0 | 344 | 109.2929 | 25.5786 | 75.4398 | 210.3113 | 0 | 210.3113 | 210.3113 | 344 | 0 | 17.0524 | 10.929 | 10.929 | 344 | 60.3518 | 3.6 | 63.9519 | 55.4257 | 0 | 0 | 344 | 6.9282 | 6.9282 | 344 | 10.4871 | 9.6995 | 20.1866 | 344 | 93.6179 | 0 | 92.2671 | 344 | 62.412 | 15.9085 | 74.9518 | 344 | 114 | 12 | 17.1134 | 15.7001 | 0 | 210.3113 | 344 | 0 | 10.4668 | 10.929
345 | 123.5897 | 18.4426 | 90.3749 | 232.4072 | 0 | 232.4072 | 232.4072 | 345 | 0 | 12.2951 | 10.929 | 345 | 72.2999 | 72.2999 | 66.1524 | 0 | 0 | 345 | 128.6017 | 18.4426 | 85.3629 | 232.4072 | 0 | 232.4072 | 232.4072 | 345 | 0 | 12.2951 | 10.929 | 10.929 | 345 | 68.2903 | 4.0096 | 72.2999 | 66.1524 | 0 | 0 | 345 | 8.269 | 8.269 | 345 | 11.6996 | 11.5767 | 23.2763 | 345 | 128.909 | 32.2998 | 169.1741 | 345 | 85.9393 | 0 | 68.1853 | 345 | 132 | 6 | 61.9022 | 12 | 50 | 232.4072 | 345 | 0 | 8 | 10.929
346 | 152.0654 | 6 | 85.9677 | 244.0331 | 0 | 244.0331 | 244.0331 | 346 | 0 | 4 | 10.929 | 346 | 68.7742 | 68.7742 | 66.7742 | 0 | 0 | 346 | 153.3325 | 6 | 84.7006 | 244.0331 | 0 | 244.0331 | 244.0331 | 346 | 0 | 4 | 10.929 | 10.929 | 346 | 67.7605 | 1.0137 | 68.7742 | 66.7742 | 0 | 0 | 346 | 8.3468 | 8.3468 | 346 | 13.3304 | 11.6855 | 25.0159 | 346 | 85.7332 | 0 | 85.7332 | 346 | 57.1555 | 0 | 83.7017 | 346 | 126 | 42 | 0 | 18 | 100 | 244.0331 | 346 | 0 | 12 | 10.929
347 | 125.6491 | 15.5526 | 95.6558 | 236.8575 | 0 | 236.8575 | 236.8575 | 347 | 0 | 10.3684 | 10.929 | 347 | 76.5246 | 76.5246 | 71.3405 | 0 | 0 | 347 | 125.9102 | 15.5526 | 95.3947 | 236.8575 | 0 | 236.8575 | 236.8575 | 347 | 0 | 10.3684 | 10.929 | 10.929 | 347 | 76.3158 | 0.20889 | 76.5246 | 71.3405 | 0 | 0 | 347 | 8.9176 | 8.9176 | 347 | 8.2426 | 12.4846 | 20.7272 | 347 | 46.1372 | 0 | 46.1372 | 347 | 30.7581 | 70.8032 | 86.9607 | 347 | 102 | 42 | 0 | 19.8736 | 30 | 236.8575 | 347 | 0 | 13.2491 | 10.929
348 | 101.2455 | 26.2616 | 92.8948 | 220.4019 | 0 | 220.4019 | 220.4019 | 348 | 0 | 17.5077 | 10.929 | 348 | 74.3158 | 74.3158 | 65.562 | 0 | 0 | 348 | 122.098 | 26.2616 | 72.0423 | 220.4019 | 0 | 220.4019 | 220.4019 | 348 | 0 | 17.5077 | 10.929 | 10.929 | 348 | 57.6338 | 16.682 | 74.3158 | 65.562 | 0 | 0 | 348 | 8.1952 | 8.1952 | 348 | 7.8085 | 11.4733 | 19.2818 | 348 | 38.794 | 0 | 38.794 | 348 | 25.8627 | 53.899 | 87.2633 | 348 | 120 | 0 | 56.2135 | 15.7104 | 0 | 220.4019 | 348 | 0 | 10.4736 | 10.929
349 | 123.9761 | 8.5745 | 83.0446 | 215.5952 | 0 | 215.5952 | 215.5952 | 349 | 0 | 5.7163 | 10.929 | 349 | 66.4357 | 66.4357 | 63.5776 | 0 | 0 | 349 | 148.0501 | 8.5745 | 58.9707 | 215.5952 | 0 | 215.5952 | 215.5952 | 349 | 0 | 5.7163 | 10.929 | 10.929 | 349 | 47.1765 | 19.2592 | 66.4357 | 63.5776 | 0 | 0 | 349 | 7.9472 | 7.9472 | 349 | 9.4183 | 11.1261 | 20.5443 | 349 | 36.4851 | 0 | 36.4851 | 349 | 24.3234 | 56.3317 | 80.2482 | 349 | 132 | 0 | 71.6055 | 11.9898 | 0 | 215.5952 | 349 | 0 | 7.9932 | 10.929
350 | 124.5453 | 15.0273 | 76.2009 | 215.7735 | 0 | 215.7735 | 215.7735 | 350 | 0 | 10.0182 | 10.929 | 350 | 60.9607 | 60.9607 | 55.9516 | 0 | 0 | 350 | 135.1079 | 15.0273 | 65.6382 | 215.7735 | 0 | 215.7735 | 215.7735 | 350 | 0 | 10.0182 | 10.929 | 10.929 | 350 | 52.5106 | 8.4501 | 60.9607 | 55.9516 | 0 | 0 | 350 | 6.9939 | 6.9939 | 350 | 14.9576 | 9.7915 | 24.7491 | 350 | 50.6835 | 0 | 50.6835 | 350 | 33.789 | 57.2497 | 91.6248 | 350 | 120 | 0 | 79.38 | 16.3934 | 0 | 215.7735 | 350 | 0 | 10.929 | 10.929
351 | 142.2064 | 17.972 | 76.5814 | 236.7597 | 0 | 236.7597 | 236.7597 | 351 | 0 | 11.9813 | 10.929 | 351 | 61.2651 | 61.2651 | 55.2744 | 0 | 0 | 351 | 150.4569 | 17.972 | 68.3308 | 236.7597 | 0 | 236.7597 | 236.7597 | 351 | 0 | 11.9813 | 10.929 | 10.929 | 351 | 54.6646 | 6.6004 | 61.2651 | 55.2744 | 0 | 0 | 351 | 6.9093 | 6.9093 | 351 | 16.9902 | 9.673 | 26.6633 | 351 | 28.7029 | 0 | 23.4055 | 351 | 19.1352 | 64.3003 | 88.1875 | 351 | 84 | 0 | 61.2795 | 21.4802 | 70 | 236.7597 | 351 | 0 | 14.3201 | 10.929
352 | 132.2897 | 24.6831 | 92.2178 | 249.1905 | 0 | 249.1905 | 249.1905 | 352 | 0 | 16.4554 | 10.929 | 352 | 73.7742 | 73.7742 | 65.5465 | 0 | 0 | 352 | 135.7642 | 24.6831 | 88.7433 | 249.1905 | 0 | 249.1905 | 249.1905 | 352 | 0 | 16.4554 | 10.929 | 10.929 | 352 | 70.9946 | 2.7796 | 73.7742 | 65.5465 | 0 | 0 | 352 | 8.1933 | 8.1933 | 352 | 12.5972 | 11.4706 | 24.0678 | 352 | 17.5337 | 0 | 21.9178 | 352 | 11.6891 | 50.0086 | 64.6183 | 352 | 66 | 0 | 7.0055 | 11.3067 | 190 | 249.1905 | 352 | 0 | 7.5378 | 10.929
353 | 130.2212 | 15.0273 | 87.1185 | 232.367 | 0 | 232.367 | 232.367 | 353 | 0 | 10.0182 | 10.929 | 353 | 69.6948 | 69.6948 | 64.6857 | 0 | 0 | 353 | 158.2186 | 15.0273 | 59.1211 | 232.367 | 0 | 232.367 | 232.367 | 353 | 0 | 10.0182 | 10.929 | 10.929 | 353 | 47.2969 | 22.3979 | 69.6948 | 64.6857 | 0 | 0 | 353 | 8.0857 | 8.0857 | 353 | 16.1314 | 11.32 | 27.4514 | 353 | 34.4244 | 0 | 22.0606 | 353 | 22.9496 | 11.9209 | 29.5535 | 353 | 72 | 0 | 89.5349 | 15.7104 | 30 | 232.367 | 353 | 0 | 10.4736 | 10.929
354 | 110.991 | 17.0765 | 86.7228 | 214.7903 | 0 | 214.7903 | 214.7903 | 354 | 0 | 11.3843 | 10.929 | 354 | 69.3782 | 69.3782 | 63.6861 | 0 | 0 | 354 | 121.8643 | 17.0765 | 75.8495 | 214.7903 | 0 | 214.7903 | 214.7903 | 354 | 0 | 11.3843 | 10.929 | 10.929 | 354 | 60.6796 | 8.6987 | 69.3782 | 63.6861 | 0 | 0 | 354 | 7.9608 | 7.9608 | 354 | 14.8519 | 11.1451 | 25.997 | 354 | 12.6278 | 0 | 25.9048 | 354 | 8.4185 | 28.2863 | 26.0946 | 354 | 114 | 0 | 83.7138 | 17.0765 | 0 | 214.7903 | 354 | 0 | 11.3843 | 10.929
355 | 91.3386 | 19.1257 | 85.0876 | 195.5519 | 0 | 195.5519 | 195.5519 | 355 | 0 | 12.7505 | 10.929 | 355 | 68.0701 | 68.0701 | 61.6949 | 0 | 0 | 355 | 114.3353 | 19.1257 | 62.0909 | 195.5519 | 0 | 195.5519 | 195.5519 | 355 | 0 | 12.7505 | 10.929 | 10.929 | 355 | 49.6727 | 18.3974 | 68.0701 | 61.6949 | 0 | 0 | 355 | 7.7119 | 7.7119 | 355 | 11.9489 | 10.7966 | 22.7455 | 355 | 22.8311 | 0 | 21.9178 | 355 | 15.2207 | 0 | 31.1479 | 355 | 120 | 0 | 59.1584 | 16.3934 | 0 | 195.5519 | 355 | 0 | 10.929 | 10.929
356 | 91.2443 | 14.3443 | 78.6538 | 184.2423 | 0 | 184.2423 | 184.2423 | 356 | 0 | 9.5628 | 10.929 | 356 | 62.923 | 62.923 | 58.1416 | 0 | 0 | 356 | 126.9654 | 14.3443 | 42.9326 | 184.2423 | 0 | 184.2423 | 184.2423 | 356 | 0 | 9.5628 | 10.929 | 10.929 | 356 | 34.3461 | 28.5769 | 62.923 | 58.1416 | 0 | 0 | 356 | 7.2677 | 7.2677 | 356 | 11.1111 | 10.1748 | 21.2858 | 356 | 23.8371 | 0 | 24.7503 | 356 | 15.8914 | 10.8464 | 26.7378 | 356 | 108 | 59.5403 | 0.99159 | 15.7104 | 0 | 184.2423 | 356 | 0 | 10.4736 | 10.929
357 | 108.1558 | 8.5745 | 76.355 | 193.0853 | 0 | 193.0853 | 193.0853 | 357 | 0 | 5.7163 | 10.929 | 357 | 61.084 | 61.084 | 58.2259 | 0 | 0 | 357 | 128.2493 | 8.5745 | 56.2615 | 193.0853 | 0 | 193.0853 | 193.0853 | 357 | 0 | 5.7163 | 10.929 | 10.929 | 357 | 45.0092 | 16.0748 | 61.084 | 58.2259 | 0 | 0 | 357 | 7.2782 | 7.2782 | 357 | 12.0187 | 10.1895 | 22.2083 | 357 | 58.2885 | 8.2861 | 58.5385 | 357 | 38.859 | 0 | 16.3934 | 357 | 113.4644 | 114 | 0 | 23.5191 | 0 | 193.0853 | 357 | 0 | 15.6794 | 10.929
358 | 64.1744 | 25.9563 | 78.7044 | 156.7416 | 0 | 156.7416 | 156.7416 | 358 | 0 | 17.3042 | 10.929 | 358 | 62.9635 | 62.9635 | 54.3114 | 0 | 0 | 358 | 67.8557 | 25.1732 | 71.1107 | 156.7416 | 0 | 156.7416 | 156.7416 | 358 | 0 | 16.7822 | 10.929 | 10.929 | 358 | 56.8886 | 5.814 | 62.7025 | 54.3114 | 0 | 0 | 358 | 6.7889 | 6.7889 | 358 | 15.3191 | 9.5045 | 24.8236 | 358 | 38.0976 | 90.0378 | 136.1714 | 358 | 25.3984 | 0 | 24.8191 | 358 | 84.0265 | 60 | 0 | 12 | 0 | 156.7416 | 358 | 0 | 8 | 10.929
359 | 75.107 | 0 | 63.5098 | 150.7102 | 0 | 150.7102 | 150.7102 | 359 | 0 | 0 | 10.929 | 359 | 50.8078 | 50.8078 | 50.8078 | 0 | 0 | 359 | 103.3716 | 0.78304 | 39.1575 | 150.7102 | 0 | 150.7102 | 150.7102 | 359 | 0 | 0.52203 | 10.929 | 10.929 | 359 | 31.326 | 19.7428 | 51.0688 | 50.8078 | 0 | 0 | 359 | 6.351 | 6.351 | 359 | 16.3216 | 8.8914 | 25.213 | 359 | 93.3898 | 50.0772 | 143.467 | 359 | 62.2599 | 0 | 50.6637 | 359 | 54 | 113.3157 | 0 | 28.9939 | 0 | 150.7102 | 359 | 0 | 19.3292 | 10.929
360 | 52.6897 | 31.043 | 80.196 | 163.9287 | 0 | 163.9287 | 163.9287 | 360 | 0 | 20.6954 | 10.929 | 360 | 64.1568 | 64.1568 | 53.8091 | 0 | 0 | 360 | 73.2488 | 31.043 | 59.6368 | 163.9287 | 0 | 163.9287 | 163.9287 | 360 | 0 | 20.6954 | 10.929 | 10.929 | 360 | 47.7095 | 16.4473 | 64.1568 | 53.8091 | 0 | 0 | 360 | 6.7261 | 6.7261 | 360 | 18.3741 | 9.4166 | 27.7907 | 360 | 53.8934 | 78.3506 | 132.244 | 360 | 35.9289 | 0 | 58.0031 | 360 | 120 | 16.9878 | 0 | 7.5137 | 0 | 163.9287 | 360 | 0 | 5.0091 | 10.929
361 | 102.4895 | 16.3934 | 74.3691 | 193.252 | 0 | 193.252 | 193.252 | 361 | 0 | 10.929 | 10.929 | 361 | 59.4953 | 59.4953 | 54.0308 | 0 | 0 | 361 | 107.457 | 16.3934 | 69.4016 | 193.252 | 0 | 193.252 | 193.252 | 361 | 0 | 10.929 | 10.929 | 10.929 | 361 | 55.5213 | 3.974 | 59.4953 | 54.0308 | 0 | 0 | 361 | 6.7539 | 6.7539 | 361 | 16.1127 | 9.4554 | 25.5681 | 361 | 89.1784 | 59.1853 | 143.0386 | 361 | 59.4523 | 0 | 60.9486 | 361 | 120 | 6 | 0 | 14.5745 | 0 | 193.252 | 361 | 0 | 9.7163 | 10.929
362 | 111.3248 | 17.0765 | 74.9183 | 203.3197 | 0 | 203.3197 | 203.3197 | 362 | 0 | 11.3843 | 10.929 | 362 | 59.9347 | 59.9347 | 54.2425 | 0 | 0 | 362 | 114.6611 | 17.0765 | 71.5821 | 203.3197 | 0 | 203.3197 | 203.3197 | 362 | 0 | 11.3843 | 10.929 | 10.929 | 362 | 57.2656 | 2.669 | 59.9347 | 54.2425 | 0 | 0 | 362 | 6.7803 | 6.7803 | 362 | 14.6153 | 9.4924 | 24.1077 | 362 | 95.6136 | 83.3258 | 182.8369 | 362 | 63.7424 | 0 | 59.6947 | 362 | 120 | 12 | 17.7958 | 22.8463 | 0 | 203.3197 | 362 | 0 | 15.2309 | 10.929
363 | 121.6326 | 12.6728 | 72.6308 | 206.9362 | 0 | 206.9362 | 206.9362 | 363 | 0 | 8.4485 | 10.929 | 363 | 58.1047 | 58.1047 | 53.8804 | 0 | 0 | 363 | 137.5575 | 12.6728 | 56.7059 | 206.9362 | 0 | 206.9362 | 206.9362 | 363 | 0 | 8.4485 | 10.929 | 10.929 | 363 | 45.3647 | 12.7399 | 58.1047 | 53.8804 | 0 | 0 | 363 | 6.735 | 6.735 | 363 | 14.0816 | 9.4291 | 23.5107 | 363 | 84.4626 | 96.8567 | 167.9958 | 363 | 56.3084 | 0 | 53.8037 | 363 | 120 | 18 | 59.4132 | 15.9406 | 0 | 206.9362 | 363 | 0 | 10.627 | 10.929
364 | 141.4995 | 4.0984 | 66.7373 | 212.3352 | 0 | 212.3352 | 212.3352 | 364 | 0 | 2.7322 | 10.929 | 364 | 53.3898 | 53.3898 | 52.0237 | 0 | 0 | 364 | 145.1173 | 4.0984 | 63.1195 | 212.3352 | 0 | 212.3352 | 212.3352 | 364 | 0 | 2.7322 | 10.929 | 10.929 | 364 | 50.4956 | 2.8942 | 53.3898 | 52.0237 | 0 | 0 | 364 | 6.503 | 6.503 | 364 | 15.0457 | 9.1041 | 24.1499 | 364 | 95.3751 | 0 | 89.2679 | 364 | 63.5834 | 0 | 44.7781 | 364 | 120 | 36 | 32.3931 | 22.153 | 0 | 212.3352 | 364 | 0 | 14.7687 | 10.929

## 19. Database output
19. Database output
In this tab are the outputs from the database to the subsequent energy system model available.
List of contents
19. Database output
19.1 Extraction of data from the database
19.2 Converted to local currency
19.1 Extraction of data from the database
| Technology | Reference | Electric capacity | Thermal capacity | Solar thermal size | Thermal storage size | Cooling storage capacity | Electric storage capacity | Electric storage energy | Fuel | Investment (el) (eqiupment) | Investment (el) (installation) | Investment (heat) (equipment) | Investment (heat) (installation) | Investment (solar) | Investment (thermal storage) | Investment (cooling storage) | Fixed O&M (el) | Fixed O&M (heat) | Fixed O&M (solar) | Fixed O&M (thermal storage) | Var. O&M (el) | Var. O&M (heat) | Lifetime | CV | CB | Electric efficiency CHP | Heat efficiency CHP | Electric efficiency condensing | Heat efficiency | CO2 capture rate (amount of emission) | Storage efficiency | SO2 (degree of desulphuring) | Emission factor SO2 | Emission factor NOX | Emission factor CH4 | Emission factor N2O | Emission factor PM2.5
| Description |  | The base thermal output capacity applied for the assumptions. | The base electrical output capacity applied for the assumptions. | The base solar field in m2 panels applied for the assumptions. | The base size in m3 thermal storage applied for the assumptions. | The capacity of the ATES storage | The dis-/charge capacity of the electric storage unit | The energy storage capacity of the electric storage unit | --- | The investment cost of the installation for units producing electricity | The investment cost of the equipment for units producing electricity | The investment cost of the installation for units producing heat | The investment cost of the equipment for units producing heat | Investment costs for solar thermal plants | Investment cost for thermal storage | Investment cost for the ATES storage | Fixed O&M costs for units producing electricity | Fixed O&M costs for units producing heat | Fixed O&M costs for solar thermal | Fixed O&M costs for thermal storage | Var. O&M costs for units producing electricity | Var. O&M costs for units producing heat | --- | Extraction plant coefficient | Backpressure plant coefficient | The electrical efficiency of a CHP plant | The thermal efficiency of a CHP plant | The electric efficiency in condensing mode (no heat) | The thermal efficiency of plants only producing heat | CO2 capture rate in the fluw gas, if carbon capture is included | Effiency of storges | --- | --- | --- | --- | --- | ---
|  |  | MW-e | MW-h | m2 panel | m3 storage | MW-c | MW-e | MWh-e |  | mil. EUR/MW-el | mil. EUR/MW-el | mil. EUR/MW-heat | mil. EUR/MW-heat | EUR/m2 panel | EUR/m3 storage | M€/drill hole pair | EUR/MW-el/year | EUR/MW-heat/year | EUR/m2 panel/year | EUR/m3 storage/year | EUR/MWh-el | EUR/MWh-heat | year |  |  | MW-el/MW-fuel | MW-heat/MW-fuel | MW-el/MW-fuel | MW-heat/MW-fuel | % | % | % | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f
Storages | ATES | [1] | --- | --- | --- | --- | 5 | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0.5 | --- | --- | --- | --- | --- | --- | 50 | --- | --- | --- | --- | --- | --- | --- | 100% | --- | --- | --- | --- | --- | ---
| Pumped hydro | [1] | --- | --- | --- | --- | --- | 500 | --- | --- | 4.6 | --- | --- | --- | --- | --- | --- | 9000 | --- | --- | --- | --- | --- | 50 | --- | --- | --- | --- | --- | --- | --- | 75% | --- | --- | --- | --- | --- | ---
| NaS battery | [1] | --- | --- | --- | --- | --- | 10 | 100 | --- | 1.7 | --- | --- | --- | --- | --- | --- | 51000 | --- | --- | --- | 5.3 | --- | 15 | --- | --- | --- | --- | --- | --- | --- | 60% | --- | --- | --- | --- | --- | ---
| Tank thermal storage | Ramboll | --- | --- | --- | 3000 | --- | --- | --- | --- | --- | --- | --- | --- | --- | 175 | --- | --- | --- | --- | 0.5 | --- | --- | 40 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| Pit thermal storage | Ramboll | --- | --- | --- | 120000 | --- | --- | --- | --- | --- | --- | --- | --- | --- | 50 | --- | --- | --- | --- | 0.2 | --- | --- | 20 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Boilers | Boiler - wood chips | [1] | --- | 7 | --- | --- | --- | --- | --- | Wood chips | --- | --- | 0.4 | 0.29 | --- | --- | --- | --- | 32200 | --- | --- | --- | 1 | 25 | --- | --- | --- | --- | --- | 1.15 | 0% | --- | 0.98 | --- | 226.8 | 39.6 | 10.8 | 1.08
| Boiler - wood pellets | [1] | --- | 6 | --- | --- | --- | --- | --- | Wood pellets | --- | --- | 0.44 | 0.28 | --- | --- | --- | --- | 33000 | --- | --- | --- | 0.5 | 25 | --- | --- | --- | --- | --- | 1 | 0% | --- | 0.983 | --- | 194.4 | 0 | 3.6 | 1.08
| Boiler - straw | [1] | --- | 6 | --- | --- | --- | --- | --- | Straw | --- | --- | 0.43 | 0.46 | --- | --- | --- | --- | 51300 | --- | --- | --- | 0.6 | 25 | --- | --- | --- | --- | --- | 1.02 | 0% | --- | 0.964 | --- | 259.2 | 39.6 | 10.8 | 1.08
| Boiler - natural gas | [1] | --- | 5.3 | --- | --- | --- | --- | --- | Natural gas | --- | --- | 0.04 | 0.02 | --- | --- | --- | --- | 1950 | --- | --- | --- | 1.1 | 25 | --- | --- | --- | --- | --- | 1.03 | 0% | --- | --- | 1.08 | 32.4 | 10.8 | 3.6 | 0
| Boiler - oil | [1] | --- | 5 | --- | --- | --- | --- | --- | Oil | --- | --- | 0.04 | 0.02 | --- | --- | --- | --- | 1950 | --- | --- | --- | 1.1 | 25 | --- | --- | --- | --- | --- | 1.03 | 0% | --- | --- | 1.8 | 90 | 0 | 0 | 0.72
| Electric boiler | [1] | --- | 5 | --- | --- | --- | --- | --- | Electricity | --- | --- | 0.12 | 0.03 | --- | --- | --- | --- | 1070 | --- | --- | --- | 0.9 | 20 | --- | --- | --- | --- | --- | 1 | 0% | --- | --- | --- | --- | --- | --- | ---
| Boiler - coal | [1] | --- | 5 | --- | --- | --- | --- | --- | Coal | --- | --- | 0.04 | 0.02 | --- | --- | --- | --- | 2140 | --- | --- | --- | 1.6 | 20 | --- | --- | --- | --- | --- | 0.9 | 0% | --- | --- | 18 | 126 | 5.4 | 2.88 | 1.8
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
CHP's | Small CHP - waste | [1] | 8 | 30 | --- | --- | --- | --- | --- | Waste | 6.5 | 4 | --- | --- | --- | --- | --- | 413600 | --- | --- | --- | 25.6 | --- | 25 | 1 | 0.26582 | 0.21 | 0.79 | --- | --- | 0% | --- | 0.998 | --- | 241.2 | 0.36 | 3.6 | 1.08
| Medium CHP - waste | [1] | 18 | 64 | --- | --- | --- | --- | --- | Waste | 5.5 | 3.6 | --- | --- | --- | --- | --- | 264800 | --- | --- | --- | 25 | --- | 25 | 1 | 0.28205 | 0.22 | 0.78 | --- | --- | 0% | --- | 0.998 | --- | 201.6 | 0.36 | 3.6 | 1.08
| Large CHP - waste | [1] | 51 | 173 | --- | --- | --- | --- | --- | Waste | 4.7 | 3.1 | --- | --- | --- | --- | --- | 188300 | --- | --- | --- | 24.8 | --- | 25 | 1 | 0.29487 | 0.23 | 0.78 | --- | --- | 0% | --- | 0.998 | --- | 201.6 | 0.36 | 3.6 | 1.08
| Boiler - waste | [1] | --- | 37 | --- | --- | --- | --- | --- | Waste | --- | --- | 1.05 | 0.78 | --- | --- | --- | --- | 78600 | --- | --- | --- | 5.5 | 25 | --- | --- | --- | --- | --- | 1.05 | 0% | --- | 0.998 | --- | 241.2 | 0.36 | 3.6 | 1.08
| Small CHP - wood chips | [1] | 3 | 21 | --- | --- | --- | --- | --- | Wood chips | 4 | 2.5 | --- | --- | --- | --- | --- | 288900 | --- | --- | --- | 7.8 | --- | 25 | 1 | 0.14433 | 0.14 | 0.97 | --- | --- | 0% | --- | 0.98 | --- | 226.8 | 39.6 | 3.6 | 1.08
| Medium CHP - wood chips | [1] | 23 | 65 | --- | --- | --- | --- | --- | Wood chips | 2.4 | 1.2 | --- | --- | --- | --- | --- | 153600 | --- | --- | --- | 3.8 | --- | 25 | 1 | 0.35366 | 0.29 | 0.82 | --- | --- | 0% | --- | 0.98 | --- | 259.2 | 7.2 | 3.6 | 1.08
| Large CHP - wood chips | [1] | 177 | 484 | --- | --- | --- | --- | --- | Wood chips | 2.2 | 1.2 | --- | --- | --- | --- | --- | 97600 | --- | --- | --- | 3.8 | --- | 25 | 1 | 0.36585 | 0.3 | 0.82 | --- | --- | 0% | --- | 0.98 | --- | 86.4 | 7.2 | 28.8 | 1.08
| Small CHP - wood pellets | [1] | 3 | 16 | --- | --- | --- | --- | --- | Wood pellets | 4 | 2.2 | --- | --- | --- | --- | --- | 275900 | --- | --- | --- | 3.4 | --- | 25 | 1 | 0.18293 | 0.15 | 0.82 | --- | --- | 0% | --- | 0.983 | --- | 194.4 | 0 | 3.6 | 1.08
| Medium CHP - wood pellets | [1] | 24 | 54 | --- | --- | --- | --- | --- | Wood pellets | 2 | 1.1 | --- | --- | --- | --- | --- | 127100 | --- | --- | --- | 1.7 | --- | 25 | 1 | 0.44776 | 0.3 | 0.67 | --- | --- | 0% | --- | 0.983 | --- | 223.2 | 0 | 3.6 | 1.08
| Large CHP - wood pellets | [1] | 261 | 522 | --- | --- | --- | --- | --- | Wood pellets | 1.3 | 1 | --- | --- | --- | --- | --- | 64000 | --- | --- | --- | 1.6 | --- | 25 | 1 | 0.5 | 0.32 | 0.64 | --- | --- | 0% | --- | 0.983 | --- | 75.6 | 0 | 3.6 | 1.08
| Small CHP - straw | [1] | 3 | 17 | --- | --- | --- | --- | --- | Straw | 3.8 | 3 | --- | --- | --- | --- | --- | 318200 | --- | --- | --- | 4 | --- | 25 | 1 | 0.17857 | 0.15 | 0.84 | --- | --- | 0% | --- | 0.964 | --- | 259.2 | 39.6 | 3.6 | 1.08
| Medium CHP - straw | [1] | 24 | 53 | --- | --- | --- | --- | --- | Straw | 2.3 | 1.5 | --- | --- | --- | --- | --- | 149900 | --- | --- | --- | 2 | --- | 25 | 1 | 0.45588 | 0.31 | 0.68 | --- | --- | 0% | --- | 0.964 | --- | 252 | 0 | 3.6 | 1.08
| Large CHP - straw | [1] | 41 | 90 | --- | --- | --- | --- | --- | Straw | 2.1 | 1.3 | --- | --- | --- | --- | --- | 124900 | --- | --- | --- | 1.9 | --- | 25 | 1 | 0.45588 | 0.31 | 0.68 | --- | --- | 0% | --- | 0.964 | --- | 241.2 | 0 | 3.6 | 1.08
| Large CHP - coal | [1] | 550 | 655 | --- | --- | --- | --- | --- | Coal | 1.9 | --- | --- | --- | --- | --- | --- | 31000 | --- | --- | --- | 2.9 | --- | 25 | 0.15 | 0.84 | 0.42 | 0.5 | 0.49 | --- | 0% | --- | 0.97 | --- | 126 | 5.4 | 2.88 | 0
| Medium CHP - natural gas SC | [1] | 27.5 | 38 | --- | --- | --- | --- | --- | Natural gas | 0.73 | --- | --- | --- | --- | --- | --- | 18600 | --- | --- | --- | 5.1 | --- | 25 | --- | 0.72727 | 0.32 | 0.44 | 0.37 | --- | 0% | --- | 0 | --- | 54 | 5.4 | 3.6 | 0
| Large CHP - natural gas SC | [1] | 82.5 | 87 | --- | --- | --- | --- | --- | Natural gas | 0.59 | --- | --- | --- | --- | --- | --- | 29500 | --- | --- | --- | 4.5 | --- | 25 | --- | 0.94595 | 0.35 | 0.37 | 0.4 | --- | 0% | --- | 0 | --- | 54 | 5.4 | 3.6 | 0
| Medium CHP - natural gas CC | [1] | 55 | 42 | --- | --- | --- | --- | --- | Natural gas | 1 | 0.3 | --- | --- | --- | --- | --- | 29300 | --- | --- | --- | 4.4 | --- | 25 | --- | 1.3143 | 0.46 | 0.35 | 0.51 | --- | 0% | --- | 0 | --- | 54 | 5.4 | 3.6 | 0
| Large CHP - natural gas CC | [1] | 300 | 167 | --- | --- | --- | --- | --- | Natural gas | 0.68 | 0.2 | --- | --- | --- | --- | --- | 29300 | --- | --- | --- | 4.4 | --- | 25 | --- | 1.8 | 0.54 | 0.3 | 0.59 | --- | 0% | --- | 0 | --- | 54 | 5.4 | 3.6 | 0
| Engine - natural gas | [1] | 5.5 | 5.8 | --- | --- | --- | --- | --- | Natural gas | 0.6 | 0.35 | --- | --- | --- | --- | --- | 9750 | --- | --- | --- | 5.4 | --- | 25 | --- | 0.95455 | 0.42 | 0.44 | 0.47 | --- | 0% | --- | 0 | --- | 216 | 1134 | 2.16 | 0
| Large CHP - coal - carbon capture | Ramboll | 495 | 619 | --- | --- | --- | --- | --- | Coal | 3.52 | --- | --- | --- | --- | --- | --- | 65666 | --- | --- | --- | 2.9 | --- | 25 | 0.15 | 0.8 | 0.32 | 0.4 | 0.39 | --- | 90% | --- | 0.97 | --- | 126 | 5.4 | 2.88 | 0
| Large CHP - wood chips - carbon capture | Ramboll | 159 | 572 | --- | --- | --- | --- | --- | Wood chips | 5.3235 | 2.8665 | --- | --- | --- | --- | --- | 132266 | --- | --- | --- | 3.8 | --- | 25 | 1 | 0.27778 | 0.2 | 0.72 | --- | --- | 90% | --- | 0.98 | --- | 86.4 | 7.2 | 28.8 | 1.08
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
HP's | Electric heat pump | [1] | --- | 4 | --- | --- | --- | --- | --- | Electricity | --- | --- | 0.33 | 0.33 | --- | --- | --- | --- | 2000 | --- | --- | --- | 3.2 | 25 | --- | --- | --- | --- | --- | 3.6 | 0% | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
RE | Geothermal | [1] | --- | 10 | --- | --- | --- | --- | --- | Electricity | --- | --- | 1.95 | 0.65 | --- | --- | --- | --- | 20000 | --- | --- | --- | 3.5 | 25 | --- | --- | --- | --- | --- | 3.6 | 0% | --- | --- | --- | --- | --- | --- | ---
| Solar PV | [1] | 10 | --- | --- | --- | --- | --- | --- | Solar PV | 0.62 | --- | --- | --- | --- | --- | --- | 8100 | --- | --- | --- | --- | --- | 20 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| Solar - small | Ramboll | --- | --- | 2000 | --- | --- | --- | --- | Solar | --- | --- | --- | --- | 380 | --- | --- | --- | --- | 4 | --- | --- | --- | 30 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| Solar - medium | Ramboll | --- | --- | 10000 | --- | --- | --- | --- | Solar | --- | --- | --- | --- | 200 | --- | --- | --- | --- | 2 | --- | --- | --- | 30 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| Solar - large | Ramboll | --- | --- | 20000 | --- | --- | --- | --- | Solar | --- | --- | --- | --- | 190 | --- | --- | --- | --- | 2 | --- | --- | --- | 30 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| Large onshore wind turbine | [1] | 4.2 | --- | --- | --- | --- | --- | --- | --- | 0.71 | 0.41 | --- | --- | --- | --- | --- | 14000 | --- | --- | --- | 1.5 | --- | 27 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
19.2 Converted to local currency
| Country |  | EU
| Currency abbreviation |  | EUR
| Currency factor |  | 1
| Equipment |  | 1
| Installation |  | 1
| Technology | Reference | Electric capacity | Thermal capacity | Solar thermal size | Thermal storage size | Cooling storage capacity | Electric storage capacity | Electric storage energy | Fuel | Investment (el) (eqiupment) | Investment (el) (installation) | Investment (heat) (equipment) | Investment (heat) (installation) | Investment (solar) | Investment (thermal storage) | Investment (cooling storage) | Fixed O&M (el) | Fixed O&M (heat) | Fixed O&M (solar) | Fixed O&M (thermal storage) | Var. O&M (el) | Var. O&M (heat) | Lifetime | CV | CB | Electric efficiency CHP | Heat efficiency CHP | Electric efficiency condensing | Heat efficiency | CO2 capture rate (amount of emission) | Storage efficiency | SO2 (degree of desulphuring) | Emission factor SO2 | Emission factor NOX | Emission factor CH4 | Emission factor N2O | Emission factor PM2.5
| Description |  | The base thermal output capacity applied for the assumptions. | The base electrical output capacity applied for the assumptions. | The base solar field in m2 panels applied for the assumptions. | The base size in m3 thermal storage applied for the assumptions. | The capacity of the ATES storage | The dis-/charge capacity of the electric storage unit | The energy storage capacity of the electric storage unit | --- | The investment cost of the installation for units producing electricity | The investment cost of the equipment for units producing electricity | The investment cost of the installation for units producing heat | The investment cost of the equipment for units producing heat | Investment costs for solar thermal plants | Investment cost for thermal storage | Investment cost for the ATES storage | Fixed O&M costs for units producing electricity | Fixed O&M costs for units producing heat | Fixed O&M costs for solar thermal | Fixed O&M costs for thermal storage | Var. O&M costs for units producing electricity | Var. O&M costs for units producing heat | --- | Extraction plant coefficient | Backpressure plant coefficient | The electrical efficiency of a CHP plant | The thermal efficiency of a CHP plant | The electric efficiency in condensing mode (no heat) | The thermal efficiency of plants only producing heat | CO2 capture rate in the fluw gas, if carbon capture is included | Effiency of storges | --- | --- | --- | --- | --- | ---
|  |  | MW-e | MW-h | m2 panel | m3 storage | MW-c | MW-e | MWh-e |  | mil. EUR/MW-el | mil. EUR/MW-el | mil. EUR/MW-heat | mil. EUR/MW-heat | EUR/m2 panel | EUR/m3 storage | mil. EUR/drill hole pair | EUR/MW-el/year | EUR/MW-heat/year | EUR/m2 panel/year | EUR/m3 storage/year | EUR/MWh-el | EUR/MWh-heat | year |  |  | MW-el/MW-fuel | MW-heat/MW-fuel | MW-el/MW-fuel | MW-heat/MW-fuel | % | % | % | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f | g/MWh-f
Storages | ATES | [1] | --- | --- | --- | --- | 5 | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0.5 | --- | --- | --- | --- | --- | --- | 50 | --- | --- | --- | --- | --- | --- | --- | 100% | --- | --- | --- | --- | --- | ---
| Pumped hydro | [1] | --- | --- | --- | --- | --- | 500 | --- | --- | 4.6 | --- | --- | --- | --- | --- | --- | 9000 | --- | --- | --- | --- | --- | 50 | --- | --- | --- | --- | --- | --- | --- | 75% | --- | --- | --- | --- | --- | ---
| NaS battery | [1] | --- | --- | --- | --- | --- | 10 | 100 | --- | 1.7 | --- | --- | --- | --- | --- | --- | 51000 | --- | --- | --- | 5.3 | --- | 15 | --- | --- | --- | --- | --- | --- | --- | 60% | --- | --- | --- | --- | --- | ---
| Tank thermal storage | Ramboll | --- | --- | --- | 3000 | --- | --- | --- | --- | --- | --- | --- | --- | --- | 175 | --- | --- | --- | --- | 0.5 | --- | --- | 40 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| Pit thermal storage | Ramboll | --- | --- | --- | 120000 | --- | --- | --- | --- | --- | --- | --- | --- | --- | 50 | --- | --- | --- | --- | 0.2 | --- | --- | 20 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
Boilers | Boiler - wood chips | [1] | --- | 7 | --- | --- | --- | --- | --- | Wood chips | --- | --- | 0.4 | 0.29 | --- | --- | --- | --- | 32200 | --- | --- | --- | 1 | 25 | --- | --- | --- | --- | --- | 1.15 | 0% | --- | 0.98 | --- | 226.8 | 39.6 | 10.8 | 1.08
| Boiler - wood pellets | [1] | --- | 6 | --- | --- | --- | --- | --- | Wood pellets | --- | --- | 0.44 | 0.28 | --- | --- | --- | --- | 33000 | --- | --- | --- | 0.5 | 25 | --- | --- | --- | --- | --- | 1 | 0% | --- | 0.983 | --- | 194.4 | 0 | 3.6 | 1.08
| Boiler - straw | [1] | --- | 6 | --- | --- | --- | --- | --- | Straw | --- | --- | 0.43 | 0.46 | --- | --- | --- | --- | 51300 | --- | --- | --- | 0.6 | 25 | --- | --- | --- | --- | --- | 1.02 | 0% | --- | 0.964 | --- | 259.2 | 39.6 | 10.8 | 1.08
| Boiler - natural gas | [1] | --- | 5.3 | --- | --- | --- | --- | --- | Natural gas | --- | --- | 0.04 | 0.02 | --- | --- | --- | --- | 1950 | --- | --- | --- | 1.1 | 25 | --- | --- | --- | --- | --- | 1.03 | 0% | --- | --- | 1.08 | 32.4 | 10.8 | 3.6 | 0
| Boiler - oil | [1] | --- | 5 | --- | --- | --- | --- | --- | Oil | --- | --- | 0.04 | 0.02 | --- | --- | --- | --- | 1950 | --- | --- | --- | 1.1 | 25 | --- | --- | --- | --- | --- | 1.03 | 0% | --- | --- | 1.8 | 90 | 0 | 0 | 0.72
| Electric boiler | [1] | --- | 5 | --- | --- | --- | --- | --- | Electricity | --- | --- | 0.12 | 0.03 | --- | --- | --- | --- | 1070 | --- | --- | --- | 0.9 | 20 | --- | --- | --- | --- | --- | 1 | 0% | --- | --- | --- | --- | --- | --- | ---
| Boiler - coal | [1] | --- | 5 | --- | --- | --- | --- | --- | Coal | --- | --- | 0.04 | 0.02 | --- | --- | --- | --- | 2140 | --- | --- | --- | 1.6 | 20 | --- | --- | --- | --- | --- | 0.9 | 0% | --- | --- | 18 | 126 | 5.4 | 2.88 | 1.8
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
CHP's | Small CHP - waste | [1] | 8 | 30 | --- | --- | --- | --- | --- | Waste | 6.5 | 4 | --- | --- | --- | --- | --- | 413600 | --- | --- | --- | 25.6 | --- | 25 | 1 | 0.26582 | 0.21 | 0.79 | --- | --- | 0% | --- | 0.998 | --- | 241.2 | 0.36 | 3.6 | 1.08
| Medium CHP - waste | [1] | 18 | 64 | --- | --- | --- | --- | --- | Waste | 5.5 | 3.6 | --- | --- | --- | --- | --- | 264800 | --- | --- | --- | 25 | --- | 25 | 1 | 0.28205 | 0.22 | 0.78 | --- | --- | 0% | --- | 0.998 | --- | 201.6 | 0.36 | 3.6 | 1.08
| Large CHP - waste | [1] | 51 | 173 | --- | --- | --- | --- | --- | Waste | 4.7 | 3.1 | --- | --- | --- | --- | --- | 188300 | --- | --- | --- | 24.8 | --- | 25 | 1 | 0.29487 | 0.23 | 0.78 | --- | --- | 0% | --- | 0.998 | --- | 201.6 | 0.36 | 3.6 | 1.08
| Boiler - waste | [1] | --- | 37 | --- | --- | --- | --- | --- | Waste | --- | --- | 1.05 | 0.78 | --- | --- | --- | --- | 78600 | --- | --- | --- | 5.5 | 25 | --- | --- | --- | --- | --- | 1.05 | 0% | --- | 0.998 | --- | 241.2 | 0.36 | 3.6 | 1.08
| Small CHP - wood chips | [1] | 3 | 21 | --- | --- | --- | --- | --- | Wood chips | 4 | 2.5 | --- | --- | --- | --- | --- | 288900 | --- | --- | --- | 7.8 | --- | 25 | 1 | 0.14433 | 0.14 | 0.97 | --- | --- | 0% | --- | 0.98 | --- | 226.8 | 39.6 | 3.6 | 1.08
| Medium CHP - wood chips | [1] | 23 | 65 | --- | --- | --- | --- | --- | Wood chips | 2.4 | 1.2 | --- | --- | --- | --- | --- | 153600 | --- | --- | --- | 3.8 | --- | 25 | 1 | 0.35366 | 0.29 | 0.82 | --- | --- | 0% | --- | 0.98 | --- | 259.2 | 7.2 | 3.6 | 1.08
| Large CHP - wood chips | [1] | 177 | 484 | --- | --- | --- | --- | --- | Wood chips | 2.2 | 1.2 | --- | --- | --- | --- | --- | 97600 | --- | --- | --- | 3.8 | --- | 25 | 1 | 0.36585 | 0.3 | 0.82 | --- | --- | 0% | --- | 0.98 | --- | 86.4 | 7.2 | 28.8 | 1.08
| Small CHP - wood pellets | [1] | 3 | 16 | --- | --- | --- | --- | --- | Wood pellets | 4 | 2.2 | --- | --- | --- | --- | --- | 275900 | --- | --- | --- | 3.4 | --- | 25 | 1 | 0.18293 | 0.15 | 0.82 | --- | --- | 0% | --- | 0.983 | --- | 194.4 | 0 | 3.6 | 1.08
| Medium CHP - wood pellets | [1] | 24 | 54 | --- | --- | --- | --- | --- | Wood pellets | 2 | 1.1 | --- | --- | --- | --- | --- | 127100 | --- | --- | --- | 1.7 | --- | 25 | 1 | 0.44776 | 0.3 | 0.67 | --- | --- | 0% | --- | 0.983 | --- | 223.2 | 0 | 3.6 | 1.08
| Large CHP - wood pellets | [1] | 261 | 522 | --- | --- | --- | --- | --- | Wood pellets | 1.3 | 1 | --- | --- | --- | --- | --- | 64000 | --- | --- | --- | 1.6 | --- | 25 | 1 | 0.5 | 0.32 | 0.64 | --- | --- | 0% | --- | 0.983 | --- | 75.6 | 0 | 3.6 | 1.08
| Small CHP - straw | [1] | 3 | 17 | --- | --- | --- | --- | --- | Straw | 3.8 | 3 | --- | --- | --- | --- | --- | 318200 | --- | --- | --- | 4 | --- | 25 | 1 | 0.17857 | 0.15 | 0.84 | --- | --- | 0% | --- | 0.964 | --- | 259.2 | 39.6 | 3.6 | 1.08
| Medium CHP - straw | [1] | 24 | 53 | --- | --- | --- | --- | --- | Straw | 2.3 | 1.5 | --- | --- | --- | --- | --- | 149900 | --- | --- | --- | 2 | --- | 25 | 1 | 0.45588 | 0.31 | 0.68 | --- | --- | 0% | --- | 0.964 | --- | 252 | 0 | 3.6 | 1.08
| Large CHP - straw | [1] | 41 | 90 | --- | --- | --- | --- | --- | Straw | 2.1 | 1.3 | --- | --- | --- | --- | --- | 124900 | --- | --- | --- | 1.9 | --- | 25 | 1 | 0.45588 | 0.31 | 0.68 | --- | --- | 0% | --- | 0.964 | --- | 241.2 | 0 | 3.6 | 1.08
| Large CHP - coal | [1] | 550 | 655 | --- | --- | --- | --- | --- | Coal | 1.9 | --- | --- | --- | --- | --- | --- | 31000 | --- | --- | --- | 2.9 | --- | 25 | 0.15 | 0.84 | 0.42 | 0.5 | 0.49 | --- | 0% | --- | 0.97 | --- | 126 | 5.4 | 2.88 | 0
| Medium CHP - natural gas SC | [1] | 27.5 | 38 | --- | --- | --- | --- | --- | Natural gas | 0.73 | --- | --- | --- | --- | --- | --- | 18600 | --- | --- | --- | 5.1 | --- | 25 | --- | 0.72727 | 0.32 | 0.44 | 0.37 | --- | 0% | --- | 0 | --- | 54 | 5.4 | 3.6 | 0
| Large CHP - natural gas SC | [1] | 82.5 | 87 | --- | --- | --- | --- | --- | Natural gas | 0.59 | --- | --- | --- | --- | --- | --- | 29500 | --- | --- | --- | 4.5 | --- | 25 | --- | 0.94595 | 0.35 | 0.37 | 0.4 | --- | 0% | --- | 0 | --- | 54 | 5.4 | 3.6 | 0
| Medium CHP - natural gas CC | [1] | 55 | 42 | --- | --- | --- | --- | --- | Natural gas | 1 | 0.3 | --- | --- | --- | --- | --- | 29300 | --- | --- | --- | 4.4 | --- | 25 | --- | 1.3143 | 0.46 | 0.35 | 0.51 | --- | 0% | --- | 0 | --- | 54 | 5.4 | 3.6 | 0
| Large CHP - natural gas CC | [1] | 300 | 167 | --- | --- | --- | --- | --- | Natural gas | 0.68 | 0.2 | --- | --- | --- | --- | --- | 29300 | --- | --- | --- | 4.4 | --- | 25 | --- | 1.8 | 0.54 | 0.3 | 0.59 | --- | 0% | --- | 0 | --- | 54 | 5.4 | 3.6 | 0
| Engine - natural gas | [1] | 5.5 | 5.8 | --- | --- | --- | --- | --- | Natural gas | 0.6 | 0.35 | --- | --- | --- | --- | --- | 9750 | --- | --- | --- | 5.4 | --- | 25 | --- | 0.95455 | 0.42 | 0.44 | 0.47 | --- | 0% | --- | 0 | --- | 216 | 1134 | 2.16 | 0
| Large CHP - coal - carbon capture | Ramboll | 495 | 619 | --- | --- | --- | --- | --- | Coal | 3.52 | --- | --- | --- | --- | --- | --- | 65666 | --- | --- | --- | 2.9 | --- | 25 | 0.15 | 0.8 | 0.32 | 0.4 | 0.39 | --- | 90% | --- | 0.97 | --- | 126 | 5.4 | 2.88 | 0
| Large CHP - wood chips - carbon capture | Ramboll | 159 | 572 | --- | --- | --- | --- | --- | Wood chips | 5.3235 | 2.8665 | --- | --- | --- | --- | --- | 132266 | --- | --- | --- | 3.8 | --- | 25 | 1 | 0.27778 | 0.2 | 0.72 | --- | --- | 90% | --- | 0.98 | --- | 86.4 | 7.2 | 28.8 | 1.08
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
HP's | Electric heat pump | [1] | --- | 4 | --- | --- | --- | --- | --- | Electricity | --- | --- | 0.33 | 0.33 | --- | --- | --- | --- | 2000 | --- | --- | --- | 3.2 | 25 | --- | --- | --- | --- | --- | 3.6 | 0% | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
RE | Geothermal | [1] | --- | 10 | --- | --- | --- | --- | --- | Electricity | --- | --- | 1.95 | 0.65 | --- | --- | --- | --- | 20000 | --- | --- | --- | 3.5 | 25 | --- | --- | --- | --- | --- | 3.6 | 0% | --- | --- | --- | --- | --- | --- | ---
| Solar PV | [1] | 10 | --- | --- | --- | --- | --- | --- | Solar PV | 0.62 | --- | --- | --- | --- | --- | --- | 8100 | --- | --- | --- | --- | --- | 20 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| Solar - small | Ramboll | --- | --- | 2000 | --- | --- | --- | --- | Solar | --- | --- | --- | --- | 380 | --- | --- | --- | --- | 4 | --- | --- | --- | 30 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| Solar - medium | Ramboll | --- | --- | 10000 | --- | --- | --- | --- | Solar | --- | --- | --- | --- | 200 | --- | --- | --- | --- | 2 | --- | --- | --- | 30 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| Solar - large | Ramboll | --- | --- | 20000 | --- | --- | --- | --- | Solar | --- | --- | --- | --- | 190 | --- | --- | --- | --- | 2 | --- | --- | --- | 30 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| Large onshore wind turbine | [1] | 4.2 | --- | --- | --- | --- | --- | --- | --- | 0.71 | 0.41 | --- | --- | --- | --- | --- | 14000 | --- | --- | --- | 1.5 | --- | 27 | --- | --- | --- | --- | --- | --- | 0% | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---

## Inputtothemodel
Index | Name | Type | Size | (Units) | Capacity/Output | (Units) | Eff. 11 | Eff. 12 | Eff. 13 | Eff. 14 | Min load | (Units) | Gradient | (Units) | Input 1 | Install Cost | (Units) | Lifetime |  | Annual O&M Cost | (Units) | Output 1 | Output 2 | Output 3 | Output 4
3 | Solar PV 10 kW system | Solar PV |  |  | 100000 | kW | 1 | 0 | 0 | 0 |  |  |  |  | Elec. from 10 kW PV system | 34630 | USD | 33 | Years | 190 | USD | Electricity to the grid
4 | Solar PV 100 kW system | Solar PV |  |  | 100000 | kW | 1 | 0 | 0 | 0 |  |  |  |  | Elec. from 100 kW PV system | 249300 | USD | 33 | Years | 1900 | USD | Electricity to the grid
5 | Solar PV 1000 kW system | Solar PV |  |  | 100000 | kW | 1 | 0 | 0 | 0 |  |  |  |  | Elec. from 1000 kW PV system | 2025000 | USD | 33 | Years | 16000 | USD | Electricity to the grid
7 | Central plant boiler | Boiler |  |  | 100 | kW | 0.84 | 0 | 0 | 0 |  |  |  |  | Natural gas | 85250 | USD | 40 | Years | 2800 | USD | 350-375F ~120 PSI heat
8 | Central plant boiler | Boiler |  |  | 1000 | kW | 0.84 | 0 | 0 | 0 |  |  |  |  | Natural gas | 812500 | USD | 40 | Years | 24375 | USD | 350-375F ~120 PSI heat
9 | Central plant boiler | Boiler |  |  | 2500 | kW | 0.86 | 0 | 0 | 0 |  |  |  |  | Natural gas | 2031249 | USD | 40 | Years | 60937.5 | USD | 350-375F ~120 PSI heat
10 | Central plant boiler | Boiler |  |  | 10000 | kW | 0.88 | 0 | 0 | 0 |  |  |  |  | Natural gas | 8124999 | USD | 40 | Years | 243750 | USD | 350-375F ~120 PSI heat
11 | Reciprocating engine (natural gas) | Recip. Engine |  |  | 300 | kW | 0.31 | 0 | 0 | 0 |  |  |  |  | Natural gas | 289230 | USD | 20 | Years | 36977 | USD | Electricity to the grid
12 | Reciprocating engine (natural gas) | Recip. engine |  |  | 1000 | kW | 0.34 | 0 | 0 | 0 |  |  |  |  | Natural gas | 878673 | USD | 20 | Years | 87867 | USD | Electricity to the grid
13 | Reciprocating engine (natural gas) | Recip. engine |  |  | 3000 | kW | 0.35 | 0 | 0 | 0 |  |  |  |  | Natural gas | 2599408 | USD | 20 | Years | 248591 | USD | Electricity to the grid
14 | Reciprocating engine (natural gas) | Recip. engine |  |  | 5000 | kW | 0.37 | 0 | 0 | 0 |  |  |  |  | Natural gas | 4240818 | USD | 20 | Years | 392352 | USD | Electricity to the grid
15 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen |  |  | 100 | kW | 0.284 | 0.51 | 0 | 0 |  |  |  |  | Natural gas | 239359 | USD | 20 | Years | 19084 | USD | Electricity to the grid | 275-300F ~30 PSI heat
16 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen |  |  | 500 | kW | 0.346 | 0.44 | 0 | 0 |  |  |  |  | Natural gas | 1050578 | USD | 20 | Years | 69425 | USD | Electricity to the grid | 275-300F ~30 PSI heat
17 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen |  |  | 1000 | kW | 0.35 | 0.44 | 0 | 0 |  |  |  |  | Natural gas | 1776236 | USD | 20 | Years | 110690 | USD | Electricity to the grid | 275-300F ~30 PSI heat
18 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen |  |  | 3000 | kW | 0.36 | 0.37 | 0 | 0 |  |  |  |  | Natural gas | 3671609 | USD | 20 | Years | 270334 | USD | Electricity to the grid | 275-300F ~30 PSI heat
19 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen |  |  | 5000 | kW | 0.39 | 0.35 | 0 | 0 |  |  |  |  | Natural gas | 6119348 | USD | 20 | Years | 404527 | USD | Electricity to the grid | 275-300F ~30 PSI heat
20 | Natural gas turbine | Natural gas turbine |  |  | 1135 | kW | 0.211 | 0 | 0 | 0 |  |  |  |  | Natural gas | 4903760 | USD | 31.25 | Years | 72318 | USD | Electricity to the grid
21 | Natural gas turbine | Natural gas turbine |  |  | 5338 | kW | 0.273 | 0 | 0 | 0 |  |  |  |  | Natural gas | 10663045 | USD | 31.25 | Years | 235401 | USD | Electricity to the grid
22 | Natural gas turbine | Natural gas turbine |  |  | 9983 | kW | 0.279 | 0 | 0 | 0 |  |  |  |  | Natural gas | 17866872 | USD | 31.25 | Years | 426209 | USD | Electricity to the grid
23 | Natural gas turbine | Natural gas turbine |  |  | 22708 | kW | 0.336 | 0 | 0 | 0 |  |  |  |  | Natural gas | 31484614 | USD | 31.25 | Years | 678409 | USD | Electricity to the grid
24 | Natural gas turbine | Natural gas turbine |  |  | 45331 | kW | 0.361 | 0 | 0 | 0 |  |  |  |  | Natural gas | 53992053 | USD | 31.25 | Years | 1141419 | USD | Electricity to the grid
25 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen |  |  | 1135 | kW | 0.211 | 0.453 | 0 | 0 |  |  |  |  | Natural gas | 6412579 | USD | 31.25 | Years | 103312 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
26 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen |  |  | 5338 | kW | 0.273 | 0.423 | 0 | 0 |  |  |  |  | Natural gas | 12756620 | USD | 31.25 | Years | 336287 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
27 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen |  |  | 9983 | kW | 0.279 | 0.402 | 0 | 0 |  |  |  |  | Natural gas | 21245185 | USD | 31.25 | Years | 608870 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
28 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen |  |  | 22708 | kW | 0.336 | 0.392 | 0 | 0 |  |  |  |  | Natural gas | 37270160 | USD | 31.25 | Years | 969156 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
29 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen |  |  | 45331 | kW | 0.361 | 0.302 | 0 | 0 |  |  |  |  | Natural gas | 63335594 | USD | 31.25 | Years | 1630598 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
30 | Electric chiller (air cooled) | Central plant chiller |  |  | 352 | kW | 2.96 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 89896 | USD | 20 | Years | 2697 | USD | Chilled water at plant
31 | Electric chiller (air cooled) | Central plant chiller |  |  | 668 | kW | 2.96 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 150335 | USD | 20 | Years | 4510 | USD | Chilled water at plant
32 | Electric chiller (air cooled) | Central plant chiller |  |  | 1055 | kW | 2.96 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 205187 | USD | 20 | Years | 6156 | USD | Chilled water at plant
33 | Electric chiller (air cooled) | Central plant chiller |  |  | 1758 | kW | 2.96 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 338935 | USD | 20 | Years | 10168 | USD | Chilled water at plant
34 | Single stage absorption chiller | Central plant chiller |  |  | 352 | kW | 0.7 | 0 | 0 | 0 |  |  |  |  | 200-225F heat | 184653 | USD | 20 | Years | 9233 | USD | Chilled water at plant
35 | Single stage absorption chiller | Central plant chiller |  |  | 879 | kW | 0.7 | 0 | 0 | 0 |  |  |  |  | 200-225F heat | 359748 | USD | 20 | Years | 17987 | USD | Chilled water at plant
36 | Single stage absorption chiller | Central plant chiller |  |  | 2339 | kW | 0.7 | 0 | 0 | 0 |  |  |  |  | 200-225F heat | 712120 | USD | 20 | Years | 35606 | USD | Chilled water at plant
37 | Single stage absorption chiller | Central plant chiller |  |  | 3359 | kW | 0.7 | 0 | 0 | 0 |  |  |  |  | 200-225F heat | 948171 | USD | 20 | Years | 47409 | USD | Chilled water at plant
38 | Single stage absorption chiller | Central plant chiller |  |  | 5152 | kW | 0.7 | 0 | 0 | 0 |  |  |  |  | 200-225F heat | 1410910 | USD | 20 | Years | 70545 | USD | Chilled water at plant
39 | Dual stage absorption chiller | Central plant chiller |  |  | 352 | kW | 1.1 | 0 | 0 | 0 |  |  |  |  | 300-325F ~80 PSI heat | 298842 | USD | 20 | Years | 14942 | USD | Chilled water at plant
40 | Dual stage absorption chiller | Central plant chiller |  |  | 879 | kW | 1.1 | 0 | 0 | 0 |  |  |  |  | 300-325F ~80 PSI heat | 578897 | USD | 20 | Years | 28945 | USD | Chilled water at plant
41 | Dual stage absorption chiller | Central plant chiller |  |  | 2339 | kW | 1.1 | 0 | 0 | 0 |  |  |  |  | 300-325F ~80 PSI heat | 1125138 | USD | 20 | Years | 56257 | USD | Chilled water at plant
42 | Dual stage absorption chiller | Central plant chiller |  |  | 3359 | kW | 1.1 | 0 | 0 | 0 |  |  |  |  | 300-325F ~80 PSI heat | 1498124 | USD | 20 | Years | 74906 | USD | Chilled water at plant
43 | Dual stage absorption chiller | Central plant chiller |  |  | 5152 | kW | 1.1 | 0 | 0 | 0 |  |  |  |  | 300-325F ~80 PSI heat | 2215611 | USD | 20 | Years | 110781 | USD | Chilled water at plant
44 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller |  |  | 527 | kW | 7.92 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 326718 | USD | 20 | Years | 3267 | USD | Chilled water at plant
45 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller |  |  | 1019 | kW | 8.49 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 631655 | USD | 20 | Years | 6316 | USD | Chilled water at plant
46 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller |  |  | 1371 | kW | 8.45 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 849467 | USD | 20 | Years | 8494 | USD | Chilled water at plant
47 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller |  |  | 2004 | kW | 8.35 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 1241529 | USD | 20 | Years | 12415 | USD | Chilled water at plant
48 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller |  |  | 2461 | kW | 8.35 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 1524684 | USD | 20 | Years | 15246 | USD | Chilled water at plant
49 | Organic Rankine cycle turbine (high temp) | Central plant heat engine |  |  | 1000 | kW | 0.019 | 0.75 | 0 | 0 |  |  |  |  | 550-575F ~1000 PSI heat | 4290000 | USD | 20 | Years | 195000 | USD | Electricity to the grid
50 | Organic Rankine cycle turbine (high temp) | Central plant heat engine |  |  | 1400 | kW | 0.19 | 0.75 | 0 | 0 |  |  |  |  | 550-575F ~1000 PSI heat | 4862000 | USD | 20 | Years | 221000 | USD | Electricity to the grid
51 | Organic Rankine cycle turbine (low temp) | Central plant heat engine |  |  | 280 | kW | 0.09 | 0 | 0 | 0 |  |  |  |  | 200-225F heat | 616000 | USD | 20 | Years | 28000 | USD | Electricity to the grid
52 | Waste to energy cogeneration | Central plant cogen |  |  | 5000 | kW | 0.3 | 0.45 | 0 | 0 |  |  |  |  | Combustable waste | 15000000 | USD | 30 | Years | 1000000 | USD | Electricity to the grid | 225_250F
53 | Waste to energy cogeneration | Central plant cogen |  |  | 10000 | kW | 0.3 | 0.45 | 0 | 0 |  |  |  |  | Combustable waste | 28000000 | USD | 30 | Years | 1900000 | USD | Electricity to the grid | 225_250F
54 | Biomass cogeneration | Central plant cogen |  |  | 100 | kW | 0.3 | 0.45 | 0 | 0 |  |  |  |  | Biomass | 552800 | USD | 30 | Years | 4100 | USD | Electricity to the grid | 225_250F
55 | Biomass cogeneration | Central plant cogen |  |  | 1000 | kW | 0.3 | 0.45 | 0 | 0 |  |  |  |  | Biomass | 5527999 | USD | 30 | Years | 41000 | USD | Electricity to the grid | 225_250F
56 | Biomass boiler | Central plant boiler |  |  | 100 | kW | 0.82 | 0 | 0 | 0 |  |  |  |  | Biomass | 100000 | USD | 30 | Years | 4300 | USD | 350-375F ~120 PSI heat
57 | Biomass boiler | Central plant boiler |  |  | 1000 | kW | 0.82 | 0 | 0 | 0 |  |  |  |  | Biomass | 1000000 | USD | 30 | Years | 43000 | USD | 350-375F ~120 PSI heat
58 | Solar thermal (100 m^2 panel area) | Solar thermal |  |  | 100000 | kW | 0.45 | 0 | 0 | 0 |  |  |  |  | Solar irradiance in 100 sq meters | 146600 | USD | 32 | Years | 1460 | USD | 225_250F
59 | Solar thermal (100 m^2 panel area) | Solar thermal |  |  | 100000 | kW | 0.45 | 0 | 0 | 0 |  |  |  |  | Solar irradiance in 1000 sq meters | 1465999 | USD | 32 | Years | 14600 | USD | 225_250F
60 | Steam turbine | Central plant heat engine |  |  | 339 | kW | 0.139 | 0.86 | 0 | 0 |  |  |  |  | 350-375F ~120 PSI heat | 169563 | USD | 30 | Years | 5086 | USD | Electricity to the grid | 225_250F
61 | Steam turbine | Central plant heat engine |  |  | 1153 | kW | 0.139 | 0.86 | 0 | 0 |  |  |  |  | 350-375F ~120 PSI heat | 576513 | USD | 30 | Years | 17295 | USD | Electricity to the grid | 225_250F
62 | Steam turbine | Central plant heat engine |  |  | 2253 | kW | 0.156 | 0.843 | 0 | 0 |  |  |  |  | 350-375F ~120 PSI heat | 1126921 | USD | 30 | Years | 33807 | USD | Electricity to the grid | 225_250F
63 | Steam turbine | Central plant heat engine |  |  | 4147 | kW | 0.156 | 0.843 | 0 | 0 |  |  |  |  | 350-375F ~120 PSI heat | 2073581 | USD | 30 | Years | 62207 | USD | Electricity to the grid | 225_250F
64 | Steam turbine | Central plant heat engine |  |  | 5934 | kW | 0.156 | 0.843 | 0 | 0 |  |  |  |  | 350-375F ~120 PSI heat | 2967205 | USD | 30 | Years | 89016 | USD | Electricity to the grid | 225_250F
65 | Electric Generator (Diesel) | Electric Generator |  |  | 2000 | kW | 0.35 | 0 | 0 | 0 |  |  |  |  | Diesel | 1200000 | USD | 20 | Years | 30000 | USD | Electricity to the grid
Lower calorific values
| Natural gas boiler |  |  |  | 30 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Natural gas boiler |  |  |  | 100 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Natural gas boiler |  |  |  | 200 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Natural gas boiler |  |  |  | 500 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Natural gas boiler |  |  |  | 1000 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Natural gas boiler |  |  |  | 5000 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Natural gas boiler |  |  |  | 10000 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Electric boiler |  |  |  | 30 | kW heat | [6 empty] | 5 | MW/min | Electricity from the grid | [6 empty] | Heat
| Electric boiler |  |  |  | 100 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat
| Electric boiler |  |  |  | 200 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat
| Electric boiler |  |  |  | 500 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat
| Electric boiler |  |  |  | 1000 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat
| Electric boiler |  |  |  | 5000 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat
| Electric boiler |  |  |  | 10000 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat
| Natural gas engine cogeneration |  |  |  | 500 | kW heat | [8 empty] | Natural gas | [6 empty] | Electricity | Heat up to 110 dgr.C
| Natural gas engine cogeneration |  |  |  | 1000 | kW heat | [8 empty] | Natural gas | [6 empty] | Electricity | Heat up to 110 dgr.C
| Natural gas engine cogeneration |  |  |  | 5000 | kW heat | [8 empty] | Natural gas | [6 empty] | Electricity | Heat up to 110 dgr.C
| Natural gas engine cogeneration |  |  |  | 10000 | kW heat | [8 empty] | Natural gas | [6 empty] | Electricity | Heat up to 110 dgr.C
| Electric heat pump combined heating and cooling |  |  |  | 10 | kW heat | [6 empty] | 1 | MW/min | Electricity from the grid | [6 empty] | Heat, 75 dgr.C | Cold, 6 dgr.C
| Electric heat pump combined heating and cooling |  |  |  | 100 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat, 75 dgr.C | Cold, 6 dgr.C
| Electric heat pump combined heating and cooling |  |  |  | 500 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat, 75 dgr.C | Cold, 6 dgr.C
| Electric heat pump combined heating and cooling |  |  |  | 1000 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat, 75 dgr.C | Cold, 6 dgr.C
| Electric heat pump combined heating and cooling |  |  |  | 5000 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat, 75 dgr.C | Cold, 6 dgr.C
MW/min
MW/min
| Wood chip boiler |  |  |  | 10 | MW heat | [8 empty] | Wood chip
| Wood chip boiler |  |  |  | 20 | MW heat | [8 empty] | Wood chip
| Wood chip boiler |  |  |  | 50 | MW heat | [8 empty] | Wood chip
| Wood chip boiler |  |  |  | 100 | MW heat | [8 empty] | Wood chip
| Wood chip boiler |  |  |  | 200 | MW heat | [8 empty] | Wood chip
| Wood chip boiler |  |  |  | 400 | MW heat | [8 empty] | Wood chip
| Wood chip CHP |  |  |  | 10 | MW heat |  |  |  |  | 30% |  |  |  | Wood chip
| Wood chip CHP |  |  |  | 20 | MW heat |  |  |  |  | 30% |  |  |  | Wood chip
| Wood chip CHP |  |  |  | 50 | MW heat |  |  |  |  | 30% |  |  |  | Wood chip
| Wood chip CHP |  |  |  | 100 | MW heat |  |  |  |  | 30% |  |  |  | Wood chip
| Wood chip CHP |  |  |  | 200 | MW heat |  |  |  |  | 30% |  |  |  | Wood chip
| Wood chip CHP |  |  |  | 400 | MW heat |  |  |  |  | 30% |  |  |  | Wood chip
| Waste for energy CHP |  | 15 | t/h | [6 empty] | 30% |  |  |  | Waste
| Waste for energy CHP |  | 30 | t/h | [6 empty] | 30% |  |  |  | Waste
| Waste for energy CHP |  | 60 | t/h | [6 empty] | 30% |  |  |  | Waste
| Solar thermal, mild climate |  | 10 | m2 | 5 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, mild climate |  | 100 | m2 | 50 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, mild climate |  | 1000 | m2 | 500 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, mild climate |  | 10000 | m2 | 5000 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, mild climate |  | 100000 | m2 | 50000 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, warm climate |  | 10 | m2 | 12 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, warm climate |  | 100 | m2 | 120 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, warm climate |  | 1000 | m2 | 1200 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, warm climate |  | 10000 | m2 | 12000 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, warm climate |  | 100000 | m2 | 120000 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
10

## Storage
Index | Stand By Loss | (Units) | Name | Type | Volume | (Units) | Max. Temp. | (Units) | Capacity | (Units) | Eff. | Input | Install Cost | (Units) | Lifetime | (Units) | Annual O&M cost | (Units) | Output | Max Power | (Units)
1 | 0.25 | kW | Chiller with integrated ice storage | Central plant chiller |  |  |  |  | 105.5 | kWhs | 3.3 | Electricity from the grid | 18000 | USD | 25 | Years | 450 | USD | Chilled water at plant | 17.6 | kW
2 | 1 | kW | Chilled water storage tank | Central plant thermal storage |  |  |  |  | 925.5 | kWhs | 0.98 | Chilled water at plant | 67196 | USD | 40 | Years | 500 | USD | Chilled water at plant | 1000 | kW
3 | 1 | kW | Chilled water storage tank | Central plant thermal storage |  |  |  |  | 3085 | kWhs | 0.98 | Chilled water at plant | 184042 | USD | 40 | Years | 1000 | USD | Chilled water at plant | 3000 | kW
4 | 1 | kW | Chilled water storage tank | Central plant thermal storage |  |  |  |  | 3702 | kWhs | 0.98 | Chilled water at plant | 209690 | USD | 40 | Years | 1000 | USD | Chilled water at plant | 3700 | kW
5 | 1 | kW | Hot water storage tank | Central plant thermal storage |  |  |  |  | 1202 | kWhs | 0.98 | 225-250F ~5 PSI heat | 67196 | USD | 40 | Years | 500 | USD | 225-250F ~5 PSI heat | 1200 | kW
6 | 3 | kW | Hot water storage tank | Central plant thermal storage |  |  |  |  | 4010 | kWhs | 0.98 | 225-250F ~5 PSI heat | 184042 | USD | 40 | Years | 1000 | USD | 225-250F ~5 PSI heat | 4000 | kW
7 | 4 | kW | Hot water storage tank | Central plant thermal storage |  |  |  |  | 4813 | kWhs | 0.98 | 225-250F ~5 PSI heat | 209690 | USD | 40 | Years | 1000 | USD | 225-250F ~5 PSI heat | 5000 | kW
8 | 288 | kW | Low temperature hot water network | Thermal distribution network |  |  |  |  | 612 | kWhs | 0.984 | 225-250F ~5 PSI heat | 0 | USD | 25 | Years | 200000 | USD | Hot water distributed to buildings | 900000 | kW
9 | 288 | kW | High temperature hot water network | Thermal distribution network |  |  |  |  | 612 | kWhs | 0.984 | 350-375F ~120 PSI heat | 0 | USD | 25 | Years | 200000 | USD | Hot water distributed to buildings | 900000 | kW
10 | 500 | kW | Steam network | Thermal distribution network |  |  |  |  | 3000 | kWhs | 0.7 | 300-325F ~80 PSI heat | 0 | USD | 25 | Years | 2000000 | USD | Hot water distributed to buildings | 900000 | kW
11 | 51 | kW | Chilled water network | Thermal distribution network |  |  |  |  | 3000 | kWhs | 1 | Chilled water at plant | 0 | USD | 25 | Years | 140000 | USD | Chilled water distributed to buildings | 900000 | kW
12 | 0 | kW | FlowBatteryZn | ElecStorage |  |  |  |  | 400 | kWhs | 0.88 | EfromBus | 3000000 | USD | 15 | Years | 150000 | USD | EtoBus | 100 | kW
1

## Wind
Index | Co-Eff. 1 | Co-Eff. 2 | Co-Eff. 3 | Co-Eff. 4 | Co-Eff. 5 | Swept Area | (Units) | Name | Type | Input | Install Cost | (Units) | Lifetime | (Units) | Annual O&M cost | (Units) | Output
1 | -0.4989 | 0.34095 | -0.03959 | 0.00169 | -0.0000247 | 8000 | m^2 | Wind turbine (2.5 MW) | Wind turbine | Wind | 5000000 | USD | 40 | Years | 50000 | USD | EtoBus

## Input
Index | Name | Type | Size | (Units) | Capacity/Output | (Units) | Eff. 11 | Eff. 12 | Eff. 13 | Eff. 14 | Min load | (Units) | Gradient | (Units) | Input 1 | Install Cost | (Units) | Lifetime |  | Annual O&M Cost | (Units) | Output 1 | Output 2 | Output 3 | Output 4
3 | Solar PV 10 kW system | Solar PV |  |  | 100000 | kW | 1 | 0 | 0 | 0 |  |  |  |  | Elec. from 10 kW PV system | 34630 | USD | 33 | Years | 190 | USD | Electricity to the grid
4 | Solar PV 100 kW system | Solar PV |  |  | 100000 | kW | 1 | 0 | 0 | 0 |  |  |  |  | Elec. from 100 kW PV system | 249300 | USD | 33 | Years | 1900 | USD | Electricity to the grid
5 | Solar PV 1000 kW system | Solar PV |  |  | 100000 | kW | 1 | 0 | 0 | 0 |  |  |  |  | Elec. from 1000 kW PV system | 2025000 | USD | 33 | Years | 16000 | USD | Electricity to the grid
7 | Central plant boiler | Boiler |  |  | 100 | kW | 0.84 | 0 | 0 | 0 |  |  |  |  | Natural gas | 85250 | USD | 40 | Years | 2800 | USD | 350-375F ~120 PSI heat
8 | Central plant boiler | Boiler |  |  | 1000 | kW | 0.84 | 0 | 0 | 0 |  |  |  |  | Natural gas | 812500 | USD | 40 | Years | 24375 | USD | 350-375F ~120 PSI heat
9 | Central plant boiler | Boiler |  |  | 2500 | kW | 0.86 | 0 | 0 | 0 |  |  |  |  | Natural gas | 2031249 | USD | 40 | Years | 60937.5 | USD | 350-375F ~120 PSI heat
10 | Central plant boiler | Boiler |  |  | 10000 | kW | 0.88 | 0 | 0 | 0 |  |  |  |  | Natural gas | 8124999 | USD | 40 | Years | 243750 | USD | 350-375F ~120 PSI heat
11 | Reciprocating engine (natural gas) | Recip. Engine |  |  | 300 | kW | 0.31 | 0 | 0 | 0 |  |  |  |  | Natural gas | 289230 | USD | 20 | Years | 36977 | USD | Electricity to the grid
12 | Reciprocating engine (natural gas) | Recip. engine |  |  | 1000 | kW | 0.34 | 0 | 0 | 0 |  |  |  |  | Natural gas | 878673 | USD | 20 | Years | 87867 | USD | Electricity to the grid
13 | Reciprocating engine (natural gas) | Recip. engine |  |  | 3000 | kW | 0.35 | 0 | 0 | 0 |  |  |  |  | Natural gas | 2599408 | USD | 20 | Years | 248591 | USD | Electricity to the grid
14 | Reciprocating engine (natural gas) | Recip. engine |  |  | 5000 | kW | 0.37 | 0 | 0 | 0 |  |  |  |  | Natural gas | 4240818 | USD | 20 | Years | 392352 | USD | Electricity to the grid
15 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen |  |  | 100 | kW | 0.284 | 0.51 | 0 | 0 |  |  |  |  | Natural gas | 239359 | USD | 20 | Years | 19084 | USD | Electricity to the grid | 275-300F ~30 PSI heat
16 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen |  |  | 500 | kW | 0.346 | 0.44 | 0 | 0 |  |  |  |  | Natural gas | 1050578 | USD | 20 | Years | 69425 | USD | Electricity to the grid | 275-300F ~30 PSI heat
17 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen |  |  | 1000 | kW | 0.35 | 0.44 | 0 | 0 |  |  |  |  | Natural gas | 1776236 | USD | 20 | Years | 110690 | USD | Electricity to the grid | 275-300F ~30 PSI heat
18 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen |  |  | 3000 | kW | 0.36 | 0.37 | 0 | 0 |  |  |  |  | Natural gas | 3671609 | USD | 20 | Years | 270334 | USD | Electricity to the grid | 275-300F ~30 PSI heat
19 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen |  |  | 5000 | kW | 0.39 | 0.35 | 0 | 0 |  |  |  |  | Natural gas | 6119348 | USD | 20 | Years | 404527 | USD | Electricity to the grid | 275-300F ~30 PSI heat
20 | Natural gas turbine | Natural gas turbine |  |  | 1135 | kW | 0.211 | 0 | 0 | 0 |  |  |  |  | Natural gas | 4903760 | USD | 31.25 | Years | 72318 | USD | Electricity to the grid
21 | Natural gas turbine | Natural gas turbine |  |  | 5338 | kW | 0.273 | 0 | 0 | 0 |  |  |  |  | Natural gas | 10663045 | USD | 31.25 | Years | 235401 | USD | Electricity to the grid
22 | Natural gas turbine | Natural gas turbine |  |  | 9983 | kW | 0.279 | 0 | 0 | 0 |  |  |  |  | Natural gas | 17866872 | USD | 31.25 | Years | 426209 | USD | Electricity to the grid
23 | Natural gas turbine | Natural gas turbine |  |  | 22708 | kW | 0.336 | 0 | 0 | 0 |  |  |  |  | Natural gas | 31484614 | USD | 31.25 | Years | 678409 | USD | Electricity to the grid
24 | Natural gas turbine | Natural gas turbine |  |  | 45331 | kW | 0.361 | 0 | 0 | 0 |  |  |  |  | Natural gas | 53992053 | USD | 31.25 | Years | 1141419 | USD | Electricity to the grid
25 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen |  |  | 1135 | kW | 0.211 | 0.453 | 0 | 0 |  |  |  |  | Natural gas | 6412579 | USD | 31.25 | Years | 103312 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
26 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen |  |  | 5338 | kW | 0.273 | 0.423 | 0 | 0 |  |  |  |  | Natural gas | 12756620 | USD | 31.25 | Years | 336287 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
27 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen |  |  | 9983 | kW | 0.279 | 0.402 | 0 | 0 |  |  |  |  | Natural gas | 21245185 | USD | 31.25 | Years | 608870 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
28 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen |  |  | 22708 | kW | 0.336 | 0.392 | 0 | 0 |  |  |  |  | Natural gas | 37270160 | USD | 31.25 | Years | 969156 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
29 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen |  |  | 45331 | kW | 0.361 | 0.302 | 0 | 0 |  |  |  |  | Natural gas | 63335594 | USD | 31.25 | Years | 1630598 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
30 | Electric chiller (air cooled) | Central plant chiller |  |  | 352 | kW | 2.96 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 89896 | USD | 20 | Years | 2697 | USD | Chilled water at plant
31 | Electric chiller (air cooled) | Central plant chiller |  |  | 668 | kW | 2.96 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 150335 | USD | 20 | Years | 4510 | USD | Chilled water at plant
32 | Electric chiller (air cooled) | Central plant chiller |  |  | 1055 | kW | 2.96 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 205187 | USD | 20 | Years | 6156 | USD | Chilled water at plant
33 | Electric chiller (air cooled) | Central plant chiller |  |  | 1758 | kW | 2.96 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 338935 | USD | 20 | Years | 10168 | USD | Chilled water at plant
34 | Single stage absorption chiller | Central plant chiller |  |  | 352 | kW | 0.7 | 0 | 0 | 0 |  |  |  |  | 200-225F heat | 184653 | USD | 20 | Years | 9233 | USD | Chilled water at plant
35 | Single stage absorption chiller | Central plant chiller |  |  | 879 | kW | 0.7 | 0 | 0 | 0 |  |  |  |  | 200-225F heat | 359748 | USD | 20 | Years | 17987 | USD | Chilled water at plant
36 | Single stage absorption chiller | Central plant chiller |  |  | 2339 | kW | 0.7 | 0 | 0 | 0 |  |  |  |  | 200-225F heat | 712120 | USD | 20 | Years | 35606 | USD | Chilled water at plant
37 | Single stage absorption chiller | Central plant chiller |  |  | 3359 | kW | 0.7 | 0 | 0 | 0 |  |  |  |  | 200-225F heat | 948171 | USD | 20 | Years | 47409 | USD | Chilled water at plant
38 | Single stage absorption chiller | Central plant chiller |  |  | 5152 | kW | 0.7 | 0 | 0 | 0 |  |  |  |  | 200-225F heat | 1410910 | USD | 20 | Years | 70545 | USD | Chilled water at plant
39 | Dual stage absorption chiller | Central plant chiller |  |  | 352 | kW | 1.1 | 0 | 0 | 0 |  |  |  |  | 300-325F ~80 PSI heat | 298842 | USD | 20 | Years | 14942 | USD | Chilled water at plant
40 | Dual stage absorption chiller | Central plant chiller |  |  | 879 | kW | 1.1 | 0 | 0 | 0 |  |  |  |  | 300-325F ~80 PSI heat | 578897 | USD | 20 | Years | 28945 | USD | Chilled water at plant
41 | Dual stage absorption chiller | Central plant chiller |  |  | 2339 | kW | 1.1 | 0 | 0 | 0 |  |  |  |  | 300-325F ~80 PSI heat | 1125138 | USD | 20 | Years | 56257 | USD | Chilled water at plant
42 | Dual stage absorption chiller | Central plant chiller |  |  | 3359 | kW | 1.1 | 0 | 0 | 0 |  |  |  |  | 300-325F ~80 PSI heat | 1498124 | USD | 20 | Years | 74906 | USD | Chilled water at plant
43 | Dual stage absorption chiller | Central plant chiller |  |  | 5152 | kW | 1.1 | 0 | 0 | 0 |  |  |  |  | 300-325F ~80 PSI heat | 2215611 | USD | 20 | Years | 110781 | USD | Chilled water at plant
44 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller |  |  | 527 | kW | 7.92 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 326718 | USD | 20 | Years | 3267 | USD | Chilled water at plant
45 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller |  |  | 1019 | kW | 8.49 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 631655 | USD | 20 | Years | 6316 | USD | Chilled water at plant
46 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller |  |  | 1371 | kW | 8.45 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 849467 | USD | 20 | Years | 8494 | USD | Chilled water at plant
47 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller |  |  | 2004 | kW | 8.35 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 1241529 | USD | 20 | Years | 12415 | USD | Chilled water at plant
48 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller |  |  | 2461 | kW | 8.35 | 0 | 0 | 0 |  |  |  |  | Electricity from the grid | 1524684 | USD | 20 | Years | 15246 | USD | Chilled water at plant
49 | Organic Rankine cycle turbine (high temp) | Central plant heat engine |  |  | 1000 | kW | 0.019 | 0.75 | 0 | 0 |  |  |  |  | 550-575F ~1000 PSI heat | 4290000 | USD | 20 | Years | 195000 | USD | Electricity to the grid
50 | Organic Rankine cycle turbine (high temp) | Central plant heat engine |  |  | 1400 | kW | 0.19 | 0.75 | 0 | 0 |  |  |  |  | 550-575F ~1000 PSI heat | 4862000 | USD | 20 | Years | 221000 | USD | Electricity to the grid
51 | Organic Rankine cycle turbine (low temp) | Central plant heat engine |  |  | 280 | kW | 0.09 | 0 | 0 | 0 |  |  |  |  | 200-225F heat | 616000 | USD | 20 | Years | 28000 | USD | Electricity to the grid
52 | Waste to energy cogeneration | Central plant cogen |  |  | 5000 | kW | 0.3 | 0.45 | 0 | 0 |  |  |  |  | Combustable waste | 15000000 | USD | 30 | Years | 1000000 | USD | Electricity to the grid | 225_250F
53 | Waste to energy cogeneration | Central plant cogen |  |  | 10000 | kW | 0.3 | 0.45 | 0 | 0 |  |  |  |  | Combustable waste | 28000000 | USD | 30 | Years | 1900000 | USD | Electricity to the grid | 225_250F
54 | Biomass cogeneration | Central plant cogen |  |  | 100 | kW | 0.3 | 0.45 | 0 | 0 |  |  |  |  | Biomass | 552800 | USD | 30 | Years | 4100 | USD | Electricity to the grid | 225_250F
55 | Biomass cogeneration | Central plant cogen |  |  | 1000 | kW | 0.3 | 0.45 | 0 | 0 |  |  |  |  | Biomass | 5527999 | USD | 30 | Years | 41000 | USD | Electricity to the grid | 225_250F
56 | Biomass boiler | Central plant boiler |  |  | 100 | kW | 0.82 | 0 | 0 | 0 |  |  |  |  | Biomass | 100000 | USD | 30 | Years | 4300 | USD | 350-375F ~120 PSI heat
57 | Biomass boiler | Central plant boiler |  |  | 1000 | kW | 0.82 | 0 | 0 | 0 |  |  |  |  | Biomass | 1000000 | USD | 30 | Years | 43000 | USD | 350-375F ~120 PSI heat
58 | Solar thermal (100 m^2 panel area) | Solar thermal |  |  | 100000 | kW | 0.45 | 0 | 0 | 0 |  |  |  |  | Solar irradiance in 100 sq meters | 146600 | USD | 32 | Years | 1460 | USD | 225_250F
59 | Solar thermal (100 m^2 panel area) | Solar thermal |  |  | 100000 | kW | 0.45 | 0 | 0 | 0 |  |  |  |  | Solar irradiance in 1000 sq meters | 1465999 | USD | 32 | Years | 14600 | USD | 225_250F
60 | Steam turbine | Central plant heat engine |  |  | 339 | kW | 0.139 | 0.86 | 0 | 0 |  |  |  |  | 350-375F ~120 PSI heat | 169563 | USD | 30 | Years | 5086 | USD | Electricity to the grid | 225_250F
61 | Steam turbine | Central plant heat engine |  |  | 1153 | kW | 0.139 | 0.86 | 0 | 0 |  |  |  |  | 350-375F ~120 PSI heat | 576513 | USD | 30 | Years | 17295 | USD | Electricity to the grid | 225_250F
62 | Steam turbine | Central plant heat engine |  |  | 2253 | kW | 0.156 | 0.843 | 0 | 0 |  |  |  |  | 350-375F ~120 PSI heat | 1126921 | USD | 30 | Years | 33807 | USD | Electricity to the grid | 225_250F
63 | Steam turbine | Central plant heat engine |  |  | 4147 | kW | 0.156 | 0.843 | 0 | 0 |  |  |  |  | 350-375F ~120 PSI heat | 2073581 | USD | 30 | Years | 62207 | USD | Electricity to the grid | 225_250F
64 | Steam turbine | Central plant heat engine |  |  | 5934 | kW | 0.156 | 0.843 | 0 | 0 |  |  |  |  | 350-375F ~120 PSI heat | 2967205 | USD | 30 | Years | 89016 | USD | Electricity to the grid | 225_250F
65 | Electric Generator (Diesel) | Electric Generator |  |  | 2000 | kW | 0.35 | 0 | 0 | 0 |  |  |  |  | Diesel | 1200000 | USD | 20 | Years | 30000 | USD | Electricity to the grid
Lower calorific values
| Natural gas boiler |  |  |  | 30 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Natural gas boiler |  |  |  | 100 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Natural gas boiler |  |  |  | 200 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Natural gas boiler |  |  |  | 500 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Natural gas boiler |  |  |  | 1000 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Natural gas boiler |  |  |  | 5000 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Natural gas boiler |  |  |  | 10000 | kW heat | [8 empty] | Natural gas | [6 empty] | Heat
| Electric boiler |  |  |  | 30 | kW heat | [6 empty] | 5 | MW/min | Electricity from the grid | [6 empty] | Heat
| Electric boiler |  |  |  | 100 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat
| Electric boiler |  |  |  | 200 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat
| Electric boiler |  |  |  | 500 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat
| Electric boiler |  |  |  | 1000 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat
| Electric boiler |  |  |  | 5000 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat
| Electric boiler |  |  |  | 10000 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat
| Natural gas engine cogeneration |  |  |  | 500 | kW heat | [8 empty] | Natural gas | [6 empty] | Electricity | Heat up to 110 dgr.C
| Natural gas engine cogeneration |  |  |  | 1000 | kW heat | [8 empty] | Natural gas | [6 empty] | Electricity | Heat up to 110 dgr.C
| Natural gas engine cogeneration |  |  |  | 5000 | kW heat | [8 empty] | Natural gas | [6 empty] | Electricity | Heat up to 110 dgr.C
| Natural gas engine cogeneration |  |  |  | 10000 | kW heat | [8 empty] | Natural gas | [6 empty] | Electricity | Heat up to 110 dgr.C
| Electric heat pump combined heating and cooling |  |  |  | 10 | kW heat | [6 empty] | 1 | MW/min | Electricity from the grid | [6 empty] | Heat, 75 dgr.C | Cold, 6 dgr.C
| Electric heat pump combined heating and cooling |  |  |  | 100 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat, 75 dgr.C | Cold, 6 dgr.C
| Electric heat pump combined heating and cooling |  |  |  | 500 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat, 75 dgr.C | Cold, 6 dgr.C
| Electric heat pump combined heating and cooling |  |  |  | 1000 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat, 75 dgr.C | Cold, 6 dgr.C
| Electric heat pump combined heating and cooling |  |  |  | 5000 | kW heat | [7 empty] | MW/min | Electricity from the grid | [6 empty] | Heat, 75 dgr.C | Cold, 6 dgr.C
MW/min
MW/min
| Wood chip boiler |  |  |  | 10 | MW heat | [8 empty] | Wood chip
| Wood chip boiler |  |  |  | 20 | MW heat | [8 empty] | Wood chip
| Wood chip boiler |  |  |  | 50 | MW heat | [8 empty] | Wood chip
| Wood chip boiler |  |  |  | 100 | MW heat | [8 empty] | Wood chip
| Wood chip boiler |  |  |  | 200 | MW heat | [8 empty] | Wood chip
| Wood chip boiler |  |  |  | 400 | MW heat | [8 empty] | Wood chip
| Wood chip CHP |  |  |  | 10 | MW heat |  |  |  |  | 30% |  |  |  | Wood chip
| Wood chip CHP |  |  |  | 20 | MW heat |  |  |  |  | 30% |  |  |  | Wood chip
| Wood chip CHP |  |  |  | 50 | MW heat |  |  |  |  | 30% |  |  |  | Wood chip
| Wood chip CHP |  |  |  | 100 | MW heat |  |  |  |  | 30% |  |  |  | Wood chip
| Wood chip CHP |  |  |  | 200 | MW heat |  |  |  |  | 30% |  |  |  | Wood chip
| Wood chip CHP |  |  |  | 400 | MW heat |  |  |  |  | 30% |  |  |  | Wood chip
| Waste for energy CHP |  | 15 | t/h | [6 empty] | 30% |  |  |  | Waste
| Waste for energy CHP |  | 30 | t/h | [6 empty] | 30% |  |  |  | Waste
| Waste for energy CHP |  | 60 | t/h | [6 empty] | 30% |  |  |  | Waste
| Solar thermal, mild climate |  | 10 | m2 | 5 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, mild climate |  | 100 | m2 | 50 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, mild climate |  | 1000 | m2 | 500 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, mild climate |  | 10000 | m2 | 5000 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, mild climate |  | 100000 | m2 | 50000 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, warm climate |  | 10 | m2 | 12 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, warm climate |  | 100 | m2 | 120 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, warm climate |  | 1000 | m2 | 1200 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, warm climate |  | 10000 | m2 | 12000 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
| Solar thermal, warm climate |  | 100000 | m2 | 120000 | MWh heat/a | [8 empty] | Solar | [6 empty] | Heat, 95 dgr.C
10

## Input (2)
Fuel Use Curve
Index | Name | Type | Capacity/Output | (Units) | Eff. 11 | Eff. 12 | Eff. 13 | Eff. 14 | Input 1 | Install Cost | (Units) | Lifetime |  | Annual O&M Cost | (Units) | Output 1 | Output 2 | Output 3 | Output 4 | Equipment | MTTF (hrs) | MTTR (hrs) | Yearly Grid Outages | Output 1 | Units | Output 2 | Units | Input | Units | Latitude | Clear Days | Cloudy Days | Sunny days
ERA 1 | Caterpillar 4 MW Diesel generators (Kwajelein) | Diesel | 4400 | kW | [5 empty] | 1000000 | USD |  |  | 10000 | USD |  |  |  |  | Generator | 4824 | 24 |  | 2200 2420 2640 2860 3080 3300 3520 3740 3960 4180 4400 | kW |  |  | 154.06 167.24 180.45 193.77 206.99 220.15 233.42 246.70 259.84 273.20 286.46 | gallons diesel
ERA 2 | 100 kW TQG | Diesel | 100 | kW | [5 empty] | 28600 | USD |  |  | 7200 | USD |  |  |  |  | Generator | 4824 | 24 |  | 0 25 50 75 100 | kW |  |  | 1.77 3.18 4.67 6.08 7.64 | gallons diesel
ERA 3 | 1 MW Cummins | Diesel | 1000 | kW | [5 empty] | 328000 | USD |  |  | 50000 | USD |  |  |  |  | Generator | 4824 | 24 |  | 250 500 750 1000 | kW |  |  | 21.6 36.4 52.1 71.1 | gallons diesel
ERA 4 | Generic 100 kW diesel | Diesel | 100 | kW | [5 empty] | 32500 | USD |  |  | 1000 | USD |  |  |  |  | Generator | 4824 | 24 |  | 25 50 75 100 | kW |  |  | 2.6 4.1 5.8 7.4 | gallons diesel
ERA 5 | 750 kW Generic | Diesel | 750 | kW | [5 empty] | 245000 | USD |  |  | 7200 | USD |  |  |  |  | Generator | 4824 | 24 |  | 187 375 562 750 | kW |  |  | 16.3 27.4 39.3 53.4 | gallons diesel
ERA 6 | 175 kW Generic | Diesel | 175 | kW | [5 empty] | 50000 | USD |  |  | 7200 | USD |  |  |  |  | Generator | 4824 | 24 |  | 44 87.5 131 175 | kW |  |  | 4.1 6.8 9.7 12.7 | gallons diesel
ERA 7 | 1250 kW Generic | Diesel | 1250 | kW | [5 empty] | 408000 | USD |  |  | 20700 | USD |  |  |  |  | Generator | 4824 | 24 |  | 312 625 937 1250 | kW |  |  | 29.2 51.0 75.1 103.4 | gallons diesel
ERA 8 | 300 kW Generic | Diesel | 300 | kW | [5 empty] | 86500 | USD |  |  | 7200 | USD |  |  |  |  | Generator | 4824 | 24 |  | 75 150 225 300 | kW |  |  | 6.8 11.3 16.1 21.5 | gallons diesel
ERA 9 | 250 kW Generic | Diesel | 250 | kW | [5 empty] | 67000 | USD |  |  | 7200 | USD |  |  |  |  | Generator | 4824 | 24 |  | 62.5 125 187.5 250 | kW |  |  | 5.7 9.5 13.6 18.0 | gallons diesel
ERA 10 | 2000 kW Generic | Diesel | 2000 | kW | [5 empty] | 754500 | USD |  |  | 20700 | USD |  |  |  |  | Generator | 4824 | 24 |  | 500 1000 1500 2000 | kW |  |  | 42.8 72.2 103.5 141.9 | gallons diesel
ERA 11 | 1500 kW Generic | Diesel | 1500 | kW | [5 empty] | 519500 | USD |  |  | 20700 | USD |  |  |  |  | Generator | 4824 | 24 |  | 375 750 1125 1500 | kW |  |  | 32.2 54.3 77.8 106.5 | gallons diesel
ERA 12 | Natural Gas Boiler | Natural Gas | 50 | MMBtu | [5 empty] | 2000000 | USD |  |  | 30000 | USD |  |  |  |  | Boiler | 51200 | 48 |  | 6.4 50 | MMBtu heat |  |  | 10.94 66.5 | MMBtu fuel
ERA 13 | Natural Gas Boiler (Psuedo Coal) | Natural Gas | 50 | MMBtu | [5 empty] | 2000000 | USD |  |  | 60000 | USD |  |  |  |  | Boiler | 51200 | 48 |  | 6.4 50 | MMBtu heat |  |  | 32.82 199.5 | MMBtu fuel
ERA 14 | Natural Gas Boiler | Natural Gas | 0.5 | MMBtu | [5 empty] | 20000 | USD |  |  | 500 | USD |  |  |  |  | Boiler | 51200 | 48 |  | 0.06 0.5 | MMBtu heat |  |  | 0.1094 0.665 | MMBtu fuel
ERA 15 | Solar Turbines Centaur 40 - 3MW | Natural Gas | 3300 | kW | [5 empty] | 11100000 | USD |  |  | 288750 | USD |  |  |  |  | Cogen | 5070 | 27 |  | 500 1000 1500 2000 2500 3000 3300 | kW | 4.27 4.96 5.82 6.84 8.21 10.95 19.66 | MMBtu heat | 10.25 11.9 13.95 16.4 19.68 26.24 47.1 | MMBtu fuel
ERA 16 | Natural Gas Fuel Cell | Natural Gas | 250 | kW | [5 empty] | 875000 | USD |  |  | 25000 | USD |  |  |  |  | Fuel Cell | 1800 | 12 |  | 100 250 | kW |  |  | 1.75 1.90 | MMBtu fuel
ERA 17 | Natural Gas Fuel Cell 2 | Natural Gas | 1000 | kW | [5 empty] | 3500000 | USD |  |  | 100000 | USD |  |  |  |  | Fuel Cell | 1800 | 12 |  | 400 1000 | kW |  |  | 7 7.6 | MMBtu fuel
ERA 18 | Solar | Panels | 10 * avg load | kW | 0.2 |  |  |  |  | site dependent | USD |  |  | site dependent | USD |  |  |  |  | Solar Array | 43800 | 48 | [7 empty] | site dependent | site dependent | site dependent | site dependent
ERA 19 | Microgrid | N/A | N/A | N/A | [5 empty] | 1500000 | USD |  |  | 50000 | USD |  |  |  |  | Microgrid | 43800 | 48 |  | N/A | N/A | N/A | N/A | N/A | N/A
ERA 20 | Grid Connection | N/A | N/A | N/A | [5 empty] | 0 | USD |  |  | 0 | USD |  |  |  |  | Grid | 365 | 12 | 24 | N/A | N/A | N/A | N/A | N/A | N/A
3 | Solar PV 10 kW system | Solar PV | 100000 | kW | 1 | 0 | 0 | 0 | Elec. from 10 kW PV system | 34630 | USD | 33 | Years | 190 | USD | Electricity to the grid
4 | Solar PV 100 kW system | Solar PV | 100000 | kW | 1 | 0 | 0 | 0 | Elec. from 100 kW PV system | 249300 | USD | 33 | Years | 1900 | USD | Electricity to the grid
5 | Solar PV 1000 kW system | Solar PV | 100000 | kW | 1 | 0 | 0 | 0 | Elec. from 1000 kW PV system | 2025000 | USD | 33 | Years | 16000 | USD | Electricity to the grid
7 | Central plant boiler | Boiler | 100 | kW | 0.84 | 0 | 0 | 0 | Natural gas | 85250 | USD | 40 | Years | 2800 | USD | 350-375F ~120 PSI heat
8 | Central plant boiler | Boiler | 1000 | kW | 0.84 | 0 | 0 | 0 | Natural gas | 812500 | USD | 40 | Years | 24375 | USD | 350-375F ~120 PSI heat
9 | Central plant boiler | Boiler | 2500 | kW | 0.86 | 0 | 0 | 0 | Natural gas | 2031249 | USD | 40 | Years | 60937.5 | USD | 350-375F ~120 PSI heat
10 | Central plant boiler | Boiler | 10000 | kW | 0.88 | 0 | 0 | 0 | Natural gas | 8124999 | USD | 40 | Years | 243750 | USD | 350-375F ~120 PSI heat
11 | Reciprocating engine (natural gas) | Recip. Engine | 300 | kW | 0.31 | 0 | 0 | 0 | Natural gas | 289230 | USD | 20 | Years | 36977 | USD | Electricity to the grid
12 | Reciprocating engine (natural gas) | Recip. engine | 1000 | kW | 0.34 | 0 | 0 | 0 | Natural gas | 878673 | USD | 20 | Years | 87867 | USD | Electricity to the grid
13 | Reciprocating engine (natural gas) | Recip. engine | 3000 | kW | 0.35 | 0 | 0 | 0 | Natural gas | 2599408 | USD | 20 | Years | 248591 | USD | Electricity to the grid
14 | Reciprocating engine (natural gas) | Recip. engine | 5000 | kW | 0.37 | 0 | 0 | 0 | Natural gas | 4240818 | USD | 20 | Years | 392352 | USD | Electricity to the grid
15 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen | 100 | kW | 0.284 | 0.51 | 0 | 0 | Natural gas | 239359 | USD | 20 | Years | 19084 | USD | Electricity to the grid | 275-300F ~30 PSI heat
16 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen | 500 | kW | 0.346 | 0.44 | 0 | 0 | Natural gas | 1050578 | USD | 20 | Years | 69425 | USD | Electricity to the grid | 275-300F ~30 PSI heat
17 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen | 1000 | kW | 0.35 | 0.44 | 0 | 0 | Natural gas | 1776236 | USD | 20 | Years | 110690 | USD | Electricity to the grid | 275-300F ~30 PSI heat
18 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen | 3000 | kW | 0.36 | 0.37 | 0 | 0 | Natural gas | 3671609 | USD | 20 | Years | 270334 | USD | Electricity to the grid | 275-300F ~30 PSI heat
19 | Reciprocating engine w/ heat recovery (natural gas) | Recip. engine cogen | 5000 | kW | 0.39 | 0.35 | 0 | 0 | Natural gas | 6119348 | USD | 20 | Years | 404527 | USD | Electricity to the grid | 275-300F ~30 PSI heat
20 | Natural gas turbine | Natural gas turbine | 1135 | kW | 0.211 | 0 | 0 | 0 | Natural gas | 4903760 | USD | 31.25 | Years | 72318 | USD | Electricity to the grid
21 | Natural gas turbine | Natural gas turbine | 5338 | kW | 0.273 | 0 | 0 | 0 | Natural gas | 10663045 | USD | 31.25 | Years | 235401 | USD | Electricity to the grid
22 | Natural gas turbine | Natural gas turbine | 9983 | kW | 0.279 | 0 | 0 | 0 | Natural gas | 17866872 | USD | 31.25 | Years | 426209 | USD | Electricity to the grid
23 | Natural gas turbine | Natural gas turbine | 22708 | kW | 0.336 | 0 | 0 | 0 | Natural gas | 31484614 | USD | 31.25 | Years | 678409 | USD | Electricity to the grid
24 | Natural gas turbine | Natural gas turbine | 45331 | kW | 0.361 | 0 | 0 | 0 | Natural gas | 53992053 | USD | 31.25 | Years | 1141419 | USD | Electricity to the grid
25 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen | 1135 | kW | 0.211 | 0.453 | 0 | 0 | Natural gas | 6412579 | USD | 31.25 | Years | 103312 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
26 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen | 5338 | kW | 0.273 | 0.423 | 0 | 0 | Natural gas | 12756620 | USD | 31.25 | Years | 336287 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
27 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen | 9983 | kW | 0.279 | 0.402 | 0 | 0 | Natural gas | 21245185 | USD | 31.25 | Years | 608870 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
28 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen | 22708 | kW | 0.336 | 0.392 | 0 | 0 | Natural gas | 37270160 | USD | 31.25 | Years | 969156 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
29 | Natural gas turbine w/ heat recovery | Natural gas turbine cogen | 45331 | kW | 0.361 | 0.302 | 0 | 0 | Natural gas | 63335594 | USD | 31.25 | Years | 1630598 | USD | Electricity to the grid | 800-1000F ~3500 PSI heat
30 | Electric chiller (air cooled) | Central plant chiller | 352 | kW | 2.96 | 0 | 0 | 0 | Electricity from the grid | 89896 | USD | 20 | Years | 2697 | USD | Chilled water at plant
31 | Electric chiller (air cooled) | Central plant chiller | 668 | kW | 2.96 | 0 | 0 | 0 | Electricity from the grid | 150335 | USD | 20 | Years | 4510 | USD | Chilled water at plant
32 | Electric chiller (air cooled) | Central plant chiller | 1055 | kW | 2.96 | 0 | 0 | 0 | Electricity from the grid | 205187 | USD | 20 | Years | 6156 | USD | Chilled water at plant
33 | Electric chiller (air cooled) | Central plant chiller | 1758 | kW | 2.96 | 0 | 0 | 0 | Electricity from the grid | 338935 | USD | 20 | Years | 10168 | USD | Chilled water at plant
34 | Single stage absorption chiller | Central plant chiller | 352 | kW | 0.7 | 0 | 0 | 0 | 200-225F heat | 184653 | USD | 20 | Years | 9233 | USD | Chilled water at plant
35 | Single stage absorption chiller | Central plant chiller | 879 | kW | 0.7 | 0 | 0 | 0 | 200-225F heat | 359748 | USD | 20 | Years | 17987 | USD | Chilled water at plant
36 | Single stage absorption chiller | Central plant chiller | 2339 | kW | 0.7 | 0 | 0 | 0 | 200-225F heat | 712120 | USD | 20 | Years | 35606 | USD | Chilled water at plant
37 | Single stage absorption chiller | Central plant chiller | 3359 | kW | 0.7 | 0 | 0 | 0 | 200-225F heat | 948171 | USD | 20 | Years | 47409 | USD | Chilled water at plant
38 | Single stage absorption chiller | Central plant chiller | 5152 | kW | 0.7 | 0 | 0 | 0 | 200-225F heat | 1410910 | USD | 20 | Years | 70545 | USD | Chilled water at plant
39 | Dual stage absorption chiller | Central plant chiller | 352 | kW | 1.1 | 0 | 0 | 0 | 300-325F ~80 PSI heat | 298842 | USD | 20 | Years | 14942 | USD | Chilled water at plant
40 | Dual stage absorption chiller | Central plant chiller | 879 | kW | 1.1 | 0 | 0 | 0 | 300-325F ~80 PSI heat | 578897 | USD | 20 | Years | 28945 | USD | Chilled water at plant
41 | Dual stage absorption chiller | Central plant chiller | 2339 | kW | 1.1 | 0 | 0 | 0 | 300-325F ~80 PSI heat | 1125138 | USD | 20 | Years | 56257 | USD | Chilled water at plant
42 | Dual stage absorption chiller | Central plant chiller | 3359 | kW | 1.1 | 0 | 0 | 0 | 300-325F ~80 PSI heat | 1498124 | USD | 20 | Years | 74906 | USD | Chilled water at plant
43 | Dual stage absorption chiller | Central plant chiller | 5152 | kW | 1.1 | 0 | 0 | 0 | 300-325F ~80 PSI heat | 2215611 | USD | 20 | Years | 110781 | USD | Chilled water at plant
44 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller | 527 | kW | 7.92 | 0 | 0 | 0 | Electricity from the grid | 326718 | USD | 20 | Years | 3267 | USD | Chilled water at plant
45 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller | 1019 | kW | 8.49 | 0 | 0 | 0 | Electricity from the grid | 631655 | USD | 20 | Years | 6316 | USD | Chilled water at plant
46 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller | 1371 | kW | 8.45 | 0 | 0 | 0 | Electricity from the grid | 849467 | USD | 20 | Years | 8494 | USD | Chilled water at plant
47 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller | 2004 | kW | 8.35 | 0 | 0 | 0 | Electricity from the grid | 1241529 | USD | 20 | Years | 12415 | USD | Chilled water at plant
48 | Electric chiller (Mag. Lev. water cooled) | Central plant chiller | 2461 | kW | 8.35 | 0 | 0 | 0 | Electricity from the grid | 1524684 | USD | 20 | Years | 15246 | USD | Chilled water at plant
49 | Organic Rankine cycle turbine (high temp) | Central plant heat engine | 1000 | kW | 0.019 | 0.75 | 0 | 0 | 550-575F ~1000 PSI heat | 4290000 | USD | 20 | Years | 195000 | USD | Electricity to the grid
50 | Organic Rankine cycle turbine (high temp) | Central plant heat engine | 1400 | kW | 0.19 | 0.75 | 0 | 0 | 550-575F ~1000 PSI heat | 4862000 | USD | 20 | Years | 221000 | USD | Electricity to the grid
51 | Organic Rankine cycle turbine (low temp) | Central plant heat engine | 280 | kW | 0.09 | 0 | 0 | 0 | 200-225F heat | 616000 | USD | 20 | Years | 28000 | USD | Electricity to the grid
52 | Waste to energy cogeneration | Central plant cogen | 5000 | kW | 0.3 | 0.45 | 0 | 0 | Combustable waste | 15000000 | USD | 30 | Years | 1000000 | USD | Electricity to the grid | 225_250F
53 | Waste to energy cogeneration | Central plant cogen | 10000 | kW | 0.3 | 0.45 | 0 | 0 | Combustable waste | 28000000 | USD | 30 | Years | 1900000 | USD | Electricity to the grid | 225_250F
54 | Biomass cogeneration | Central plant cogen | 100 | kW | 0.3 | 0.45 | 0 | 0 | Biomass | 552800 | USD | 30 | Years | 4100 | USD | Electricity to the grid | 225_250F
55 | Biomass cogeneration | Central plant cogen | 1000 | kW | 0.3 | 0.45 | 0 | 0 | Biomass | 5527999 | USD | 30 | Years | 41000 | USD | Electricity to the grid | 225_250F
56 | Biomass boiler | Central plant boiler | 100 | kW | 0.82 | 0 | 0 | 0 | Biomass | 100000 | USD | 30 | Years | 4300 | USD | 350-375F ~120 PSI heat
57 | Biomass boiler | Central plant boiler | 1000 | kW | 0.82 | 0 | 0 | 0 | Biomass | 1000000 | USD | 30 | Years | 43000 | USD | 350-375F ~120 PSI heat
58 | Solar thermal (100 m^2 panel area) | Solar thermal | 100000 | kW | 0.45 | 0 | 0 | 0 | Solar irradiance in 100 sq meters | 146600 | USD | 32 | Years | 1460 | USD | 225_250F
59 | Solar thermal (100 m^2 panel area) | Solar thermal | 100000 | kW | 0.45 | 0 | 0 | 0 | Solar irradiance in 1000 sq meters | 1465999 | USD | 32 | Years | 14600 | USD | 225_250F
60 | Steam turbine | Central plant heat engine | 339 | kW | 0.139 | 0.86 | 0 | 0 | 350-375F ~120 PSI heat | 169563 | USD | 30 | Years | 5086 | USD | Electricity to the grid | 225_250F
61 | Steam turbine | Central plant heat engine | 1153 | kW | 0.139 | 0.86 | 0 | 0 | 350-375F ~120 PSI heat | 576513 | USD | 30 | Years | 17295 | USD | Electricity to the grid | 225_250F
62 | Steam turbine | Central plant heat engine | 2253 | kW | 0.156 | 0.843 | 0 | 0 | 350-375F ~120 PSI heat | 1126921 | USD | 30 | Years | 33807 | USD | Electricity to the grid | 225_250F
63 | Steam turbine | Central plant heat engine | 4147 | kW | 0.156 | 0.843 | 0 | 0 | 350-375F ~120 PSI heat | 2073581 | USD | 30 | Years | 62207 | USD | Electricity to the grid | 225_250F
64 | Steam turbine | Central plant heat engine | 5934 | kW | 0.156 | 0.843 | 0 | 0 | 350-375F ~120 PSI heat | 2967205 | USD | 30 | Years | 89016 | USD | Electricity to the grid | 225_250F
65 | Electric Generator (Diesel) | Electric Generator | 2000 | kW | 0.35 | 0 | 0 | 0 | Diesel | 1200000 | USD | 20 | Years | 30000 | USD | Electricity to the grid
Note on V2: Sean Wallace: Mean time to failure
Note on W2: Sean Wallace: Mean time to repair

## Storage (2)
Index | Stand By Loss | (Units) | Name | Type | Capacity | (Units) | Eff. | Input | Install Cost | (Units) | Lifetime | (Units) | Annual O&M cost | (Units) | Output | Max Power | (Units) | Charge Rate | Units | Discharge Rate | Untis | Base Charge Duration (days) | Base Charge Duration (hrs) | MTTF (hrs) | MTTR (hrs)
ERA 1 |  |  | Prime Battery | Large Scale Battery | 25000 | kW | 0.85 |  | 12500000 | USD |  |  | 125000 | USD |  |  |  | 0.5 | C Rate | 1 | C Rate | 1 | 24 | 43800 | 24
ERA 2 |  |  | UPS Battery | UPS | 40 | kW | 0.85 |  | 20000 | USD |  |  | 200 | USD |  |  |  | 1 | C Rate | 25 | C Rate |  |  | 43800 | 24
1 | 0.25 | kW | Chiller with integrated ice storage | Central plant chiller | 105.5 | kWhs | 3.3 | Electricity from the grid | 18000 | USD | 25 | Years | 450 | USD | Chilled water at plant | 17.6 | kW
2 | 1 | kW | Chilled water storage tank | Central plant thermal storage | 925.5 | kWhs | 0.98 | Chilled water at plant | 67196 | USD | 40 | Years | 500 | USD | Chilled water at plant | 1000 | kW
3 | 1 | kW | Chilled water storage tank | Central plant thermal storage | 3085 | kWhs | 0.98 | Chilled water at plant | 184042 | USD | 40 | Years | 1000 | USD | Chilled water at plant | 3000 | kW
4 | 1 | kW | Chilled water storage tank | Central plant thermal storage | 3702 | kWhs | 0.98 | Chilled water at plant | 209690 | USD | 40 | Years | 1000 | USD | Chilled water at plant | 3700 | kW
5 | 1 | kW | Hot water storage tank | Central plant thermal storage | 1202 | kWhs | 0.98 | 225-250F ~5 PSI heat | 67196 | USD | 40 | Years | 500 | USD | 225-250F ~5 PSI heat | 1200 | kW
6 | 3 | kW | Hot water storage tank | Central plant thermal storage | 4010 | kWhs | 0.98 | 225-250F ~5 PSI heat | 184042 | USD | 40 | Years | 1000 | USD | 225-250F ~5 PSI heat | 4000 | kW
7 | 4 | kW | Hot water storage tank | Central plant thermal storage | 4813 | kWhs | 0.98 | 225-250F ~5 PSI heat | 209690 | USD | 40 | Years | 1000 | USD | 225-250F ~5 PSI heat | 5000 | kW
8 | 288 | kW | Low temperature hot water network | Thermal distribution network | 612 | kWhs | 0.984 | 225-250F ~5 PSI heat | 0 | USD | 25 | Years | 200000 | USD | Hot water distributed to buildings | 900000 | kW
9 | 288 | kW | High temperature hot water network | Thermal distribution network | 612 | kWhs | 0.984 | 350-375F ~120 PSI heat | 0 | USD | 25 | Years | 200000 | USD | Hot water distributed to buildings | 900000 | kW
10 | 500 | kW | Steam network | Thermal distribution network | 3000 | kWhs | 0.7 | 300-325F ~80 PSI heat | 0 | USD | 25 | Years | 2000000 | USD | Hot water distributed to buildings | 900000 | kW
11 | 51 | kW | Chilled water network | Thermal distribution network | 3000 | kWhs | 1 | Chilled water at plant | 0 | USD | 25 | Years | 140000 | USD | Chilled water distributed to buildings | 900000 | kW
12 | 0 | kW | FlowBatteryZn | ElecStorage | 400 | kWhs | 0.88 | EfromBus | 3000000 | USD | 15 | Years | 150000 | USD | EtoBus | 100 | kW
Note on Y1: Sean Wallace: Mean time to failure
Note on Z1: Sean Wallace: Mean time to repair